

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0109
	Date:
	3/5/01
	Supersedes:
	
	Date:
	

	Title:
	Brass Water-Side Pressure Transducers for PIC-II

	Category:
	GENERAL
	Termination Date:
	

	Author:
	Matt Canino
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  19XR, XRV and 23XL with PIC-II controls

BDP:  

	
	Purpose:

This bulletin is to inform the field of the availability of brass-bodied pressure transducers for waterside pressure readings and to suggest adding dirt legs in the transducer piping.

Information:

To reduce the number for problems related to corrosion of the water-side pressure transducers, RCD is now providing brass-bodied transducers which can be ordered as part number HK05YZ007.  This change is reflected in the latest RCD parts catalog.  These transducers were also introduced into production in July 2000.

In addition to installing the new transducer, we also recommend the use of dirt legs (traps) to allow an operator the opportunity to clean out the dirt and corrosive material periodically.  The picture and drawing attached (page 2) shows the dirt legs installed.

*Caution: do not confuse this brass transducer with the one that is used for 30 Series products, which is part number HK05YZ001.  It will not operate correctly for our application due to differences in the Maximum Supply Current and Pressure Reading.  For your reference, here is a table with the Manufacturer’s part numbers:

      RCD/Carrier Part Number      Manufacturer’s Part Number      Max. Supply Current

            HK05YZ007                                  2CP5-32-1                                 8.0 mA

            HK05YZ001                                  2CP5-39                                   20.0 mA

File: Controls & Wiring
[image: image1.jpg]LA SR S N Ty & e

e






[image: image2.png]ALTERNATIVE #2: ADD
PIPE & FITTING ASSY

@ 4 WATERBOX
NozaLe

114 - 18 1PT

114 NPTF TEE, BRASS
CAZ01A051 o CAZIRADS!
BALL VALVE
EPTICaDE2
















Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_1045570663

_988694773.doc
�



�
















