

BULLETIN

Carrier Corporation


North American Operations

[image: image1.png]




	Number:
	C0111
	Date:
	3/5/01
	Supersedes:
	C0009
	Date:
	7/21/00

	Title:
	PIC Thermistor Thermowells

	Category:
	Controls / Wiring
	Termination Date:
	

	Author:
	Ted Libera
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models:

Affected:
	CAC:  All PIC-Equipped Chillers 

BDP:  

	
	

	
	


PURPOSE:

Bulletin C0009 informed the field of a set of thermowells that can be used with the standard PIC

thermistors and which can be inserted in the existing thermistor connections.  The purpose of this

bulletin is to correct the application information.

INFORMATION:

Carrier Transicold Marine Division designed these thermowells to satisfy requests from its marine customers.  They are now available through RCD.   

With the exception of the oil temperature sensor, every sensor on a machine equipped with PIC controls from the factory can use the following wells:


P/N 90C02-3932-1  Material = 316SS

Use for corrosive waterside applications: 


P/N 90C02-3932-2  Material = 90/10 Cu-Ni 

These two wells are dimensionally identical.

The other two thermowells presented on bulletin C0009 have applications on marine systems but not on the CSS PIC-equipped chillers. 

Installation:

Transfer the refrigerant from the chiller or drain the waterbox, as appropriate.

The threads on the well OD match the threads on the sensors.

Remove the sensor from its position, install the well in its place. Then install the sensor into the well along with some heat transfer grease. 

FILE:
Controls

[image: image2.png]



	Part Number
	Material
	“A”
	“B”NPT
	“C” NPT
	“D”
	“E”
	“F”
	
	.
	

	90C02-3932-1
	316SS
	37/8”
	1/4
	1/4
	7/8 Hex
	0.258”
	2 1/8
	
	.
	

	90C02-3932-2
	90/10 Cu/Ni
	37/8”
	1/4”
	1/4”
	11/8 Round 

w/flats
	0.258”
	2 1/8
	
	.
	





� EMBED PBrush  ���














Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















_1041229262

