

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0113
	Date:
	3/12/01
	Supersedes:
	
	Date:
	

	Title:
	Head Pressure Reference from PIC-II Benshaw Starters

	Category:
	GENERAL
	Termination Date:
	

	Author:
	Matt Canino
	
	

	
	
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  19XR, XRV and 23XL with PIC-II controls

BDP:  

	
	Purpose:

This bulletin is to inform the field of the location of the output terminals for Head Pressure Reference on PIC-II machines with Benshaw Solid-State starters or Electro-mechanical starters with an ISM.

Information:

PIC-II provides a 4-20mA Head Pressure Reference Signal that can be used by a head pressure controller.  The output terminals are located:

     (ISM - terminals labeled “4-20mA out, Spare, (G) and (+),” on terminal block J8   Wiring diagrams for the 19XR, XRV PIC-II show these terminals labeled as 3 (+) and 4 (-).

     (Benshaw solid-state - terminals labeled J8, 3 (+) and 4 (-)   Refer to the picture below.

[image: image1.jpg]



Refer to page 40 of the 19XR, XRV Start-Up, Operation and Maintenance Instructions (19XR-4SS) for specifics about the functions of the Head Pressure Reference Output.

File: Controls and Wiring


Input/Output Card





Benshaw Terminals J8, 3 & 4








Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















