

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0114
	Date:
	3/12/2001
	Supersedes:
	
	Date:
	

	Title:
	23XL PIC II Software, Version 02

	Category:
	Controls and Wiring
	Termination Date:
	

	Author:
	David Jensen
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  23XL PIC II

BDP:  

	
	


Purpose:

This bulletin is to inform the field of the release of 23XL PIC II software and associated hardware (OTP-PROM) upgrades from version 01 to version 02.  This new version was released to production in August 2000.

Summary:

The RCD replacement CVC part number, with software, is 23XL04009802.

This new version of software, P/N CESR131209-02, requires an OTP “one time programmable” PROM, #69 which is included in the latest CVCs, CEPL130286-04. 

The CCN related updates are found on the Controls Systems Support (CSS) Internet Site at

http://www.carrier-commercial.com/ccnsupport/

The following chart described the software changes that will affect the “local” operation

	23XL PIC II Ver 02 Updated Software Parameters

	The low discharge superheat requirements have been revised.

Compressor = TC Model

                        R-22 low discharge superheat limit = 20o F. R-134a low discharge superheat

                        Limit = 5o F

	Corrected the discharge superheat calculation when the compressor type is not a TC and refrigerant = R-134a.

	The head pressure reference output has been updated to = 0% (4ma) when the condenser pump is off. 

	The capability was added to support Language Translation with the Interactive Language Translator.

	The compressor starts value for the “8 starts in 12 hours” algorithm will reset to 0 when the first valid time is entered into a new chiller and will clear after 12 hours.  

	The start counter will now increment when the 1CR start complete = TRUE.

File: Controls – Wiring


	The random SIO communications lock up, when connected to a CCN device, has been fixed.

	The control point is now allowed to go below 20o F.

	The 23XL controls now have a VFD Load Factor to adjust for load side current error.

	The slide valve 2% delta now equals a 3-sec command to unload. 

	The unit unload shutdown timer is now operational. 

	When the manual slide valve control is released the unit reverts back to automatic temperature control.


Field action:

Most chillers are in applications that do not require this software upgrade.  Contact your warranty engineer if you think a software change is required on a specific chiller.  Most chillers with TD compressors have been upgraded already.







Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















