

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0115
	Date:
	4/19/2001
	Supersedes:
	C9804
	Date:
	1/30/98

	Title:
	23XL Slide Valve Support

	Category:
	GENERAL
	Termination Date:
	

	Author:
	David Jensen
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  23XL
BDP:  


Purpose:

This bulletin is provided to advise the field of a product improvement, the implementation of a slide valve relief shelf that provides support at low load operation and helps to eliminate broken shafts and loose locknuts.  A field installed slide valve shaft clamp is also discussed.  

This bulletin revision adds information for a slide valve shaft clamp for C series compressors.

Machines Affected:

23XL frame 4 chillers built after Oct. 15, 1997 having D40, D41, D60 and D61 compressors with serial numbers higher than 3897V02382 or have model number TD4B*00AH or TD6B*00AH.

Information:

The current relief shelf is not retrofitable to existing C or D series compressors.  If a compressor has a relief shelf from the factory do not remove it.  Removing this component can cause detrimental misalignment.

For the C and D series compressors without the relief shelf, it is recommended that a slide valve clamp be installed during an overhaul of the slide valve assembly. Refer to bulletin C9803 for the slide valve rework procedures.

Service Parts:

A field retrofit kit for the slide valve clamp is available from RCD for both the C and D series compressors.  The C series compressor slide valve clamp kit part number is 23XL660023; the D series is 23XL660021. These kits include the clamp, drills, taps, bolts and necessary instructions to retrofit this component in the field. 

Filing Instructions: Compressor-Motor-Drive-Gears

Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















