

BULLETIN

Carrier Corporation


North American Operations

[image: image1.jpg]




Number:
C0117
Date:
5/14/01
Supersedes:

Date:


Title:
Product Change – Flanged & Dished Water Box Covers

Category:
GENERAL
Termination Date:


Author:
Matt Canino



Dept:
CSS Service Engineering





Models Affected:
CAC:  19XR with Frame 4 through 8 heat exchangers

BDP:  

[image: image2.jpg]



Purpose:

This bulletin is to inform the field of the implementation of flanged and dished water box covers.

Information:

On 19XR machines that call for 150 psi, N.I.H., non-ASME, Frame 4 – 8 heat exchangers, the water box covers will now incorporate a flanged and dished design.  The division plates are welded to the covers and the covers are attached to the tube sheets with loose nuts and bolts (5/8”).

The flanged and dished covers are lighter than the old design, but may require two technicians to tighten the bolts on the inboard locations of the heat exchangers.  

Apply Neverseez (or equivalent) to the bolts at re-assembly, but do not use sealant or lubricant on the gasket.  Bring the nozzle heads straight in at the correct height to avoid wiping the seal off the division plate.  Inspect the seal through the nozzles after assembly.

Torque the bolts twice in a star pattern, waiting at least 20 minutes between passes for gasket relaxation. The final torque spec is 150 ft-lbs.

File: Cooler, Condenser, Economizer

�





�








Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















