

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0124A
	Date:
	6/3/02
	Supersedes:
	C9408
	Date:
	8/25/94

	Title:
	19EA/EB Oil Overheating

	Category:
	
	Termination Date:
	

	Author:
	Scott Nieforth
	
	

	Dept:
	North American Commercial Service Engineering
	
	

	

	Models:

Affected:
	CAC:  19EA / EB5

BDP:  

	
	

	
	


PURPOSE:   

      This bulletin describes modifications required to prevent high thrust bearing oil temperatures

when 19EA/EB5 chillers are converted to higher speed gears or converted to ice storage duty.

This revision includes piping instructions for an alternate oil cooler.

BACKGROUND:

      Changing a chiller’s refrigerant to R-134a or its application to ice storage duty may require impeller speeds to be increased.   Higher shaft speeds will increase thrust bearing oil temperatures.  

PROCEDURE:

      In anticipation of this problem, the diameter of the oil flow orifice in the bearing housing can be 

enlarged from 0.136” to 0.170” as shown in Figure 1.  This modification will increase oil flow to the

thrust bearing.

      Alternatively, if the problem appears after the conversion is completed, the existing oil cooler

can be replaced with a larger 17DA71-2012 oil cooler.  The 1-1/2” NPT water flow connections are on the end of the oil cooler.   Figure 2 shows the water entering the top connection and leaving the center connection of this 4 pass cooler.  The 2” NPT oil connections are on the top of the oil cooler shell.

      An optional method to install the oil cooler without the 2” NPT  threaded connection is available.  A 17FX05007301 weld boss can be attached to the top of the 2” coupling with a ¼” groove weld.  A DE12BA701 1-1/8” C X C elbow can be brazed into the boss.  The 17FX05007301 weld boss will accept a  ¾” NPT pipe plug so the weld between the boss and the oil cooler can be leak checked before the DE12BA701 elbow is brazed into place.  Minor adjustments to the oil lines leading from the oil pump and to the compressor may also be required.

FILE:  Compressor, Motor, Drive, Gears


            [image: image1.jpg]



                                                         FIGURE 1:  19EA / EB5 THRUST BEARING HOUSING  

                                       [image: image2.jpg]



                                                               FIGURE 2:  17DA71-2012 OIL COOLER INSTALLATION















_988694773.doc
�



�
















