

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0125
	Date:
	6/21/01
	Supersedes:
	New
	Date:
	

	Title:
	02XR45003601 Thrust Pad Removal Holes

	Category:
	
	Termination Date:
	

	Author:
	Scott Nieforth
	
	

	Dept:
	North American Commercial Service Engineering
	
	

	

	Models:

Affected:
	CAC:  19XR Frame 4

BDP:  

	
	

	
	


PURPOSE:

      This bulletin summarizes changes to the 19XR Frame 4 high-speed thrust bearing.

BACKGROUND: 

       Revision 4 of 02XR45003601 was placed in production on 5/24/99.  This revision updated some tolerances and eliminated six .094” diameter holes that were centered in the .375” diameter adjusting pad recesses.  

INFORMATION: 

      The .094” diameter holes are not oil passages.  The function of the six .094” diameter holes was to allow a wire to be inserted behind the adjusting pads for removal.  The adjusting pads can be removed with a small screwdriver or a magnet so the .094” holes are unnecessary.  

      The absence of .094” holes in the thrust bearing pockets of 02XR45003601 Rev. 4 thrust bearing housings is not a defect.  

         [image: image1.jpg]


                                         [image: image2.jpg]



              02XR45003601 Rev. 3                                                  02XR45003601 Rev. 4  

FILE:
Compressor, Motor, Drive, Gears










.094” holes








Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















