

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0126
	Date:
	7/3/01
	Supersedes:
	New
	Date:
	

	Title:
	Unlanded Tubes in 23XL Coolers

	Category:
	GENERAL
	Termination Date:
	

	Author:
	Scott Nieforth
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models:

Affected:
	CAC: 23XL Frame 1 & 2

BDP:  

	
	

	
	


PURPOSE: 

This bulletin summarizes unlanded tube usage in 23XL coolers.

INFORMATION:

Unlanded tubes entered production on 23XL Frame 1 & 2 coolers during July 2000.  Eddy current measurements on these chillers will not reveal any cooler tube lands or any swaging at the cooler support sheets.

Refer to Service Bulletin C9819 for swaging requirements on all other heat exchangers.

ACTION – FIELD:

No action is required.

FILE:  Cooler, Condenser, Economizer
















Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















