

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0128
	Date:
	8/17/01
	Supersedes:
	New
	Date:
	

	Title:
	23XL Compressor Bearing Replacement Under Warranty

	Category:
	General
	Termination Date:
	

	Author:
	Scott Nieforth
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models:

Affected:
	CAC:  23XL

BDP:  

	
	

	
	


PURPOSE: 

This bulletin provides guidance for the replacement of 23XL compressor rolling element bearings.

MACHINES AFFECTED:  23XL
INFORMATION: 

The compressor bearings are designed to operate throughout the life of the machine.  23XL bearings will only be covered under first year or extended warranty if they actually fail.  Bearings are not covered under warranty if they are changed as a part of routine maintenance. 

ACTION – FIELD: 

It is not necessary to disassemble 23XL compressors to inspect the bearings unless a symptom indicates there is a problem.  23XL bearings will only be covered under warranty if there is evidence of excessive wear or damage revealed by oil analysis or vibration tests.  

FILE:  Compressor, Motor, Drive, Gears

















_988694773.doc
�



�
















