18
C0206A  19XR Split Ring Diffuser Assembly and Setup
16 of 18


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation




[image: image2.png]MARK |NDICATES CAM
MAX. OFFSET
POSITION




Number:   C0206A
Date:  06/25/02
Supersedes: C9823





Title:  19XR Split Ring Diffuser Assembly and Setup





Author: Steve Bayes

Dept: North American Commercial 



      Service Engineering

Category: General

  





Dealer Bulletin Number:  none                 



MODELS AFFECTED:
Carrier:  19XR chillers (XR5 and XR4 compressors) with PIC- II Controls and Split Ring Diffuser (SRD)

SITUATION: 

This bulletin, which supersedes Bulletin C9823, describes the recommended field assembly and disassembly procedure for the variable diffuser (Split Ring Diffuser or SRD) portion of the 02XR5 compressor, and the 02XR4 compressor with the SRD option.  The diffuser actuator calibration procedure is now covered in separate Bulletin C0207 which complements this bulletin.

SOLUTION:

General Information:

The sequence for assembly and set-up of the split ring diffuser (SRD) follows.  Disassembly of the split ring diffuser can be done by following the procedure in reverse order (omitting calibration and alignment steps).  As with any disassembly, mark all parts removed, and store them in a clean and dry location.  Before any work begins be sure that the refrigerant has been removed or stored in a vessel, and all electrical power has been disconnected and tagged open.  Before beginning this procedure, read all instructions carefully.  Since this bulletin applies to two different machines, some of the figures are representative only.  Two sets of procedural steps starting with number 25 are provided: one for XR5 and one for XR4 assemblies.

[image: image3.png]


Item or part numbers referenced in the figures are listed in Appendix A.  Before assembly, all parts must be clean and free of any contaminants such as machining chips.  Prior to installation, virtually all fasteners are to be treated with either Red or Blue Loctite (Items 60 and 61).  Internal O-rings are to be treated with a light coating of silicone-based O-ring lubricant, such as Parker Super “O-Lube” (Item 40), or compressor oil.

In addition to standard tools, the tools listed in Appendix B will be needed for the assembly.  Jacking Studs (TS-422, TS-432) are listed for the easy removal of the outer diffuser ring (in disassembly).

This procedure is written specifically for setup of the split ring diffuser within a mounted compressor.  Preassembly of the diffuser away from the compressor (e.g., on a table) is not recommended.

The following other Service Bulletins are referenced here:

•
C9815 - 19XR Impeller Spacing Procedure

•
C0015 - 19XR5 [Outer Ring Support] Advisory

•
C0207 - 19XR Split Ring Diffuser Actuator Alignment

•
C0208 - Revised 19XR Impeller Torque Requirements

Procedure:

Ring Assembly

1. Lightly coat face seal O-ring (Item 12) with silicone O-ring lubricant.  Referring to Figures 1 and 2, install O-ring in the discharge wall of compressor base (Item 24)

2. Treat radial seal O-ring (Item 22) with silicone O-ring lubricant.  Install O-ring in the diffuser outer ring (Item 3).  Install one Outer Diffuser Guide Pin (Service Tool TS-420 for XR5, TS-430 for XR4) into the top center diffuser mounting hole in the compressor base.  Mounting hole locations differ with compressor build.  See Figure 3 for a representative hole layout.  (Do not use threaded rod in place of the service tool; damage to the mounting holes in the outer ring will result.)

Apply Blue Loctite to hex head bolts (Item 23).  Slide the outer ring into place over the Guide Pin, with the hole marked “TOP” lined up with the pin (located at 12 o’clock).  Fasten the outer ring in place using the 5 hex head bolts and hardened washers (Item 80).  Hint:  If bolts do not catch the threads in the base easily, try using bolts which are similar to Item 23, but 2” longer, to pull the outer ring towards the base to the point where the standard bolts can reach.  Remove and replace the Guide Pin and extra length bolts (if used) as you go.

Apply torque to tighten the bolts in accordance with the following chart.

Outer Diffuser Ring Attachment (Step 0)

Compressor
Torque - ft-lbs (N-m)

XR4
175 - 250 (237 - 339)

XR5
415 - 590 (562 - 800)

Caution:  When removing the outer ring (in a disassembly operation), be sure that guide pin(s) are installed in diffuser mounting holes, not jacking holes.  (Jacking holes have "JH" stamped next to them.)  Refer to Service Bulletin C0015 for details.

3. Coat the bore and end surfaces of roller assemblies (Item 97) with compressor oil.  Also, coat the outside surface of the eccentric portion of the roller adjusters (Item 198).  (Refer to Figures 4 and 5.)  Apply Blue Loctite to the threads of the 3 socket head roller mounting screws (Item 199).  Place a roller assembly into a pocket in the outer ring.  Insert a roller adjuster and roller mounting screw into the hole in the roller pocket and through the bore of the roller assembly.  Install the other two rollers in the same manner.  The roller mounting screws should be only hand tight, that is, lightly contacting the roller adjusters, allowing the adjusters to rotate freely.

4. Rotate the roller adjusters so that the indicator mark on the top of the adjuster is oriented radially outward and away from the compressor centerline.  This will move the rollers radially outward as far as possible, as shown in Figure 6.

5. Lubricate the outer diameter of the inner ring (Item 7) with compressor oil.  Slide the inner ring into place within the outer ring, with the 3 cutouts in the ring aligned to match the rollers.  Rotate it to a position such that the rack cutout in the inner ring is adjacent to the milled pocket in the outer ring.  (Note: At this point in assembly the rack is not yet fastened to the inner ring.)  Refer to Figure 7.

6. Move the pipes of the inner ring and outer ring into alignment (passages fully open) as follows.  Lightly tap on the lower edge of the inner ring's rack cutout such that the inner ring moves slightly clockwise until an edge appears (can be felt when probing from the inside) in one of the diffuser passages.  Tap lightly on the upper edge of the inner ring rack cutout until the edge just disappears (the passage just becomes smooth) as the ring moves counterclockwise.

Alignment can be best held using the tapered pin suited to the diffuser for the specific compressor build. [from Special Tool Kit xxxxx]  The pin must be inserted into one diffuser passage from the compressor discharge opening, passing through the matched holes in both diffuser rings.

Alternative method:  If the discharge is not accessible or the pin is not available, when the holes are aligned make a precise mark or scribe on the inner ring indicating where the top edge of the rack pocket in the outer diffuser ring meets the inner ring.  (See Figure 8).  This marks the inner ring's position when the diffuser holes are fully open.

7. Apply Blue Loctite to the threads of the two rack mounting screws (Item 56).  Mount the gear rack (Item 41) onto the inner ring.  Install rack mounting screws and washers (Item 14), but do not tighten.  Place a shim in accordance with the chart below at the bottom inside of the milled pocket in the outer ring.

Keeping the diffuser passages aligned as described in Step 6, position the gear rack such that it rests against the shim on the bottom edge of the pocket in the outer ring. Applying force in a direction so as to avoid rotating the inner ring, tighten the rack mounting screws.  Use a torque in accordance with the following chart.

Rack Attachment (Step 7)

Compressor
Shim Thickness - in. (mm)
Torque - ft-lbs (N-m)

XR4
0.050 (1.3)
53 - 75 (72 - 102)

XR5
0.060 (1.5)
80 - 115 (108 - 156)

If this assembly had not been previously shimmed, document in service records for this unit that the shimming process has been done.

Note: It must be assured that after the rack is tightened, the correct shim gap exists between the rack and the bottom edge of the pocket in the outer ring.  If an alignment pin is not used as described in Step 6, (i.e., the alternative method is used instead), this gap must be checked when the mark made on the inner ring is aligned with the upper edge of the rack pocket (as shown in Figure 8).

8. Remove the shim and diffuser alignment tool.

Preloading

9. Rotate the two lower roller adjusters clockwise just enough to permit insertion and free movement of a .008” shim along the gap between the rings, between these rollers.  Next, adjust these same two roller adjusters further (if necessary) until a .008” shim will fit snugly next to the uppermost roller.  (See Figure 9.)

10. Lock the two lower roller adjusters in position by tightening each socket head roller retaining screw (Item 199) while holding the roller adjuster in position (without rotation) with a wrench.  Torque the retaining screws to 45 - 55 ft-lbs (61 - 75 N-m).

11. Rotate the upper roller adjuster clockwise until a torque of 18 - 22 in-lb (2.0 - 2.5 N-m) is applied.  Recheck that the .008” shims still can be moved as described in Step 9.  Readjust upper roller if necessary to achieve this.  Now lock the upper roller adjuster in place in a manner similar to that described in the previous step. 

12. Using a torque wrench applied to one of the rack mounting screws and with the handle aligned radially outward, measure the torque needed to rotate the inner ring in both directions.  The torque, measured at the mounting rack screws, should fall in the ranges shown in the table below.  If the measured values are beyond these ranges, repeat the preload procedure varying the upper adjuster torque applied in Step 11 as necessary.

Torque to Rotate Inner Ring (Step 12)

Compressor
Clockwise 

Torque - ft-lbs (N-m)
Counterclockwise 

Torque - ft-lbs (N-m)

XR4 and XR5
12 - 30 (16 - 41)
40 (54) max

Remove shims.  Rotate the rack down until it hits the bottom of the outer ring pocket, and leave it in that position.

Impeller and Shroud Assembly

13. Install the 6 foot supports (Item 191) into the shroud (Item 1) from the side which will face the diffuser assembly, until each is lightly seated against the face of the shroud.  See Figure 10.  Hint:  If a new shroud is being installed, chase the external threads of the six foot supports (Item 191) and re-tap the internal threads of the corresponding holes in the shroud with die and tap respectively (1/2” – 13 UNC).

14. Install the impeller (Item 2) with associated assembly parts.  Refer to the latest revision of Centrifugal Service Bulletin C9815 for proper spacing requirements and Bulletin C0208 for impeller bolt torque requirements.

15. Apply silicone O-ring lubricant to face seal O-ring (Item 16 for XR5, Item 30 for XR4).  Install O-ring in shroud.  Screw 4 guide pins (Service Tool TS-421 for XR5, TS-431 for XR4) into shroud mounting holes in outer diffuser wall, but not into the top hole corresponding to the rigging point.  (Do not use threaded rod in place of the service tool, due to the weight of the part.)  Connect the shroud rigging shackle (Service Tool TS-423) to the top mounting hole of the shroud, and slide the shroud into place.

Apply Blue Loctite to the threads of hex head screws (Item 15).  Fasten the shroud in place using these screws.  Replace the guide pins with the same hardware.  Tighten the bolts according to the following chart.

Shroud Attachment (Step 15)

Compressor
Torque - ft-lbs (N-m)
Bolt Qty.

XR4
105 - 150 (143 - 203)
9

XR5
260 - 370 (352 - 501)
7

16. Using a screwdriver, screw all six foot supports into contact with the inner ring. Lightly tighten all of the foot supports in a star pattern.  Apply Blue Loctite to jam nuts (Item 192), and loosely install a jam nut  on the threaded end of each foot support.  Back each of the foot supports out of contact with the ring, then screw back in until it just makes contact.  Using a torque wrench fitted with a screwdriver blade, tighten the foot support to 5 - 7 in-lbs. (0.56 - 0.79 N-m) (gentle contact). Holding the foot support with a screwdriver so that it does not rotate, tighten the jam nut.  Repeat for each of the six foot supports.

Verify that the torque required to rotate the inner ring counterclockwise at one of the rack mounting bolts is still within the specifications listed in Step 12.

17. Assemble the rotating stall pressure transducer tube assembly (Item 11) using fittings (Item 220 or 13) into the shroud.  See Figure 10.  If installing new fittings, use Red Loctite on the mating thread surfaces entering the shroud and compressor housing.

18. Apply Blue Loctite to the threads of the 3 set screws (Item 20).  Plug the shroud jacking screw holes in the shroud with set screws until hand tight.  Do not apply high torque - the set screws MUST NOT protrude past the opposite surface of the shroud.

Suction Housing and Pinion  Assembly

19. Rig suction housing (Item 9) for mounting.  Apply silicone O-ring lubricant to face seal O-ring (Item 19).  Install O-ring into the groove in the suction housing (Item 9).  Refer to  Figure 11.  Apply Blue Loctite to bolts (Item 17 or 18).  Move housing into position, and pull it up to the compressor with 2 of these bolts.  Note: It must be assured that the O‑ring remains in its groove during this operation.

20. (XR4 only)  Refer to Figures 11 and 13.  Attach sprocket Item 224 (with smaller bore than other sprocket, Item 227) to the pinion shaft prior to installation into the compressor assembly as follows.  Slide the sprocket over the shaft such that the end of the shaft is flush with the end of the matching sprocket bore.  Using one of the sprocket set screw holes as a guide, use a .250” carbide drill to drill approximately 1/8” into the pinion shaft.  Blow out chips.  Apply Blue Loctite to set screw (Item 225), and seat the set screw through the sprocket into the drilled cavity.  Repeat for the second set screw.

21. Apply a light coating of silicone O-ring lubricant to the O-ring (Item 36) for use with the diffuser pinion/seal housing assembly (Item 29).  Refer to Figure 12 for XR5, Figure 13 for XR4.  Note radial tick mark on the flange of the pinion/seal housing assembly.

Install O-ring onto diffuser actuator pinion/seal housing assembly, and insert assembly into suction housing as follows:  Insert with radial tick mark on seal housing flange between the 2 o'clock and 4 o’clock positions.  If assembly will not permit insertion, it may be necessary to readjust the position of the suction housing.

22. Install remaining suction housing mounting bolts, and tighten all in accordance with the following chart.

Suction Housing Attachment (Step 22)

Compressor
Torque  ft-lbs (N-m)

XR4
175 - 250 (237 - 339)

XR5
410 - 580 (555 - 786)

23. Apply Blue Loctite to pinion/seal housing mounting bolts (Item 21).  On XR4 units, place mounting ring (Item 70) over seal housing flange, with flat facing to the left.  Hand tighten the mounting screws (Item 21) through slots in the seal housing flange with washers (Item 32) for XR5, or through holes in the mounting ring (for XR4).

24. Remove pinion/rack backlash as follows. (The seal housing mounting circle center is offset from the shaft centerline to permit this adjustment.)  Rotate the pinion assembly flange clockwise by hand (or with light force using a wrench) until it stops (tick mark will end up at approximately 6 o’clock).  After zero backlash is achieved, tighten mounting bolts (Item 21) to 22-31 ft-lb. (30-42 N-m).

Hint: For disassembly, it may be helpful to first rotate the seal housing flange counterclockwise so as to add backlash, to facilitate pinion removal.

XR5 Actuator Installation and Shaft Alignment

25. Refer to Figure 12.  Apply Blue Loctite to screws (Item 59).  Install actuator support bracket (Item 58) onto the suction housing (Item 9) using screws and washers (Item 65).  Do not fully tighten.  Lay the actuator (Item 72 without coupling, Item 70) onto the support bracket.  Adjust the height of the bracket until the shafts are aligned vertically, and tighten the mounting screws to 22-31 ft-lbs. (30-42 N-m).  Remove the actuator from the bracket.

26. Verify that the SRD pinion shaft is rotated fully counterclockwise by one of the following methods: (a) Slide one coupling half (Item 70, without the plastic insert) onto the pinion shaft such that the end of the shaft is flush with the end of the matching coupling bore.  Tighten the coupling set screw (temporarily) such that it grabs the shaft.  Try to rotate the pinion counterclockwise, using a screwdriver shaft placed between the coupling teeth as a lever.  (b) Using padding to protect the shaft surface, try to rotate the shaft counterclockwise with a strap wrench or similar device.  Note: It is critical that the shaft surface not be marred; surface abnormalities will make it impossible to slide on coupling!

27. If not already done in the preceding step, slide one coupling half (Item 70, without the plastic insert) onto the pinion shaft such that the end of the shaft is flush with the end of the matching coupling bore. If the pointer (Item 189) is not already attached to this coupling half, apply Blue Loctite to screws (Item 190) and attach the pointer with screws hand tight.  Rotate the coupling so that the pointer is 5o to the left of the 12 o’clock position (one mark on the angle indicator plate).  Assure that the pointer does not touch the angle indicator plate.

28. Using the coupling set screw hole as a guide, use a .250” carbide drill to drill approximately 1/8” into the pinion shaft.  Blow out chips.  Apply Blue Loctite to set screw (part of coupling assy, Item 70), and seat the set screw through the coupling into the drilled cavity.  If the pointer does not still indicate 5o to the left of the 12 o’clock position, shift the pointer plate along its mounting slots.  Tighten the pointer mounting screws.  (It may be necessary to temporarily rotate the coupling, now joined to the shaft, clockwise to get access to both pointer mounting screws.  Return the assembly to the farthest counterclockwise position.)

29. Refer to procedure Step 2 of Service Bulletin C-0207. 19XR Split Ring Diffuser Actuator Alignment.  If the configuration calls for a pinion shaft rotation of 5o, rotate the pinion clockwise by this amount using a screwdriver shaft placed between the coupling teeth as a lever.  The pointer should now be in the 12 o’clock position.

30. With the actuator shaft disconnected from the compressor assembly, move the actuator to its 0% or 4mA position per Procedure Step 3 in Service Bulletin C‑0207.

31. Apply Blue Loctite to screws (Item 73).  Slide the second metal coupling piece onto the actuator shaft, positioned such that the set screw hole is accessible.  Loosely assemble the actuator onto the bracket using screws (Item 73), washers (Item 197), and nuts (Item 78, two per screw).  Mesh the coupling halves with the plastic insert between (assembly, Item 70).

Align the shafts horizontally using the slotted holes in the bracket.  Maximum allowable misalignment is as follows:


•
Parallel (offset between axes) - within 0.015 in (0.381 mm)


•
Angular (yaw between axes) - within 0.5 degrees

Fasten the actuator in place using screws (Item 73), washers (Item 197), and nuts (Item 78, two per screw).  Tighten the hardware and jam nuts to 6-9 ft‑lbs. (8-12 N-m).

32. Using the actuator side coupling set screw hole as a guide, use a .250” carbide drill to drill approximately 1/8” into the actuator shaft.  Blow out chips.  Apply Blue Loctite to set screw (Item 41), and seat the set screw through the coupling into the drilled cavity.

33. Complete the actuator setup per Procedure Steps 6 - 7 in Service Bulletin C‑0207.

XR4 Actuator Installation and Shaft Alignment

25. Refer to Figure 13.  Apply Blue Loctite to bolts (Item 69).  Install actuator mounting plate (Item 59) onto the suction housing (Item 9) using the two bolts.  Tighten to 53 - 75 ft-lbs (72 - 102 N‑m).

26. Verify that the SRD pinion is rotated fully counterclockwise by rotating the sprocket and pinion shaft counterclockwise until it stops.

27. Refer to procedure Step 2 of Service Bulletin C-0207. 19XR Split Ring Diffuser Actuator Alignment.  If the configuration calls for a pinion shaft rotation of 5o, rotate the pinion clockwise by this amount.

28. Apply Blue Loctite to actuator mounting screws (Item 73).  Mount the actuator (Item 72) onto the plate using these screws, washers (Item 197), and nuts (Item 78).  Do not tighten hardware.

29. Move the actuator to its 0% or 4mA position per Procedure Step 3 in Service Bulletin C‑0207.

30. Slide the second sprocket (Item 227) over the actuator shaft such that the end of the shaft is flush with the end of the matching sprocket bore.  Assemble the chain (Item 221) onto the sprockets.

31. Adjust the position of the actuator such that (a) the end of the shaft is flush with the end of the matching sprocket bore, (b) the sprockets are aligned in the same plane (the chain is not bent or kinked), and (c) there is no slack in the chain.  Tighten the actuator mounting screws (Item 73) to 6-9 ft‑lbs. (8-12 N‑m).  Using one of the sprocket set screw holes as a guide, use a .250” carbide drill to drill approximately 1/8” into the actuator shaft.  Blow out chips.  Apply Blue Loctite to set screw (Item 225), and seat the set screw through the sprocket into the drilled cavity.  Repeat for the second set screw.

32. Assemble the chain guard (Item 201) over the chain-sprocket assembly, and tighten with the two chain guard mounting screws (Item 202).

33. Assemble label (Item 190) onto the chain guard (if not already done).  "180" should be at the top.  Apply Blue Loctite to screw Item 184, and install pointer (Item 189) into the end of the pinion shaft using screw pointing at the 6 o'clock position.

34. Complete the actuator setup per Procedure Steps 6 - 7 in Service Bulletin C‑0207.

POLICY:

N/A

[image: image4.png]MARK |NDICATES CAM
MAX. OFFSET
POSITION



[image: image5.png]




[image: image6.png]




[image: image7.png]soue s



[image: image8.png]- TORQUE TO 5-7 IN-LBS

;j

\\\/

-,

\

1\

&\’/&/

iz

N

/\',////,_

A

i

il

1 . ////f\*

/

oy
<&

Z

M.

iall
(2.2 7T
L)

(il

7

\

\

%'

Z




[image: image9.png]


[image: image10.png]


[image: image11.png]




[image: image12.png]



[image: image13.png]




[image: image14.png]





APPENDIX A:  PARTS LISTS

Note: the item numbers shown are the same as those appearing in the parts lists in the associated engineering drawings.

KEY: 

ITEM NUMBERS IN THIS FONT APPLY TO BOTH XR4 AND XR5 COMPRESSORS (e.g., 14), ALTHOUGH  THE PARTS ARE NOT NECESSARILY IDENTICAL.  IN SOME CASES THE DIFFERENCES ARE SHOWN.
ITEM NUMBERS IN THIS FONT APPLY TO ONE COMPRESSOR SIZE ONLY: 13
ITEM
COMPONENT OR PART NAME

1
SHROUD

2
IMPELLER

3
DIFFUSER, OUTER RING

7 ‡
DIFFUSER, INNER RING

9
HSG, SUCTION END ,VARIABLE DIFFUSER

11
TUBE ASY, IMPELLER TIP PRESSURE

12
O RING, 
27.5 x 28 x 0.25 (XR5)


22 x 22.5 x 0.25 (XR4)

13
COUPLING, UNION (XR5)

(= Item 220 for XR4)

14
WASHER, 1/2 HARDENED

15
HEX HD SCREW,


3/4-10 x 2-1/2 LG (XR5)


5/8-11 x 1-1/2 LG (XR4)

16
O RING, 
31.94 ID x 1/4 (XR5)

17
SCREW, HEX HEAD (26 ea.)


3/4-10 x 3 LG (XR4)

18
SCREW, HEX HEAD (20 ea.)


1-8 x 3 1/2 LG (XR5)

19
O RING,
44 x 44 1/2 x 1/4 (XR5)


35 x 35 x 1/4  (XR4)

20
SCREW, SET,


3/4-10 x 1.00 LG (XR5)


5/8-11 x 0.75 LG (XR4)

21
SCREW, HEX HEAD,


3/8-16 x 1-1/4 LG




ITEM
COMPONENT OR PART NAME

22
O RING, 
33 x 33 1/2 x 1/4 (XR5)


26.75 x 27 x 0.25 (XR4)

23
SCREW, HEX HEAD,


7/8-9 x 5-1/2 LG (XR5)


3/4-10 x 4-1/2 LG (XR4)

24
BASE, COMPRESSOR

29
HSG ASY, SEAL, DIFFUSER DRIVE

30
O-RING, 
26 x 26.5 x 0.25 (XR4)

32
WASHER, PLAIN, 3/8 SAE (XR5 only)

36
O RING 

40
GREASE, O-RING, POLYSILOXANE 

(PARKER "SUPER O-LUBE")

41
GEAR RACK, VARIABLE DIFFUSER

56
SCREW, SOCKET HEAD, 


1/2-13 x 1-1/2 LG

58
BRACKET,SUPPORT, ACTUATOR (XR5 only)

59
SCREW, HEX HEAD, 3/8-16 x 7/8 LG (XR5)

MOUNTING PLATE, ACTUATOR (XR4)

60
SEALANT, THREAD – Red Loctite 554

61
ADHESIVE, THREAD LOCKING – Blue Loctite 242

65
WASHER, PLAIN, 3/8 (XR5 only)

69
SCREW, HEX HEAD  1/2-13 x 2 LG (XR4 only)

ITEM
COMPONENT OR PART NAME

70
COUPLING ASSEMBLY, JAW TYPE , INCLUDING SET SCREWS (XR5)

MOUNTING RING (XR4)

72
MOTOR, OPERATOR

73
SCREW, HEX HEAD,


1/4-20 x 1 LG (XR5)


1/4-20 x 1-1/2 (XR4)

78
NUT, HEX, 1/4-20

80
WASHER, HARDENED


7/8 (XR5)


3/4 (XR4)

97 ‡
ROLLER ASSEMBLY, VARIABLE DIFFUSER

184
SCREW, HEX HEAD, 


#10-24 x 1/2 LG  (XR4 only)

189
POINTER, DIFFUSER POSITION  

190
LABEL, DIFFUSER POSITION  (XR4 only; included in Item 29 for XR5)

190
SCREW, PAN HEAD


#10-24 x ½ LG (XR5 only)

191
FOOT, SUPPORT, VARIABLE DIFFUSER.

192
NUT, HEX, 1/2-13

197
WASHER, PLAIN, 1/4

198
CAM LOCK, ROLLER

199
SCREW, SOCKET HEAD,

 
3/8-16 x 4.00 LG (XR5)


 3/8-16 x 3.5 LG (XR4)

201
CHAIN GUARD  (XR4 only)

202
SCREW, HEX HEAD, 1/4-20 x 1/2 LG  (XR4 only)

220
COUPLING, UNION (XR4)

(= Item 13 for XR5)

221
CHAIN (XR4 only)

224
SPROCKET (XR4 only)

225
SCREW, SET 5/16-18 x 1/2 LG 

(XR4 only)

227
SPROCKET (XR4 only)

‡ IMPORTANT:  The roller assemblies (Item 97) and the inner ring (Item 7) have an anodized coating.  They must not be exposed to harsh solvents.

APPENDIX B:  SPECIAL TOOLS

Part No. (02XR5)
Part No. (02XR4)
Qty Req’d
Grainger Order

No. ***
Description

TS-420
TS-430
3

Outer Diffuser Guide Pins

TS-421
TS-431
4

Shroud Guide Pins

TS-422
TS-432
3

Outer Diffuser Ring Jacking Studs

TS-423
TS-423
1

Shroud Rigging Shackle



3 **
1AC11
Feeler Gages (25 blade set)



1
1ARP7
Dial Torque Wrench, 0-75 in-lb.(0-90 cm-kg.), ¼” Drive



1

Torque Wrench capable of applying at least 415 ft-lb.(562 N-m)



1
1AH90
¼” Drive Standard Screw Driver Bit

Notes:



**
- A minimum of 3 are required to set-up the inner diffuser ring.



***
- Specific part number is not required.  Similar equivalent tools can be substituted.  Part numbers are from the Grainger 1997 Catalog No. 388.

APPENDIX C:  WEIGHTS

Part
02XR5:  lb. (kg) 
02XR4:  lb. (kg) 

Outer Diffuser Ring (Item 3)
260 (118)
 140(64) 

Inner Diffuser Ring (Item 7)
70 (32)
 30(14) 

Impeller (Item 2)
40 (18)
 18(8) 

Shroud (Item 1)
525 (239)
 210(95) 

Suction Housing (Item 9)
1400 (636)
 700(318) 

� EMBED PBrush  ���


Figure 6 - View of Inner Ring Roller Lock (Step 4)











� EMBED PBrush  ���


Figure 5 - Roller Assembly, Side View


(Step 3)





� EMBED PBrush  ���


Figure 9 - Roller Lock 


Adjustment (Step 9)








� EMBED PBrush  ���


Figure 10 - Shroud Installation, Exploded View (Step 13)





�


Figure 3 - Outer Diffuser Ring Assembly, End View (Step 2)








� EMBED Word.Picture.8  ���





Figure 4 - Inner Diffuser Ring Assembly, Exploded View (Step 3)





�


Figure 2 - Diffuser/Impeller/Shroud Assembly (Step 1)


Note: Item 16 (XR5, shown) = Item 30 (XR4)





� EMBED PBrush  ���


Figure 12 - XR5 Actuator Assembly (Step 25)








� EMBED PBrush  ���


Figure 11 - 02XR4 Compressor Assembly (Step 19)





� EMBED PBrush  ���





Figure 8 - Marking the Inner Ring With Diffuser


Fully Open (Step 6)





� EMBED PBrush  ���


Figure 7 - Inner Ring and Rack Installation, Exploded View


(Step 5)








� EMBED PBrush  ���


Figure 1 - Outer Diffuser Ring Assembly, Exploded View (Step 1)





� EMBED PBrush  ���


Figure 13 - XR4 Actuator Assembly (Step 25)





FILE:  COMPRESSOR, MOTOR, DRIVE, GEARS








_1083672194

_1083758352.doc


�












_1084187619

_1084792929

_1084098311

_1083674518.doc
[image: image1.png]soue s







_1080135531

_1080370423

_1083565922

_1079962227

_1079963861

_1078732832

