9
 C0207A  19XR Split Ring Diffuser Actuator Alignment
2 of 9


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:   C0207A
	Date:  09/04/02
	Supersedes: C0207

	
	
	

	Title:  19XR Split Ring Diffuser Actuator Alignment

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	      Service Engineering

	Category: General
	
	  

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR chillers (XR5 and XR4 compressors) with PIC- II Controls and Split Ring Diffuser (SRD)

SITUATION: 

Some failures of diffuser actuator gears have occurred which have been attributed to its motor operating in a stalled condition, when the split ring diffuser hits a stop at either end of its travel.  In order to avoid this situation, a revised procedure is needed for field setup and calibration of the actuator to the diffuser hardware.  In addition, the procedure is adapted to include the XR4 compressor which was provided with the SRD option in early 2002.

SOLUTION:

(1) The actuator gear material has been modified (since June, 2001) to improve resistance to mechanical failure.  (2)  A detailed procedure is provided below which sets the actuator operating range to avoid stalling. 

Refer also to Service Bulletin C0206, 02XR Diffuser Ring Assembly and Set-up.  (Bulletin C9823, 02XR5 Diffuser Ring Assembly and Set-up, previously addressed this procedure, and it is superseded.)

The recommended procedure and its outcome are affected by the following variables:

•
Diffuser Rack Shimming - This determines whether or not the rack is against its clockwise mechanical stop (internal) when the diffuser rings are aligned to be fully open.  In machines shipped after November 1, 2001,  the assembly was shimmed to position the rack 5o from its clockwise mechanical stop when the diffuser is set to be full open.  In the field it is recommended that this shimming be done if the opportunity to shim in this manner is present (i.e., when the compressor assembly has been opened).  See Appendix A for serial number limits.

•
Outer Ring Pocket / Rack Fit - In XR5 machines produced before 2002, the diffuser outer ring’s pocket is sized closely to accommodate travel of the rack corresponding to full open to full closed diffuser travel, with little or no margin.  In XR4 machines and XR5s produced after Spring 2002, the hardware is changed so that margin will exist beyond the rack positions at both full open and full closed ends of travel.

•
SRD / IGV Schedule - The diffuser / IGV schedule which must be entered in the SERVICE / EQUIPMENT SERVICE / SETUP2 screen may need to be adjusted to avoid hitting the mechanical limits.  The nominal schedule values (current as of March 1, 2002) are listed in Tables 2 and 3 below (for 19XR4 and 19XR5 compressor builds, respectively).  The compressor build can be determined from the chiller model number, positions 10 - 12.  (For example, “4G5” in 19XR‑60604G5DGH64‑.)  

•
Controller & Software -.  This procedure is applicable to all versions of PIC software which support the SRD feature, including PIC-I for 19XR and either type of PIC-II controller (CVC or ICVC).  It is recommended that machines equipped with ICVC Version 2 software be upgraded to Version 3 (or later version), particularly if the diffuser shimming history is uncertain.

View the software version in a PIC- II controller in the SERVICE / EQUIPMENT SERVICE / CVC CONFIGURATION screen.  For example, ICVC Version 2 is shown as CESR 131294‑02, Version 3 as CESR 131294‑03.

Note: When upgrading a 19XR control with an ICVC controller from Version 2 to Version 3 software,  this procedure requires changes in schedule and possibly in actuator setup.

Field Setup Procedure.  

1. Shim Rack on Inner Diffuser Ring.  If the opportunity exists during the present servicing operation, reattach the diffuser actuator rack to the inner diffuser ring as directed in step 7 in referenced bulletin C0206:  First hold the diffuser rings to be aligned in a fully open position.  Then, before fastening the rack to the inner ring, place shim stock or feeler gages (.060” for XR5, .050” for XR4) between the rack and its clockwise mechanical stop.  Complete fastening the rack while it is held in this position. 

(This procedure will set the full open diffuser position to occur when the rack is 5o from its clockwise mechanical stop.)

If the compressor is not open and the opportunity does not exist for the rack to be shimmed in this manner, try to determine if the rack was previously shimmed in this manner.  Proceed with the following steps after shims have been removed and the compressor is closed and fully reassembled.

If the shimming step has been performed, document this fact for future reference.

2. Set Up Pinion to 0% Limit.  Rotate the SRD pinion shaft until it stops in the counterclockwise direction, then back off 5o clockwise.  This rotation may be measured by moving one tick mark on the “protractor” plate mounted on the pinion shaft seal housing (XR5) or chain guard (XR4).  (At this position the diffuser rings are expected to be aligned, fully open.)

This angle may also be gauged by the distance (arc) traveled at any radius using the expression {.087 ( radius}.  (At the OD of the shaft, where it enters the housing seal, this corresponds to approximately .070” or 1.8 mm.)  Mark the position.

Exception:  If (a) the control is an ICVC with software CESR131294-02 and cannot be upgraded to Version 03 at this time, and (b) the rack was not shimmed or it cannot be determined if it was shimmed: leave the SRD pinion shaft against its counterclockwise stop. (Refer to Appendix A for serial number cutoffs.)  This exception is to be avoided if possible.

3. Set Up Actuator to 0% Limit.  With the actuator shaft disconnected from the SRD pinion shaft, run the actuator to its 0% (4 mA) position.  This may be done, for example, by (a) using the Decrease command in CONTROLS TEST, Diffuser Actuator Test, (b) disconnecting the control signal from the actuator’s orange wire, or (c) unplugging power to the CCM module in the control panel.  For any of these it is necessary to have 115 vac power applied to actuator terminals L1 and L2.

4. Link Shafts.  Link the actuator and pinion shafts using the coupling (XR5) or the chain and sprockets (XR4), making sure that the pinion shaft does not rotate from the position set in Step 2.  Refer to Bulletin C0206.

5. Set Indicator.  Set the SRD pinion shaft pointer so that it indicates 0o (12 o’clock for XR5, 6 o’clock for XR4).

Note: In the case where the rack shimming cannot be determined, the indicator may end up 5o off diffuser full open.

6. Check SRD / IGV Schedule.  With power provided to all PIC control system components, access the SERVICE3 screen in PIC I, or SETUP2 screen in PIC II (CVC or ICVC) control systems, and scroll to “Diffuser Full Span mA”.  (All variable diffuser (SRD) actuators are shipped with a full scale milliamp value (corresponding to 100% or 185( rotation) stamped or otherwise marked on its label.)  Verify that this value is entered for the “Diffuser Full Span mA” value, and verify that the diffuser option is ENABLED.

The schedules listed in Tables 2 and 3 should be adjusted in accordance with Table 1.  (Note: The “unknown” shimming category should be avoided unless chiller production date and/or serial number place it at the transition defined in Appendix A.)

Check and modify in accordance with the above chart the values for “Guide Vane 25% Load Pt”, “Diffuser 25% Load Pt”, etc. at the three load points listed in the tables.  Note that for many cases the values recommended here may differ from the as-shipped condition.

7. Verify No Stall.  Restore the control signal (overridden, disconnected, or disabled in Step 3) to the actuator.  Remove the cover to the actuator, and monitor ac current in the yellow, black-striped, wire connected to actuator terminal X with an ammeter (clamp-on or in-line, 0 to 3 ac amps range).

With the control system powered up and guide vanes closed, the actuator should now rotate the pinion shaft clockwise toward the diffuser’s full closed position (the configured 25% Load Point position).

•
Current in the wire to terminal X should go to approximately 1.0 amps while the pinion shaft is rotating, then to 0 amps when the farthest clockwise position is reached.  If it does not, reduce the value of the SRD 25% Load Point in steps of 1% and repeat the test until the current shut off is observed.

•
Mark and measure the angular travel when rotation stops.  The total angular travel (start point to end point) should be within 2o of the “SRD Full Closure” value listed in Table 2 or 3, as adjusted per Table 1.  (Adjustments recommended for 25% load points apply to the SRD Full Closure angle.  3% is equivalent to 5o.)

•
Remove the control signal by disconnecting 2-wire connector J1 from the CCM board in the Control Panel.  Current in the wire to terminal X should go to approximately 1.0 while the pinion is rotating, then to 0 amps when the farthest counterclockwise position is reached.

•
Reconnect the power connector to CCM board at J1, remove ammeter, and reinstall actuator cover plate.

If the angular travel measurement is too short, the “Diffuser Full Span mA” entry (in the SETUP2 screen) may be modified for fine adjustment: increasing the value will result in increasing the travel.  (Note:  The controller does not accept a new value until the screen is exited.)

POLICY: 

N/A





APPENDIX A

Serial Number Applicability:

Shimming (Charlotte Factory) - 

Rule:  19XR5 chillers with serial numbers starting with 66169 were shimmed.  All 19XR4 chillers with SRD were shimmed.

Exceptions:  

The following are believed not to have been shimmed:  66189, 66190 ,66191.

The following are believed to have been shimmed:  65859, 66130, 66131, 66156.

ICVC Introduction with Software CESR 131294-02 (Charlotte Factory) - 

Rule:  Chillers with serial numbers after 66094 were equipped with the ICVC.

Exceptions:  

The following 19XR5s are believed not to have ICVC:  66189, 66191.

The following 19XR5s are believed to have ICVC: 65859, 65945, 65946, 66045 through 66050, 66060 through 66063, 66075.

FILE:    CONTROLS & WIRING





Internal Diffuser Ring Setup (Step 1)�
Rotation of Pinion Shaft (Step 2)�



Original Controller Software�



Adjustment to SRD % Values in Tables 2 or 3�
�
Shimmed 5o  per Step 1�
5o�
CESR 131294-03 


(after July 2002) 


or


XR4 with CESR 131294-02�
Use tables as shown�
�
�
5o�
all other cases, including field upgrades from


 CESR 131294-02 to -03�
Deduct 3% from 25% Load Pt. only�
�
Seated (not shimmed)�
0o�
CESR 131294-02�
Deduct 3% from 25% Load Pt. only�
�
�
5o�
all other�
Deduct 3% from all 3 SRD points�
�
Unknown�
0o�
CESR 131294-02�
Use tables as shown�
�
�
5o�
all other�
Deduct 3% from all 3 SRD points�
�



Table 1.  Schedule Adjustment Chart





�
SRD�
25% Load�
50% Load�
75% Load�
�
�
Full�
Load Pt.�
Load Pt.�
Load Pt.�
�
Comp�
Closure�
IGV�
SRD�
IGV�
SRD�
IGV�
SRD�
�
Code�
[o]�
[%]�
[%]�
[%]�
[%]�
[%]�
[%]�
�
509�
175�
0�
95�
28�
48�
42�
32�
�
508�
175�
0�
95�
28�
48�
42�
32�
�
507�
177.5�
0�
96�
28�
49�
42�
33�
�
506�
177.5�
0�
96�
18�
45�
39�
24�
�
505�
175�
0�
95�
23�
49�
42�
32�
�
504�
175�
0�
95�
23�
50�
42�
32�
�
503�
175�
0�
95�
28�
48�
42�
32�
�
502�
175�
0�
95�
28�
48�
42�
32�
�
501�
175�
0�
95�
28�
48�
42�
32�
�
599�
172.5�
0�
93�
17�
46�
32�
27�
�
598�
172.5�
0�
93�
17�
46�
32�
27�
�
597�
172.5�
0�
93�
17�
46�
32�
27�
�
596�
172.5�
0�
93�
20�
45�
43�
26�
�
595�
172.5�
3�
93�
24�
47�
41�
31�
�
594�
172.5�
0�
93�
18�
43�
34�
22�
�
593�
170�
0�
92�
17�
46�
32�
27�
�
592�
170�
0�
92�
17�
46�
32�
27�
�
591�
170�
0�
92�
17�
46�
32�
27�
�
589�
172.5�
0�
93�
20�
46�
35�
24�
�
588�
172.5�
0�
93�
20�
46�
35�
24�
�
587�
172.5�
3�
93�
25�
57�
42�
37�
�
586�
172.5�
0�
93�
20�
46�
35�
24�
�
585�
172.5�
4�
93�
18�
49�
39�
28�
�
584�
172.5�
0�
93�
20�
47�
39�
25�
�
583�
170�
0�
92�
20�
46�
35�
24�
�
582�
170�
0�
92�
20�
46�
35�
24�
�
581�
170�
0�
92�
20�
46�
35�
24�
�
579�
155�
0�
84�
20�
41�
32�
20�
�
578�
155�
0�
84�
20�
41�
32�
20�
�
577�
155�
0�
84�
22�
35�
42�
18�
�
576�
155�
0�
84�
17�
35�
31�
20�
�
575�
155�
0�
84�
20�
38�
37�
22�
�
574�
155�
0�
84�
20�
41�
32�
14�
�
573�
155�
0�
84�
17�
45�
31�
24�
�
572�
155�
0�
84�
20�
39�
36�
26�
�
571�
152.5�
0�
82�
20�
39�
36�
26�
�
569�
155�
0�
84�
18�
39�
38�
24�
�
568�
155�
0�
84�
18�
39�
38�
24�
�
567�
155�
0�
84�
18�
39�
38�
24�
�
566�
155�
0�
84�
18�
41�
33�
27�
�
565�
155�
0�
84�
18�
39�
38�
24�
�






Table 2.  19XR5  Compressor SRD / IGV Configuration Setup Values (sht. 1 of 2)








�
SRD�
25% Load�
50% Load�
75% Load�
�
�
Full�
Load Pt.�
Load Pt.�
Load Pt.�
�
Comp�
Closure�
IGV�
SRD�
IGV�
SRD�
IGV�
SRD�
�
Code�
[o]�
[%]�
[%]�
[%]�
[%]�
[%]�
[%]�
�
564�
155�
0�
84�
17�
39�
35�
24�
�
563�
155�
0�
84�
18�
39�
38�
24�
�
562�
155�
0�
84�
18�
39�
38�
24�
�
561�
152.5�
0�
82�
18�
39�
38�
24�
�
559�
137.5�
0�
74�
28�
38�
44�
22�
�
558�
137.5�
0�
74�
28�
38�
44�
22�
�
557�
137.5�
0�
74�
28�
38�
44�
22�
�
556�
137.5�
0�
74�
28�
38�
44�
22�
�
555�
137.5�
0�
74�
23�
37�
39�
20�
�
554�
137.5�
0�
74�
23�
37�
39�
20�
�
553�
140�
0�
76�
23�
37�
39�
20�
�
552�
140�
0�
76�
23�
37�
39�
20�
�
551�
137.5�
0�
74�
23�
37�
39�
20�
�
549�
137.5�
0�
74�
19�
39�
37�
27�
�
548�
137.5�
0�
74�
19�
39�
37�
27�
�
547�
137.5�
4�
74�
20�
38�
36�
20�
�
546�
137.5�
0�
74�
19�
39�
37�
27�
�
545�
137.5�
0�
74�
19�
39�
37�
27�
�
544�
137.5�
0�
74�
19�
39�
37�
27�
�
543�
140�
0�
76�
19�
39�
37�
27�
�
542�
140�
0�
76�
19�
39�
37�
27�
�
541�
137.5�
0�
74�
19�
39�
37�
27�
�
539�
120�
0�
65�
14�
26�
32�
18�
�
538�
120�
0�
65�
14�
26�
32�
18�
�
537�
117.5�
0�
64�
26�
39�
38�
26�
�
536�
117.5�
0�
64�
32�
38�
43�
24�
�
535�
117.5�
18�
64�
23�
37�
32�
18�
�
534�
117.5�
0�
64�
14�
26�
32�
18�
�
533�
117.5�
0�
64�
14�
26�
32�
18�
�
532�
117.5�
0�
64�
14�
26�
32�
18�
�
531�
115�
0�
62�
14�
26�
32�
18�
�
529�
120�
0�
65�
14�
26�
32�
18�
�
528�
120�
0�
65�
14�
26�
32�
18�
�
527�
117.5�
0�
64�
18�
39�
32�
24�
�
526�
117.5�
0�
64�
17�
38�
30�
23�
�
525�
117.5�
0�
64�
14�
26�
32�
18�
�
524�
117.5�
0�
64�
14�
26�
32�
18�
�
523�
117.5�
0�
64�
14�
26�
32�
18�
�
522�
117.5�
0�
64�
14�
26�
32�
18�
�
521�
115�
0�
62�
14�
26�
32�
18�
�






Table 2.  19XR5  Compressor SRD / IGV Configuration Setup Values (sht. 2 of 2)








�
SRD�
25% Load�
50% Load�
75% Load�
�
�
Full�
Load Pt.�
Load Pt.�
Load Pt.�
�
Comp�
Closure�
IGV�
SRD�
IGV�
SRD�
IGV�
SRD�
�
Code�
[o]�
[%]�
[%]�
[%]�
[%]�
[%]�
[%]�
�
4K7�
185�
0�
98�
17�
41�
35�
21�
�
4K6�
185�
0�
100�
14�
44�
33�
23�
�
4K5�
180�
0�
95�
15�
49�
32�
25�
�
4K4�
180�
0�
95�
17�
53�
34�
21�
�
4K3�
185�
0�
98�
17�
42�
37�
25�
�
4K2�
185�
0�
98�
17�
41�
37�
25�
�
4K1�
185�
0�
98�
17�
41�
37�
25�
�
4J7�
185�
0�
98�
17�
41�
35�
21�
�
4J6�
185�
0�
98�
17�
44�
34�
22�
�
4J5�
180�
0�
95�
14�
46�
32�
25�
�
4J4�
180�
0�
95�
14�
46�
32�
25�
�
4J3�
185�
0�
98�
17�
43�
37�
25�
�
4J2�
185�
0�
98�
17�
43�
37�
25�
�
4J1�
185�
0�
98�
17�
43�
37�
25�
�
4H7�
150�
0�
79�
17�
41�
34�
22�
�
4H6�
152.5�
4�
80�
18�
43�
34�
22�
�
4H5�
147.5�
0�
80�
22�
35�
33�
23�
�
4H4�
147.5�
5�
77�
14�
44�
32�
25�
�
4H3�
152.5�
5�
80�
14�
44�
32�
25�
�
4H2�
152.5�
5�
80�
14�
44�
32�
25�
�
4H1�
152.5�
5�
80�
14�
44�
32�
25�
�
4G7�
150�
0�
79�
17�
41�
34�
22�
�
4G6�
152.5�
4�
80�
18�
43�
34�
22�
�
4G5�
147.5�
6�
77�
13�
35�
29�
22�
�
4G4�
147.5�
6�
77�
14�
44�
28�
27�
�
4G3�
152.5�
6�
83�
20�
46�
33�
27�
�
4G2�
152.5�
6�
80�
14�
44�
28�
27�
�
4G1�
152.5�
6�
80�
14�
44�
28�
27�
�
4F7�
150�
4�
79�
16�
40�
32�
27�
�
4F6�
152.5�
7�
80�
19�
43�
34�
22�
�
4F5�
147.5�
8�
77�
14�
50�
28�
31�
�
4F4�
147.5�
7�
77�
14�
52�
28�
27�
�
4F3�
152.5�
0�
80�
9�
40�
24�
26�
�
4F2�
152.5�
9�
80�
17�
38�
31�
31�
�
4F1�
152.5�
9�
80�
17�
38�
31�
31�
�
4E7�
142.5�
6�
75�
17�
41�
32�
27�
�
4E6�
142.5�
7�
75�
19�
35�
33�
19�
�
4E5�
140�
5�
73�
14�
41�
28�
25�
�
4E4�
140�
5�
73�
14�
41�
28�
25�
�
4E3�
135�
9�
71�
17�
38�
31�
31�
�
4E2�
135�
9�
71�
17�
38�
31�
31�
�






Table 3.  19XR4  Compressor SRD / IGV Configuration Setup Values (sht. 1 of 2)








*





�
SRD�
25% Load�
50% Load�
75% Load�
�
�
Full�
Load Pt.�
Load Pt.�
Load Pt.�
�
Comp�
Closure�
IGV�
SRD�
IGV�
SRD�
IGV�
SRD�
�
Code�
[o]�
[%]�
[%]�
[%]�
[%]�
[%]�
[%]�
�
4E1�
135�
9�
71�
17�
38�
31�
31�
�
4D7�
142.5�
6�
75�
17�
41�
32�
27�
�
4D6�
142.5�
7�
75�
19�
35�
33�
19�
�
4D5�
140�
0�
73�
12�
35�
26�
18�
�
4D4�
140�
0�
73�
17�
30�
32�
17�
�
4D3�
135�
9�
71�
17�
38�
31�
30�
�
4D2�
135�
9�
71�
17�
35�
31�
27�
�
4D1�
135�
9�
71�
17�
35�
31�
27�
�
4C7�
132.5�
6�
69�
17�
41�
32�
27�
�
4C6�
132.5�
6�
69�
20�
30�
33�
15�
�
4C5�
130�
0�
68�
16�
38�
35�
25�
�
4C4�
130�
0�
68�
16�
41�
34�
20�
�
4C3�
125�
0�
65�
17�
38�
31�
31�
�
4C2�
125�
0�
65�
19�
27�
30�
15�
�
4C1�
125�
0�
65�
19�
27�
30�
19�
�
4B7�
132.5�
6�
69�
17�
41�
32�
27�
�
4B6�
132.5�
7�
69�
20�
30�
33�
15�
�
4B5�
130�
0�
68�
16�
38�
35�
25�
�
4B4�
130�
0�
68�
17�
35�
32�
19�
�
4B3�
125�
0�
65�
17�
35�
32�
19�
�
4B2�
125�
0�
65�
17�
35�
32�
19�
�
4B1�
125�
0�
65�
17�
35�
32�
19�
�






Table 3.  19XR4  Compressor SRD / IGV Configuration Setup Values (sht. 2 of 2)








*





*








_1080636184.doc


�












