1
1
SMB C0122A


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





Number:   C0208
Date:  03/08/02
Supersedes: (New)





Title:  Revised 19XR Impeller Torque Requirements





Author: Steve Bayes 

Dept: North American Commercial 



     Service Engineering

Category: General







Dealer Bulletin Number:  none                 



MODELS AFFECTED:
Carrier:  19XR chillers (02XR compressors)

SITUATION: 

Recommended impeller retaining bolt torque values have been revised.

SOLUTION:

The recommended impeller retaining bolt torque values are changed to:

Compressor:
XR2
XR3
XR4
XR5

Torque, ft-lbs
32 - 46
53 - 75
53 - 75
160 - 225

Torque, N-m
43 - 62
72 - 102
72 - 102
217 - 305

This supersedes values previously shown (a) in the list on page 98, in Start-Up, Operation, and Maintenance Instructions  for 19XR and XRV, Form 19XR-5SS (and prior revision 19XR-4SS), and (b) in Service Bulletin C9815.

POLICY: 

N/A


FILE:  COMPRESSOR, MOTOR, DRIVE, GEARS








_1074335172.doc


�












