3
C0209 
CVC Version 5 Software Release
2 of 3


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:   C0209
	Date:  08/01/02
	Supersedes: new

	
	
	

	Title:  CVC Version 5 Software Release

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR centrifugal chillers with CVC controller (PIC-II Controls, standard production until October 2001).

SITUATION: 

Either of the following symptoms may be observed with Version 4 CVC software:

•
In some VFD applications, line side current imbalance results from, or is aggravated by, the manner in which the drive draws current from the line to charge its DC bus. This may result in nuisance trips due to (a) unacceptably high current imbalance values, or (b) motor overload when the average current read by the ISM is at or below 100% design rated load amps.

•
Displayed Compressor Ontime inexplicably decrease to a lower value, sometimes to 0.  (This is extremely rare in the CVC.)

SOLUTION:

A new version of downloadable software for the CVC, Version 5, is now available to address these issues.

Hardware and Software Identification:

The CVC controller may be distinguished from the ICVC by inspecting the back of the plate on which the display is mounted as indicated in the following table.  (Open up the control panel door to view.)  Look for any of the following distinguishing features:

	CONTROLLER
	COLOR OF PLATE
	CEPL No.
	SOFTWARE No.
	OTHER MARKINGS

	CVC
	black
	CEPL 130286-05
	CESR 131158-0x
	CESO130045

CEPP130194-0x-04-01

	ICVC
	metallic
	CEPL 130445-01
	CESR 131294-0x
	"PIC-III" marking on back of green circuit board


Because of the possibility that a software upgrade may previously have been made, the best way to identify CVC module software version is by examining SOFTWARE PART # in the CVC CONFIGURATION screen, the last item in the SERVICE menu.  The new CVC software is CESR 131158-05, where "05" is the version number.  (The prior production version was Version 04, CESR 131158-04.)

No change in CVC hardware is required to upgrade from Version 04, which uses microchip (OTP) Version 68 or 69.  Upgrades from earlier CVC software versions, however, will require an OTP change.

Software Changes:
•
In the SERVICE / ISM (STARTER) CONFIG DATA / ISM_CONF screen, first line entry, Starter Type can now be set to 3, now uniquely indicating a VFD.  When combined with a new ISM (with Version 6 ISM software - see Bulletin C0215), this configuration will allow the system to utilize new logic intended to work specifically with VFDs.  The new logic will (a) permit setting allowable current imbalance to levels greater than 40% RLA, and (b) change the ISM's overload algorithm (based on line side current) so that it starts integrating overload when line side current exceeds 120% RLA instead of the standard 108%.  This allows the VFD to perform and act on motor overload calculations based on measured load side (motor) current and a lower threshold.

•
In the SERVICE / ISM (STARTER) CONFIG DATA / ISM_CONF screen, the maximum configurable current imbalance value is changed from 40% to 100%.  Values entered which are greater than 40% will be honored when Starter Type = 3 (VFD).  (For other starter types it will appear that the value can be set higher than 40%, but in those cases a 40% limit will be applied.)

•
Power down storage has been changed so that the following parameters will no longer be unintentionally set back to an earlier value or state: Compressor Ontime, the Pumpdown Lockout state, Service Ontime, Motor Kilowatt-Hours.

Usage:
Recommendations for field upgrades to CVC Version 5 will be managed through field service engineers and warranty managers.

In order to take advantage of the new feature benefits for VFDs described above, you must do all of the following:

•
Use a new ISM (Version 6 or later).

•
Use a CVC controller with Version 5 software or later.  
•
Configure for a Type 3 starter (in the ISM_CONF table).

Replacement Parts:

RCD will stock the following associated items: 

•
19XR04011605 - CVC controller downloaded with Version 05 software

•
19XR04012202 - ISM with Version 06 software

Related Service Bulletins:

The following other Service Bulletins discuss related material:

•
C0211   - 
ICVC Version 03 Software
•
C0215   - 
ISM Version 06 Software
POLICY: 

Administered by Warranty Managers.



















FILE:  CONTROLS & WIRING








_1086519084.doc


�












