1
2
SMB





SERVICE BULLETIN




Carrier Corporation





	Number:  C0214
	Date: 6/3/02
	Supercedes:  New

	
	
	

	Title:  19XR4 Stepped Bore Impeller & Nose Piece
	
	

	
	
	

	Author:  Alan Johnson
	
	Dept: North American Commercial

	
	
	     Service Engineering

	Category:  General 
	
	

	
	
	

	Dealer Bulletin Number:  N/A
	
	


MODELS AFFECTED:  

Carrier:   19XR Frame 4 Compressor


Serial Number(s):  ALL

SITUATION:

Some Frame 4 impellers have shown signs of being loose on the shaft.

SOLUTION: 

Factory and Field Action: Since about 3/02 frame 4 impellers have been machined with a reduced diameter step in the bore on the inlet end of the impeller.  This gives an interference fit on the front of the impeller in addition to the one on the back.  The stepped bore requires an impeller nose piece with a smaller diameter on the section that fits inside the impeller bore.

Part number format of stepped bore impellers – 02XR450224xx

Part number of nose piece for stepped bore impellers – 02XR45014001

File: Compressor, Motor, Drive and Gears

_984987439.doc
�



�
















