2
C0215       ISM Version 06 Software
3 of 3


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:   C0215
	Date:  08/01/02
	Supersedes: new

	
	
	

	Title:  ISM Version 06 Software

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR and 19XRV chillers with PIC-II Controls (CVC or ICVC controller)

SITUATION: 

In some VFD applications, line side current imbalance results from, or is aggravated by, the manner in which the drive draws current from the line to charge its DC bus. This may result in nuisance trips due to (a) unacceptably high current imbalance values, or (b) motor overload when the average current read by the ISM is at or below 100% design rated load amps.

SOLUTION: 

The software included in the Integrated Starter Module (ISM) used with PIC-II chiller controls has been revised from Version 4 to Version 6 to address these issues.

Identification:

The new module can be distinguished by its labels as follows:

	VERSION
	ORDER PART NO.
	CEPL No.

(HARDWARE)
	PROGRAMMED PART No.

	04 (prior)
	(19XR04012201)
	CEPL 130259-01
	CEPP 130173-04-04-01

	06 (new)
	19XR04012202
	CEPL 130259-02
	CEPP 130173-06-04-01


Hardware:
ISM software is not downloadable, so ISM modules must be physically replaced in order to upgrade in the field.  (ICVC/CVC controller upgrades are downloadable as always.)

Software Changes:
•
For VFDs, new Starter Type 3 is now made available to utilize logic intended to work specifically with VFDs.  (Starter types are set in the ISM_CONF screen of the CVC or ICVC.  Previously Type 2 applied to both VFDs and solid state starters.)

•
The overload (I2t) protection provided by the ISM for the line side of VFDs has been changed for Type 3 (VFD only) to begin accumulating I2t in any line phase when its current exceeds 120% of RLA.  (This value was previously 108%.  The 108% threshold will continue to be used for all non-VFD starters, Types 0 - 2, for motor protection.)  Primary overload protection of the motor is now relegated to the drive's software for VFD applications.

•
In VFD applications (Starter Type 3), the ISM will now honor current imbalance trip thresholds up to 100%, set in the ISM CONFIG screen.  Previously this was limited to 40%.  The 40% limit will still apply to non-VFD starters, Types 0 - 2.

The above changes collectively will reduce the operational limitations resulting from VFD-caused line side current imbalance.

Usage:
In order to take advantage of the new feature benefits for VFDs described above, you must do all of the following:

•
Use a new ISM (Version 6 or later).

•
Use a new controller: CVC with Version 5 software or later, or ICVC with Version 3 software or later (as shipped in production chillers starting in July, 2002).  ICVC and CVC module software version may be determined by examining SOFTWARE PART # in the ICVC (or CVC) CONFIGURATION screen, the last item in the SERVICE menu.  The matching ICVC software is CESR 131294-03, where "03" is the version number.  CVC software is CESR 131158-05, where "05" is the version number.  See also Service Bulletins C0209 and C0211.
•
Configure for a Type 3 starter (in the ISM_CONF table).

Otherwise, permissible combinations of controllers, configured starter types, and ISMs are summarized in the following table.  Note that in most cases a new Version 6 ISM may be used as a drop-in replacement for an existing ISM in any starter or VFD.  Conversely, it is not necessary to change an ISM unless there is a need to take advantage of the new VFD features.

	PERMISSIBLE COMBINATIONS

	Application
	ISM
	PIC-II

Controller
	Configured Starter Type

	non-VFD 
	any
	any (including 23XL)
	any

	VFD
	old (Ver 4)
	any
	2

	VFD
	new (Ver 6)
	new:

ICVC (Ver ≥ 03),

CVC (Ver ≥ 05)
	3


Recommendations for field upgrades to ISM Version 6 will be managed through field service engineers and warranty managers.  Field upgrades should be considered only for sites with a history of VFD line side current imbalance problems.  These sites have been typically faced with the dilemma of either being forced to run at less than 100% RLA (as displayed on the CVC or ICVC) or risk shutting down on motor overload trips (based on the ISM's overload).  (Note that changing a chiller's controller from CVC to ICVC, or the reverse, typically involves further considerations.)

Replacement Parts:

RCD will stock the following associated items: 

•
19XR04012202 - ISM with Version 06 software

•
19XR04011605 - CVC controller downloaded with Version 05 software

•
19XR04023403 - ICVC controller downloaded with Version 03 software

Related Service Bulletins:

The following other Service Bulletins discuss related material:

•
C0132A - ICVC - Product Information
•
C0209   - 
CVC Version 05 Software
•
C0211   - 
ICVC Version 03 Software
POLICY:  Administered by Warranty Managers.

























FILE: CONTROLS & WIRING


_1085833783.doc


�












