1
C0217 
19XR Line Voltage Oil Heaters
3 of 3
3 of 3


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation




[image: image2.png]FROM STARTER

Jl

CPT (115v)

]

2] 1

AAT
o
o

oL
" HEATER

BLK 2112

10 115Y
TRANSFORMERS
LINE VOLTAGE OIL HEATER WIRING
(WITH 115V CONTROL PWR)

2313





	Number:   C0217
	Date:  08/01/02
	Supersedes: new

	
	
	

	Title:  19XR Line Voltage Oil Heaters

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none
	
	


MODELS AFFECTED:
Carrier:  19XR centrifugal chillers with Frame 3 and 4 compressors.

SITUATION: 

A limited population of these chillers were shipped with oil heaters which are powered by line voltage (same voltage as oil pump) rather than 115vac control power. 

INFORMATION:

The intent of this bulletin is to make Field personnel aware that some chillers are equipped with line voltage oil heaters.  An incorrect assumption regarding the source of oil heater power may lead to equipment damage or personal injury.

19XR3 and 19XR4 chillers employing this design began production in January of 2002.  (Line voltage oil heaters allow the starter to use a smaller and less expensive control power transformer.)  However, the design was changed back to use the original 115v design [in mid-2002] due to production complexity issues.  The RCD parts manual has the part numbers for both styles.

[image: image3.png]21

S | F—o——®L0—e—at—awn
2¢  COMPRESSOR OIL HEATER W
10 TH-Gox —  — WIRING FOR 346V, 400V, 416V, l
/77 4BOV,480V & S7SV OIL PUMP
HD)
2 21 1
| —o— & —o O——(WHT————BLK— AN
ISOLATED
x OmerMinaL 1€
2 12
115v o
1c
2 | 13
co o
1c
SHOWN NITH
115V SUPPLY L 6LO
| GHHD
AS ®LY
L GRED>
WHTY -




Identification:

Determination can be readily made regarding whether an oil heaters is powered by 115v or line voltage from the label on the right side of the power panel.  See the two label images below.

[image: image4.png]CONTROL AN OIL HEATER®
BRMNCH € IRCUIT SELECTIOW CURRENT

01 L HEATER 2200 WATTS

VoL Thae 5150750 [e30- 150760
weense e )
RO SRRLYETREUTT |3 eS| T8 e
sty e 15w | ik 14 e
WLV SIPLTETREOT | 30 s | 15 s
SRR e | T ot | Th bEr
o1t pune
Jonseroner s
o Jo s [oo e
sesionvoursee | 3o | s | | & | >

o] s e @) wn

VOLTAGE RANGE | 200/ | 380/ |07/ | 220/ |3as¢

WINL AL 20 | amn | eis | za | aa0
RATED LoAD
APERAGE a3 | 205] 2,00 | 4.0 | 250
LOCKED ROTOR 5o
PERAGE 2.5 | 13,1 0 | 122

WOTOR. THERKALLY PROTECTED BY AUTO RESET DEVICE
WAIT 370 10 KINUTES BEFORE ATTENPTING RESTART

WIKINUN SUPPLY-CIRCUIT ANPACITT 15 ANPS MIK 14 4G
MAXIMUN SUPPLY-CIRCUIT OVER CURRENT PROTECTIVE DEVICE
15 4HPS TIME DELAT

—  aEEN L



[image: image5.png]miTey
TRCi0LOG1ES
i

CONTROL BRAICH CIRCIT SELECTION CURRENT

voLTaGe. sy 200
werice L L
I
MINSUPPLY CIRCUIT WPASITY | gl M4PS | 18 475
WAL SUPPLY GIRCUIT OUER CURRENT
PROTEETIVE 0¥ 1SR |15 s

OIL PUNP 40D OIL HEATER BRANCH CIRCUIT SELECTION CURRENT

DEsIeN voLTAGE [2207arsa]ssorarao|seararso 220sarso svarsrs)

vourace mwee | s | s | swr | 2z | asr

Wi Too | | W | Tw | W
oL puke
DI s | s | s | s | s

oL pune
s | a3 | 2asn | 2 | i | 250

oL e
Lotk s | 20 [ 1 | s | o | e

1L paTER mTTs
SRS SE | g00w | toanw | 1soon | 100k | 1800w

SRR CTRUIT
b surevy cracun]
iR 1
Tl GeLan

s | s | o | s

s sty cincn

THE DELAT)

—— SIS BT R T




Arrangement:

The line voltage oil heater is shown on the Control Panel schematic diagram as follows:

Perhaps a clearer presentation of how the oil heater is wired to the oil pump contactor terminals is as follows:

POLICY: N/A



� EMBED PBrush  ���





� EMBED PBrush  ���





� EMBED PBrush  ���





Label with Standard 115 Volt Oil Heater


(19XR5)





� EMBED PBrush  ���


Label with Line Voltage Oil Heater








FILE:  CONTROLS & WIRING








_1087910415

_1087911045

_1087903030

_1087904137

_1086519084.doc


�












