1
C0218     Potentiometers for Inlet Guide Vanes and Diffuser Actuators                                           5 of 5




SERVICE BULLETIN




Carrier Corporation





	Number:  C0218
	Date: 9/9/02
	Supercedes:  C0118B

	
	
	

	Title:  Potentiometers for Inlet Guide Vanes and

          Diffuser Actuators
	
	

	
	
	

	Author:  Scott Nieforth
	
	Dept:  North American Commercial

	
	
	         Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  None
	
	


MODELS AFFECTED:  

Carrier:  19XR Chillers with PIC II Controls

SITUATION: 

This bulletin provides part numbers for replacement guide vanes and diffuser feedback potentiometers and instructions for installing and calibrating them.  It corrects a wire number error in C0118B.

SOLUTION: 
Field Action: 

	In some PIC-II applications, mostly associated with constant light loading of the compressor, the inlet guide vane feedback potentiometer may wear out, resulting in erratic operation.  One indication of this problem is “Alarm 253 – Protective Limit, Guide Vane Calibration”.  This is 

caused when the signal from the feedback potentiometer is not within range of the Actual Guide Vane Position, as determined by the PIC-II software.

Before replacing the potentiometer, a Guide Vane Calibration can be performed in the Controls Test menu.  Additionally, the connection points for the feedback signal on the CCM module

terminal J4, pins 9 and 10 should be checked.

19XR PIC-II compressors use the following guide vane actuator:

               Description                    Actuator Part #    Resistance (ohms)    Feedback Pot Part #
 19XR, PIC-II Guide Vane, 110V    HF-26BB-030            10,000                   AD-718-704

Installation of the PIC-II guide vane potentiometer only is done as follows:

Caution: Terminals L1 and L2 in the diffuser actuator terminal box carry 115 V power.

1. Unplug the J11 connector on the CCM board.  Insert a jumper between the sockets for

      terminals 1 and 3 on the J11 wiring harness.

2. Enter the “Service” menu on the CVC, select “Control Test” then “Guide Vane Calibration”.  Monitor the inlet guide vane position on the CVC until clockwise motion of the guide vane actuator ceases and the guide vanes are fully closed.

3. Loosen set screws from potentiometer coupling.

4. Remove potentiometer from the coupling and bracket using a 9/16” open-end wrench.

Calibration Instructions for PIC-II Guide Vane Potentiometer:

5. Measure the resistance across terminals 1 and 2 of the new potentiometer.  See Diagram 2 for actuator terminal numbers.  Rotate the potentiometer shaft until the resistance reads approximately 150 ohms.  Install the new potentiometer noting the orientation of the terminals.  Be careful not to bend the bracket when tightening, as this will affect alignment.

6. Tighten the actuator shaft coupling screws, and install the potentiometer retaining nut finger tight.

7. Connect the wires to the feedback pot terminals as shown in Diagrams 1 & 2.  

8. Connect a voltmeter to measure the guide vane feedback signal on terminals 9 & 10 on J4 (upper) of the CCM.  Rotate the potentiometer until a signal of approximately 0.25 V is obtained.  The minimum acceptable signal is 0.20 V.  Tighten the potentiometer retaining nut while monitoring the guide vane feedback signal.  Check the potentiometer feedback signal after the retaining nut is tight to confirm that it is still 0.25V.

9. Remove the jumper wires from the J11 sockets and reinstall connector J11 to the CCM board.

10. Select “Yes” on the CVC guide vane calibration screen to begin the guide vane actuator calibration.  The CVC will display “Calibration Successfully Completed” when the process is complete. 

11. If the calibration fails, either the potentiometer voltage was set too low or the guide vanes were not fully closed when the potentiometer nut was secured.   Loosen the potentiometer retaining nut and repeat steps 5 – 9.

Diagram 1:  Potentiometer Connections (View of Actuator Looking Down)

[image: image1.jpg]



Diagram 2:  Side View of Actuator


[image: image2.jpg]


                                [image: image3.jpg]


            


       AD-718-703 Potentiometer                                            AD-718-704 Potentiometer
17EX, 19EX, 19XR, 19XL PIC-I, and 19XR PIC-II Actuators:

            Description                          Actuator Part #  Resistance (ohms)  Feedback Pot Part #
   19XR, PIC-II Diffuser, 110V           HF-26BB-029             120                    AD-718-701

   19XL Guide Vane, 24V                  HF-26BB-024             120                    AD-718-701

   17EX, 19EX Guide Vane, 110V   HF-26BB-025             100                    AD-718-702

   19XR, PIC-I Guide Vane, 110V     HF-26BB-026             100                    AD-718-702

Note – the actuators for the 19XL and the 19EX/FA/EF are not interchangeable.  The 19XL 

actuator uses 24 volts AC as its power source.  The actuators for 19EX/FA/EF chillers are similar but they use a 120 volt power source.

Potentiometer Setting:   2 – 5 Ohms resistance between actuator terminals 4 & 7 when the

                                       actuator is in the full clockwise position.

PIC I Guide Vane Actuator and PIC II Diffuser Actuator “Open” and “Close” Signal:

Check “open signal” between actuator terminals ‘3’ and ‘X’:

To check the guide vane actuator triac driver, or “black box”, “open” signal for proper orientation and calibration, first check the DC current set point of the triac.  The actuator should begin to open when a 4.0 mA signal is received from the PSIO or CCM.

1. Turn off control power and disconnect the following wires from the vane actuator.

Terminal 3 – remove the blue/black wire (open signal wire)

Terminal 2 – remove the red/black wire (close signal wire)

Terminal X – remove the yellow/black wire (common wire)

2. Install a digital ammeter in series with the 4-20 mA DC signal to the actuator in order to measure the current signal from the PSIO or CCM to the actuator. 

a) PIC I guide vane actuator only: Separate the black wire leading from PSIO terminal J6, pin 52 from the orange wire inside of the guide vane actuator terminal box.  Install an ammeter in series between these wires.  Set the meter to “amps DC”.

b) PIC II diffuser actuator only: Separate the black wire connected to CCM terminal J8, pin 3 from the orange wire in the diffuser actuator terminal box.  Install an ammeter in series between these wires.  Set the meter to “amps DC”. 

3. Attach an ohmmeter to read the resistance between terminals ‘3’ and ‘X’ (the blue/black wire and the yellow/black wire).  At this point, the meter should read infinite resistance.

4. Turn on the control power

5. Access the chiller Controls Test and set the control to open the guide vanes.  Watch both the ammeter and the ohmmeter.  As soon as the current signal from the PSIO of CCM increases to 4.0 mA, the resistance should go to zero.  This indicates that the actuator is trying to open.

Note – The triac “steps” the actuator open.  When a 4.0 mA signal is applied, the triac may only close the open vane switch for a moment, and then open up again, stepping the actuator open according to the current signal.

6. If the triac does not start closing the vane switch at 4.0 mA, but does close at a higher current signal, then the starting point adjustment screw should be turned CCW a small amount.  This decreases the current set point at which the triac will start to open the guide vanes or diffuser.  The starting point adjustment screw is located under a piece of tape on the top of the “black box”.

7. Command the guide vanes or diffuser to close completely and then open them again from the controls test screen.  Watch the current signal from the PSIO or CCM and the resistance between actuator terminals ‘3’ and ‘X’ .  Check that the resistance goes to zero when the current signal reaches 4.0 mA.

8. If the triac cannot be calibrated to the above settings, then replacing the actuator is recommended.

Check “close signal” between actuator terminals ‘2’ and ‘X’:

9. To ensure that the close vane signal from the triac is working properly, reconnect the voltmeter to read the resistance between actuator terminals ‘2’ and ‘X’.  When the actuator is closing, this resistance should read zero.  When the guide vanes are opening, the reading should be infinite.  There are no means to calibrate for the close signal.

10.  If the close vane signal is not working properly, a new actuator is recommended.

11.  Remove the instrumentation and reconnect the actuator wires following completion of these tests.



	








Brown/White


(Terminal 8)





Brown/Black


(Terminal 7)





Brown


(Terminal 4)





Brown/White


(Terminal 1)





    Brown


(Terminal 2)





Brown/Black


(Terminal 3)








FILE:  Controls and Wiring

_984987439.doc
�



�
















