1
2
SMB C0122A


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:   C0220
	Date:  10/28/02
	Supersedes: (New)

	
	
	

	Title: 23XL Slide Valve Shaft Seal Ring 

	
	
	

	Author: Scott Nieforth 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  None                 
	
	


MODELS AFFECTED:
Carrier:  23 XL Screw Chillers

SITUATION: 

     The 8TC0057C slide valve shaft seal ring has been replaced by part number 8TC1047.  Orders for the 8TC0057C will be automatically converted to 8TC1047 by RCD.  The new part is made of a polymer filled PTFE with high wear resistance.  The 8TC1047 has the same dimensions as the seal ring it replaces.

     The surface finish of the slide valve shaft should be inspected before installing a new seal ring.   Service Bulletin C9827 specifies a 22 micro-inch (.55 micro-meter) finish.  Install the seal ring on the slide valve shaft first with the open end facing the slide valve per Service Bulletin C9803A.  Position the 1TC0226C slide seal adapter over the seal ring and uniformly tighten the four 8TC0092C (M6 X 1 X 16) socket head cap screws to guide the shaft seal ring into position. 

                      [image: image2.jpg]



8TC0092C               M6 X 1 X 16 Socket head cap screws





1TC0226C Slide Seal Adapter





8TC1047 Slide Valve Shaft Seal Ring








FILE: Compressor, Motor, Drive, Gears


_1083758842.doc


�












