1
C0302
Thermal Dispersion Flow Switch
3 of 3


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation




[image: image2.png]CHLLED WATER

CONDENSER WATER

CCM

33 (LOWER)
13
in
o[ #x
E » FLow
RESISTOR 16 SWITCH
e
HIEEA Ku.o.
g P
ResisToR —
19
0
o[ #x
$
- o FLow
RESISTOR 2| o g
= 23
HIEEA Ho.
g o] I





	Number:   C0302
	Date:  02/07/2003
	Supersedes: (New)

	
	
	

	Title:  Thermal Dispersion Flow Switch

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR and 23XL chillers, especially (but not exclusively) with PIC-II CVC Controller

SITUATION: 

The subject chillers equipped with CVC controllers were provided with water side differential pressure transducer pairs for flow detection (freeze protection) as standard equipment.  In the late 1990s these transducers in this application proved to be problematic and unreliable for a number of reasons.  The need exists for a field retrofit substitute which is reliable and not significantly affected by sediment, scaling, or deposits which are common in water side plumbing.  This bulletin describes a thermal dispersion flow switch which can meet this need.

If a chronic water side transducer problem exists at a jobsite, it is likely that it will be more cost effective to replace the four transducers with two flow switches as described in this bulletin than to replace or recalibrate the existing transducers on a periodic basis.

19XR chillers equipped with ICVC controllers do not rely upon these water side transducers, however their systems may be optionally equipped with the same switch for flow detection.

SOLUTION:

Material Needed (for each water system)

•
switch: IFM Efector Inc. model ST-0572 (RCD Part #ST0572).  See Figure 1 below.

•
cables: RCD (and IFM Efector Inc.) part #E18005 (15 ft length) or RCD part # E18006 (30 ft length).  Check that the cables provided have four wires (with brown, blue, black, and white insulation) at the open lead end.

•
Note: In a typical installation there will be two sensor and sensor cable sets, one for the chilled water system and one for the condenser water system.

Water System Interface (for each sensor):

Install in a ¼” NPT tapped hole such that the sensing tip of the switch extends into or is at the edge of the flow stream (i.e., not recessed in a branch cavity).  When used as a direct replacement for a waterside pressure transducer, install in place of the ¼” NPT Schrader adapter in the waterbox nozzle to which a waterside pressure transducer has been connected.  

For chillers which have additional couplings which would prevent adequate penetration of the sensor, or which have thick or cast nozzles (e.g., 23XL waterboxes), install the flow dispersion switch in a ¼” NPT tapped hole elsewhere in the system piping where the pipe wall is thin enough to permit adequate penetration.  It does not matter if the flow dispersion switch is on the inlet or outlet side.  

Electrical Interfaces (for each sensor):

•
Note: In a typical installation there will be two sensor and sensor cable sets.

•
At the switch, connect one of the cables specified above, which has a sealing threaded M12 connector, to the corresponding sensor terminal.  Refer to Figure 1.

•
Terminate the other end of each cable in the chiller Control Panel.
•
24vac Power Supply (in the control panel):  For recently produced 19XR chillers the brown and blue wires from each cable may be readily connected to terminals 1 and 2 of the 6-screw terminal block in the control panel (connected to red and gray wires, respectively).  For control panels not so equipped, consult the schematic to determine a convenient location to splice these wires into either of the standard 24vac supplies: (a) on the load side of circuit breaker CB1, joining to the red and gray leads, or (b) on the load side of circuit breaker CB2, joining to the yellow (or black) and brown leads.

•
Switch Input Wiring (control panel):  The black and white wires from each sensor cable are to be wired as the appropriate switch shown in Figure 2.  The switch in the cooler loop connects to CCM J3 17-18, and the switch in the condenser loop connects to CCM J3 23-24.  Add resistors as shown (3.3k or 3.9k ohm resistors will work just as well, as long as the values are equal).  An open switch should indicate no flow.

•
Provide strain relief for the cable at the switch end and at the control panel end.  The wires within the cable are AWG 22, which is smaller than standard chiller control wiring.

Controller Configuration and Usage:

•
For ICVC controllers with Version 03 or later software, in the Equipment Service / Options screen set Flow Delta P Display (line 14) to Enable for the calibration procedure described below.  After calibration, change the selection back to Disable.  (With 4.3 k ohm resistors installed, a “phony” delta p value of approximately 20 psi will appear when the display option is Enabled.)

•
With the switches open or disconnected, calibrate (set) the zero point values in the Status, HEAT_EX screen for Chilled Water Delta P and Condenser Water Delta P by selecting each of these lines then pressing Enter.  This will assure that the no-flow differential will be interpreted as zero taking into account tolerance differences between the resistors.

POLICY: 

Contact your warranty administrator if additional guidance is needed.

[image: image3.png][ H w2
- L
Liz 534,1
WRING DIAGRAM 2

fe— 236
]

4
(35)
M12x 4PN MALEJ J
o %
ifmefector 114 npT—%
Srores
L7
Nyl

Rz





� EMBED PBrush  ���


Figure 2.  Recommended CCM Connection Schematic





� EMBED PBrush  ���


Figure 1.  Thermal Dispersion Flow Switch











FILE: CONTROLS & WIRING


_1103117053

_1105170467

_1074335172.doc


�












