1
C0219
19XRV VFD Wiring Changes
2 of 2


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:  C0304 
	Date:  2/11/03
	Supersedes: C0125

	
	
	

	Title:  19XR Compressor Thrust Pad Removal Holes

	
	
	

	Author: Scott Nieforth
	Dept: North American Commercial Service Eng'g

	
	
	

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none
	
	


MODELS AFFECTED:
Carrier:  19XR Compressors
SITUATION: 

     This bulletin summarizes changes to the 19XR Frames 2, 4 & 5 high-speed thrust bearings.  This bulletin also applies to replacement parts for earlier 19XR Frame 3 compressors with high-speed journal bearings. 

      Six .094” holes that were centered in the .375” diameter adjusting pad recesses were removed from all 19XR compressors with journal bearings on 5/24/99.  The following part numbers were affected:

02XR25003901

02XR45003601




02XR35003001

02XR55008801

      The .094” diameter holes were not oil passages.  The function of the six .094” diameter holes was to allow a wire to be inserted behind the adjusting pads for removal.  The adjusting pads can be removed with a small screwdriver or a magnet so the .094” holes are unnecessary.  

      The absence of .094” holes in the thrust bearing pockets of 19XR thrust bearing housings is not a defect.  The following photographs show an example of this change.  

          [image: image2.jpg]


                                         [image: image3.jpg]



               02XR45003601 Rev. 3                                                    02XR45003601 Rev. 4 

.094” holes














FILE:  COMPRESSOR, MOTOR, DRIVE, GEARS

_1074335172.doc


�












