1
C0307
PIC-II Reset Faults 213, 214, 147, 148
6 of 6


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation




[image: image2.png]~

——

- 0

I B S . T R R EX R

:@ [a) ®2§§E

D
laan sty
QoD

comt
cea

GGG
s39v1T0A 31

XY XY LU LIS 08 AL 7L
WZWULIS WA 3l dvas 3804

SLNAN LOWINOD

QN0 GaHVS TAIVIDALYT

g

DISCRETE CONTROL CONTACTS
420 s out

TRE M L0 COND EVAP SHUNT TRANS
SPARE VFD  ALARM FAN FAN POMP PUMP TRP

T m
SwAsE

1R

I}

STa1_cin

o

INTEGRATED STARTER MODULE

o





	Number:   C0307
	Date:  03/24/2003
	Supersedes: (New)

	
	
	

	Title:  PIC-II Reset Faults 213, 214, 147, 148 

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR and 23XL chillers with PIC-II controls

SITUATION: 

Confusion exists in interpreting PIC-II “module reset” fault codes 213, 214, 147, and 148.  The intent of this bulletin is to provide more information regarding these fault indications and possible remedies.  

In addition, nuisance ICVC resets (code 214 or 148) which become more frequent as time passes are known to be a problem in ICVCs with Version 2 and 3 software.

EXPLANATION:

ISM Resets 

•
Fault Messages:

(a) Alarm 213 (machine running with Autorestart not enabled): 

“Protective Limit - Starter Module Reset”

“Starter Module Power On Reset While Running”

(b) Alert 147 (machine running with Autorestart enabled): 

“Autorestart Pending – Starter Module Reset”

“Starter Module Power On Reset While Running”

Note: The above two conditions indicate exactly the same fault.  Alert 147 will appear instead of Alarm 213 if the Autorestart After Power Failure option is enabled.  The alert status permits the machine to restart in accordance with this option.

•
Basic Indication: Either message indicates that the control power voltage level within the starter or VFD has dropped to a level which is in danger of allowing critical contactor or relay coils to drop out.  If the control power voltage input (nominally 115vac) drops below approximately 95vac, the fault is triggered.

•
How It Works:  This fault is detected solely by the ISM.  The nominal 115vac ISM power input (not the 3-phase voltage-sensing input) to J1 1-2 is transformed down to 24vac inside the ISM for its internal power supply.  The voltage on this 24v secondary circuit is internally monitored such that, if it drops below a threshold (approximately 20 vac), the fault is triggered.  The trip will occur within a few cycles of the trigger condition being detected.

Any electrical event which would similarly pull down or distort the internal 24vac, or which imposes significant electrical noise in the ISM’s circuitry, will cause the fault.  This may include (a) transient dips or sags, including those possibly resulting from high EMI fields, in the 115vac input, (b) waveform distortions or harmonics in the 115vac input, (c) shorts or excessive current draw from any of the discrete input channels (all ISM J2 terminals, including contact circuits for remote start, ice build, 1M Aux input, 2M Aux input, Spare Safety input, and Starter Fault), (d) poor grounding (especially with VFDs), or (e) any other situation which would abnormally draw down the ISM’s internal power supply or introduce electrical noise into the ISM’s circuitry.  ISM terminals are shown in Figure 1.

An ISM reset can also be generated through software.  At this time there is no reason to believe that this is a factor in ISM resets observed in the field.  

•
Troubleshooting and Remedies:  

· The ISM is grounded only through the four corner metal standoffs and fasteners passing through those standoffs.  Assure that there is a solid connection from the ISM at these standoffs through the starter or VFD, to the chiller unit frame ground and to earth ground.

· Instrument the starter’s line power supply to verify presence, magnitude, and characteristics of any voltage dips, particularly when other equipment at the site starts up.  Waveform or power quality abnormalities can be analyzed at the jobsite using power analyzer instrumentation.  Expect to have to make an investment of learning time before setting up this equipment so that it can detect the events which can cause a 213/147 fault.  If the problem is found to be in the supply voltage, add a constant voltage transformer, regulation transformer, or uninterruptable power supply (UPS) to the 115v line providing power to the ISM.

· Monitor the 5v communication input channels (SIO bus) at J7 for electrical noise when the chiller is running, preferably with an oscilloscope.  Use the measurement between SIO common (middle terminal “B”, the black wire) and equipment ground as a baseline for measuring noise amplitude and the effect of changes made.  If significant noise is found to be present, try the following and measure the effect on the noise amplitude: 

· Try disconnecting SIO common (the black wire) at the ISM.  If this makes a significant difference and a CCN network is installed, reconnect and check the effect of disconnecting the CCN common (middle terminal) in the chiller control panel.  Check the routing of CCN cable(s) to assure that they are well removed from the VFD.  Consider adding an isolating component such as Carrier’s RS‑485 Repeater module in the communications circuit close to the ISM.  If the unit is equipped with a hot gas bypass valve, check the effect of valve operation on the noise level.  If significant, add a snubber on the load side of the hot gas bypass relay (in the chiller power panel).

· Pass the SIO bus communications cable through several Ferrite Beads (small chokes, inner diameter 0.5 – 0.75 inches).  Do this at the ISM end of the cable, and loop the cable through the beads such that each bead has at least 2 passes of cable through it.

(I)CVC Resets:

•
Indications:

(a) Alarm 214 (machine running with Autorestart not enabled): 

“Protective Limit - Power Loss”

“Control Power Loss While Running”

(b) Alert 148 (machine running with Autorestart enabled): 

“Autorestart Pending – Power Loss”

“Control Power Loss While Running”

Note: The above two conditions indicate exactly the same fault.  Alert 148 will appear instead of Alarm 214 if the Autorestart After Power Failure option is enabled.  The alert status permits the machine to restart in accordance with this option.

(c) When chiller is in OFF mode (no alarm or alert), screen goes blank, Carrier oval appears, followed by self-test and default screen display.

•
Basic Indication: Any of the above three “reset” conditions indicate that the control power voltage level at the master controller (CVC or ICVC) in the chiller control panel dropped to a level at which the controller could no longer function properly.  This will happen every time control power is lost or turned off, then restored.

•
How It Works:  This fault is detected solely by the (I)CVC - it has nothing to do with the ISM.  The nominal 24vac (I)CVC power input to J1 4-5 (yellow and brown wires), is internally monitored such that, if it drops below a threshold (approximately 12 vac), the fault is triggered.  In most cases this power originates in the starter where line voltage is transformed to 115v, then in the chiller power panel it is transformed from 115v to 24v.  

It has also been observed that poor grounding of the control panel, in which the (I)CVC is mounted, can make the module more susceptible to resets.

However, it should be noted that there are other conditions unrelated to power quality which will also produce the same resets.  For example, if the software running in the module hangs up for any reason, it will trigger a reset.

>>> It has been determined that the ICVC (not the CVC) with Version 2 or 3 software is susceptible to such software-induced resets, most likely due to a software flaw.  In this case the reset is not related to voltage at all, despite the displayed message (if any).  Appearance of the resets may increase in frequency with time.  In some cases they are aggravated by connection to a CCN communication network.  At the time of this writing, there is a high priority effort underway to uncover and eliminate the root cause of these “phony” resets.

•
Troubleshooting and Remedies:  

See the troubleshooting/remedy flowchart, Figure 2.  Notes referred to within the figure are listed below.

Note 1.
Check to see if the reset corresponded with any known power outage as indicated by other equipment which may be on the same circuit.  If you have an ICVC with Version 3 or earlier software, and if the reset seems to have been detected only by the one chiller, then a software induced reset is to be suspected.

Note 2.
Assure that the ICVC has a solid connection to building ground through the chiller unit frame ground.

Note 3.
As of this writing, Version 4 (which resolves the software reset problem) is not available.

Note 4.
The quickest but least satisfactory remedy is to enable the Autorestart After Power Failure feature if site requirements permit and if not already enabled.  With this approach, a reset while running will still shut down the chiller, but no manual intervention will be required to restart.  This will not be a satisfactory remedy if the resets occur frequently.  (The frequency of the resets will not be affected.)

Note 5.
Convert the system to utilize a CVC controller (with Version 5 software) instead of an ICVC. This requires two changes.  First, relocate the evaporator saturation temperature sensor input (from CCM terminals J4 11-12) to be a spare temperature sensor.  Connect as Spare Temperature Sensor #1 across CCM terminals J4 25-26.  Configure “Spare Temp #1” in the SERVICE / EQUIPMENT SERVICE / SETUP1 table as Enable = 3, Limit = 33o F or 1o C.

Note 6.
Replace the ICVC with another ICVC (preferably with software version 3).  In most cases this will significantly although temporarily reduce the frequency of nuisance resets.

POLICY: 

Contact your warranty administrator if additional guidance is needed.


 
� EMBED PBrush  ���


Figure 1. ISM Terminals














Resolve power quality issues with power provider or facility





Check grounding (See Note 2.)





Did a real power interruption occur?














Y





Is primary nuisance that chiller needs to be manually restarted?








Does site need specific ICVC features (vs. CVC)?





(Nuisance lies in frequency of resets.)





Enable Autorestart feature.  (See Note 4.)





Figure 2.  ICVC Reset Remedy Decision Flowchart





(See Note 1.)





(See Note 3.)





Does site have a problem with Autorestart?





N





Y





Replace with CVC (See Note 5.)

















Is ICVC software Version 4 or later available?





Replace with ICVC (See Note 6.)





Y





N














Download new ICVC software version.














N





N








Y











Y





N











FILE: CONTROLS & WIRING


_1074335172.doc


�












_1107842369

