3
C0402 
19XR Liquid Isolation Valve Problem
4 of 4


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation





	Number:   C0402
	Date:  01/23/04
	Supersedes: C0003

	
	
	

	Title:  19XR Liquid Isolation Valve Potential Problem

	
	
	

	Author:  Brice Auten and Alan Johnson
	
	Dept: North America Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  19XR centrifugal with frame 2, 3 &4 heat exchangers

PURPOSE:

To inform the field of a potential problem with the crossover isolation valve between the float chamber and the cooler on frame 2,3, & 4 chillers.  This revision provides information about hard to open valves.

INFORMATION:

Several reports have been received about 19XR chillers that surge immediately after startup or trip quickly on low refrigerant temperature. First impressions have been stuck floats, low refrigerant charge, non-condensables in the chiller, & inadequate water flows. While all of these items are relatively easy to verify, it can be, in some cases, difficult and very expensive to determine which one is causing the problem.

ACTION:

Another possibility is a closed isolation valve.  The valve used (part # EP71BA-571) has a brass cap cover that fits over a steel valve stem. Rotation direction to open and close the valve is marked on the cap but is usually unreadable after painting.  It is possible to turn the cover cap and have the appearance that the valve is open while in fact, the valve is still closed.  Without too much effort the cover cap can be rotated and enlarge the slot that fits over the stem.  There will still be a resistance when turning the cover, adding to the belief that the valve is turning with the cover. There have also been instances where the valve stem broke allowing the cap and stem to turn without moving the valve.  Careful analysis of a “locked” valve returned to the CAT clinic revealed that the ball was “hydro-locked in the closed position by refrigerant liquid, captured between the ball and the valve body.

If the above symptoms are encountered, first check the valve to verify that it is open by removing the cover and turning the valve stem.  Pictures are attached.  If the stem is hard to turn remove the insulation and pack the valve body in ice.  Chilling the refrigerant trapped in the valve body has allowed the valve to be opened without breaking the stem.  The final picture shows a Teflon seal that has been damaged, possibly by the hydraulic pressure.  Be certain that a valve isn’t leaking through, the first time it is closed for isolation, if it has been “hydrolocked” and then opened by chilling. 

In September, 2003, the factory switched to Mueller valves.  Mueller plans to add an internal vent in about April, 2004 that will prevent “hydrolocking”.

[image: image2.jpg]Yot




[image: image3.jpg]



[image: image4.jpg]





[image: image5.wmf]Teflon seal has

been damaged.


POLICY: 

N/A







Notice stripped area under cap cover from turning in wrong direction. 





Cover Cap – Notice rotation direction indicator on cover. Remove this cover to open/close valve.





Open/Close the valve here – not with the cap shown in the next picture.

















FILE: COOLER, CONDENSER, ECONOMIZER


_1086519084.doc


�












_1011183395.doc
[image: image1.png]





Teflon seal has been damaged.












