[image: image1.png]



Remote Air-Cooled Condenser

Service Manual

09AW/AZ001-020

1 to 20 Nominal Tons

09AZV091-182

90-200 Nominal Tons

This document is not intended for general distribution.  It is to be used by Carrier Distributor Service or Carrier Commercial Service personnel only, and may not be distributed to individuals not employed within these organizations.  This document is intended as a guide only.  There is no guarantee of the accuracy of the information contained within.

[image: image2.png]




Table of Contents

3Safety Considerations


3Introduction


609AW/AZ001-024 Model Number Significance


809AW/AZ001-024 Factory Installed Options


809AZV091-182 Model Number Significance


909AZV091-182 Factory Installed Options


10Serial Number Significance


10Application


10Head Pressure Control


11Fan Cycling


11Variable Speed Fan Control


11Mounting Information


1109AW,AZ001-020


1109AZV091-182


11Leg Extension Kits


1109AZV091-182


12Refrigerant Circuit Information


13Literature


14Service


14Condenser Fan System, 09AZV091-182


15Condenser Fan Blades


15Condenser Fan Motor


16Head Pressure Control




Safety Considerations

Installing, starting up, and servicing this equipment can be hazardous due to system pressures, electrical components, and equipment location (roof, elevated structures, etc.).  Only trained, qualified installers and service mechanics should install, start-up, and service this equipment.

When working on this equipment, observe precautions in the literature, and on tags, stickers, and labels attached to the equipment and any other safety precautions that apply.  Follow all safety codes.  Wear safety glasses and work gloves.  Use care in handling, rigging, and setting this equipment, an in handling all electrical components.

	WARNING

	Electrical shock can cause personal injury and death.  Shut off all power to this equipment during installation and service.  There may be more that one disconnect switch.  Tag all disconnect locations to alert others not to restore power until work is complete.


	WARNING

	DO NOT VENT refrigerant valves within a building.  Outlet from relief valves must be vented outdoors in accordance with the latest edition of ANSI/ASHRAE (American National Standards Institute/American Society of Heating, Refrigeration and Air Conditioning Engineers) 15 (Safety Code for Mechanical Refrigeration).  The accumulation of refrigerant in an enclosed space can displace oxygen and cause asphyxiation.  Provide adequate ventilation in enclosed or low overhead areas.  Inhalation of high concentrations of vapor is harmful and may cause heart irregularities, unconsciousness or death.  Misuse can be fatal.  Vapor is heavier than air and reduces the amount of oxygen available for breathing.  Product causes eye and skin irritation.  Decomposition products are hazardous. 


	WARNING

	DO NOT attempt to unbraze factory joints when servicing this equipment.  Compressor oil is flammable and there is no way to detect how much oil may be in any of the refrigerant lines.  Cut lines with a tubing cutter as required when performing service.  Use a pan to catch any oil that may come out of the lines and as a gage for how much oil to add to the system.  DO NOT re-use compressor oil.  DO NOT leave refrigerant system open to air any longer than necessary.  Seal circuits being serviced and charge with dry nitrogen to prevent oil contamination when timely repairs cannot be completed.


Introduction

This information should be used with the Installation Instructions for these machines.  Follow all safety precautions and procedures.

The 09AW/AZ001-020 condensers were introduced in March 1999, replacing the 9AB product offering obsoleted in December 1998.  The 09AZ006-016 models are specifically designed to mate with Carrier’s 50BZ VPAC product shown in the table below.  

	VPAC
	Condenser

	50BZN006
	09AZ*006

	50BZN008
	09AZ*008

	50BZN012
	09AZ*012

	50BZN014
	09AZ*014

	50BZN016
	09AZ*016


Note: “*” denotes a variable character, H, L, V, or W.

The 09AW/AZ001-020 condensers are special condensers produced by Carrier Heat Transfer Products.  Below is a cross-reference chart of units produced between March 1999 and December 2001:

	Carrier Part Number
	Carrier HTP Part Number
	Carrier Part Number
	Carrier HTP Part Number

	09AWL001
	CDL-001
	09AZH006
	CDS-005 (14 fpi)

	09AWL002
	CDL-002
	09AZH008
	CDS-010 (12 fpi)

	09AWL003
	CDL-003
	09AZH012
	RCS-015 (8 fpi)

	09AWL004
	CDL-004
	09AZH014
	RCS-016 (10 fpi)

	09AWL006
	CDL-006
	09AZH016
	RCS-016 (14 fpi)

	09AWL008
	CDL-008
	09AZL006
	CDL-006 (10 fpi)

	09AWL012
	CDL-009
	09AZL008
	CDL-008 (14 fpi)

	09AWL014
	RCL-013
	09AZL012
	RCL-014 (10 fpi)

	09AWL016
	RCL-014
	09AZL014
	RCL-017 (8 fpi)

	09AWL018
	RCL-017
	09AZL016
	RCL-018 (12 fpi)

	09AWL020
	RCL-018
	09AZV012
	RCS-015 (8 fpi)

	09AWW014
	RCL-013
	09AZV014
	RCS-016 (10 fpi)

	09AWW016
	RCL-014
	09AZV016
	RCS-016 (14 fpi)

	09AWW018
	RCL-017
	09AZW012
	RCL-014 (10 fpi)

	09AWW020
	RCL-018
	09AZW014
	RCL-017 (8 fpi)

	
	
	09AZW016
	RCL-018 (12 fpi)


Below is a cross-reference chart of units produced after January 2002:

	Carrier Part Number
	Carrier HTP Part Number
	Carrier Part Number
	Carrier HTP Part Number

	09AWL001
	CDL-001
	09AZH006
	CDS-005 (14 fpi)

	09AWL002
	CDL-002
	09AZH008
	CDS-010 (12 fpi)

	09AWL003
	CDL-003
	09AZH012
	RCS-015 (8 fpi)

	09AWL004
	CDL-004
	09AZH014
	RCS-016 (10 fpi)

	09AWL006
	CDL-006
	09AZH016
	RCS-016 (14 fpi)

	09AWL008
	CDL-008
	09AZL006
	CDL-006 (10 fpi)

	09AWL012
	CDL-009
	09AZL008
	CDL-008 (14 fpi)

	09AWL014
	WCS-013
	09AZL012
	WCS-014 (10 fpi)

	09AWL016
	WCS-014
	09AZL014
	WCS-017 (8 fpi)

	09AWL018
	WCS-017
	09AZL016
	WCS-018 (12 fpi)

	09AWL020
	WCS-018
	09AZV012
	RCS-015 (8 fpi)

	09AWW014
	WCS-013
	09AZV014
	RCS-016 (10 fpi)

	09AWW016
	WCS-014
	09AZV016
	RCS-016 (14 fpi)

	09AWW018
	WCS-017
	09AZW012
	WCS-014 (10 fpi)

	09AWW020
	WCS-018
	09AZW014
	WCS-017 (8 fpi)

	
	
	09AZW016
	WCS-018 (12 fpi)


The 09AZV091-182 machines introduced in December 1999 and were designed specifically to mate with the Carrier 30HXA Condenserless Screw Chillers as shown in the table below:

	30HXA
	Chiller Circuit Split A/B
	Matching Condenser

	
	
	Circuit A
	Circuit B

	106
	64/36
	09AZV102

	116
	60/40
	09AZV112

	126
	55/45
	09AZV122

	136
	59/41
	09AZV132

	146
	55/45
	09AZV142

	161
	59/41
	09AZV162

	171
	47/53
	09AZV172

	186
	50/50
	09AZV182

	206
	54/46
	09AZV101
	09AZV091

	246
	61/39
	09AZV151
	09AZV091

	261
	63/37
	09AZV171
	09AZV091

	271
	64/36
	09AZV181
	09AZV091


The 09AZV091-182 condensers are special condensers produced by Carrier Heat Transfer Products.  Below is a cross-reference chart:

	Carrier Model Number
	Carrier Heat Transfer Products Model Number

	
	Circuit A
	Circuit B

	09AZV091
	WCS-121
	-

	09AZV101
	WCS-140
	-

	09AZV102
	WCS-069
	WCS-053

	09AZV112
	WCS-077
	WCS-077

	09AZV122
	WCS-140

	09AZV132
	WCS-088
	WCS-077

	09AZV142
	WCS-162

	09AZV151
	WCS-177
	-

	09AZV162
	WCS-098
	WCS-096

	09AZV171
	WCS-193
	-

	09AZV172
	WCS-193

	09AZV181
	WCS-200
	-

	09AZV182
	WCS-212


09AW/AZ001-024 Model Number Significance

The following chart is a model number breakdown for the 09AW/AZ001-024.

	Position
	1,2
	3,4
	5
	6-8
	9
	10
	11
	12
	13
	14
	15

	Description
	09
	AZ
	H
	012
	V
	E
	-
	6
	0
	1
	A

	Remote Air-Cooled Condenser
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Direct Drive

AW – Direct Drive

AZ – Direct Drive (designed for 50BZ)
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Condenser Air Discharge

H – Horizontal, Standard Motor

L – Horizontal, Low Noise Motor

V – Vertical, Standard Motor

W – Vertical, Low Noise Motor
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Nominal Heat Rejection

001 – 1 ton

002 – 2 tons

003 – 3 tons

004 – 4 tons

006 – 5 tons

008 – 7.5 tons

012 – 10 tons

014 – 12 tons

016 – 15 tons

018 – 17 tons

020 – 20 tons
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Fan Motor†/Control Option

  -  – ODP, No Control

  C – ODP, Contactors

  D – TEAO, Fan Cycling

  E – TEAO, Contactors

  F – ODP, Fan Cycling

  T – TEAO, No Control

  V – ODP, Speed Control ‡
 W – TEAO, Speed Control ‡
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Circuiting Options

 -  – Single Circuit, No Sub-cooler

 A – Single Circuit with Sub-cooler

 D – Dual Circuit, No Sub-cooler

 E – Dual Circuit with Sub-cooler
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Coil Construction

-  – Al Fin/Cu Tube

C – Cu Fin/Cu Tube

E – Pre-Coat Al Fin/Cu Tube

X – E-coat Al Fin/Cu Tube

Z – E-coat Cu fin/Cu Tube
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Electrical

1 – 575-1-60 or 575-3-60

3 – 208/230-1-60

5 – 208/230-3-60

6 – 460-3-60
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Design Series
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Packaging

   1 – Standard
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Factory Options

   See 09AZV091-182 Factory Installed Options below
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	


Note:  † - Fan motor terms

ODP – Open Drop-proof

TEAO – Totally Enclosed Air Over

‡ - Speed Control is not available on 575-3-60 machines.

09AW/AZ001-024 Factory Installed Options

Factory installed options are determined by Position 15 of the model number and are based on the following options:

	Option Description
	FIOP Code

	
	A
	B
	C
	D
	E
	F
	G

	Aluminum Cabinet

Fabricated cabinet with embossed aluminum for a corrosion-resistant finish
	X
	
	
	X
	X
	
	X

	Fused Disconnect

A power circuit fused disconnect switch
	
	X
	
	X
	
	X
	X

	24-volt Control Transformer

Line to control voltage transformer.
	
	
	X
	
	X
	X
	X


09AZV091-182 Model Number Significance

The following chart is a model number breakdown for the 09AZV091-182.

	Position
	1,2
	3,4
	5
	6-8
	9
	10
	11
	12
	13
	14
	15

	Description
	09
	AZ
	V
	091
	V
	A
	-
	3
	0
	1
	A

	Remote Air-Cooled Condenser
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Direct Drive
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Vertical Discharge
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Nominal Heat Rejection

Single Circuit

   091 – 120 tons

   101 – 140 tons

   151 – 190 tons

   171 – 206 tons

   181 – 216 tons

Dual Circuit

   102 – 120 tons

   112 – 139 tons

   122 – 162 tons

   132 – 160 tons

   142 – 174 tons

   162 – 192 tons

   172 – 209 tons

   182 – 223 tons
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Fan Motor†/Control Option

   D – TEAO/Fan Cycling

   F – ODP/Fan Cycling

   V – ODP/Speed Control ‡
  W – TEAO/Speed Control ‡
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Circuiting Options

   A – Single Circuit and Sub-cooler

   E – Dual Circuit and Sub-cooler
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Coil Construction

-  – Al Fin/Cu Tube

C – Cu Fin/Cu Tube

E – Pre-Coat Al Fin/Cu Tube

X – E-coat Al Fin/Cu Tube

Z – E-coat Cu fin/Cu Tube
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Electrical

1 – 575-3-60

5 – 208/230-3-60

6 – 460-3-60
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Design Series
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Packaging

   1 – Standard
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Factory Options

   See 09AZV091-182 Factory Installed Options below
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	


Note:  † - Fan motor terms

ODP – Open Drop-proof

TEAO – Totally Enclosed Air Over

‡ - Speed Control is not available on 575-3-60 machines.

09AZV091-182 Factory Installed Options

Factory installed options are determined by Position 15 of the model number and are based on the following options:

	Option Description
	FIOP Code

	
	A
	B
	C
	D
	E
	F
	G

	Aluminum Cabinet

Fabricated cabinet with embossed aluminum for a corrosion-resistant finish
	X
	
	
	X
	X
	
	X

	Fused Disconnect

A power circuit fused disconnect switch
	
	X
	
	X
	
	X
	X

	115-volt Control Transformer

Line to control voltage transformer.  No longer offered.
	
	
	X
	
	X
	X
	X


Options and FIOP Codes in gray are no longer offered.   See Bulletin,.

Product Bulletins pertaining to this information:

· 111-01-100 – Discontinued:  Control Transformer, 09AZV091-182, dated 10/12/01.

The 115-volt Control Transformer Option was removed from the offering shortly after the product was introduced. 

· 111-04-69 – 09AZV091-182 Price Page Clarification, dated: 12/02/04.

This bulletin clarified the model number for the 09AZV091-182 machines.

Serial Number Significance

The following chart is the serial number breakdown for the 09AZV

	
	Position

	
	1-7
	8-9
	10-11
	12
	13-14

	
	123456-
	01
	01
	A
	00

	Sales Order Number

(This number always precedes the “-“, and is a numeric counter.)
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	Item Number

Identifies Unit by Item Number on the sales order.
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	Unit Number

Identifies the Unit as a subset of the sales order
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	Month Code

A = January       E = May          I = September

B = February     F = June         J = October

C = March         G = July          K = November

D = April            H = August     L = December 
	
	
	
	
	
	
	

	
	
	
	
	
	
	

	Year Code

00 = 2000, 01 = 2001, etc.
	
	
	
	
	
	

	
	
	
	
	
	


Application

Head Pressure Control

Two types of head pressure controls are offered, fan cycling or variable speed fan control.

Fan Cycling

This option relies on temperature and pressure switches to control the number of fans that are energized.  This is the preferred control when using floodback control.

Variable Speed Fan Control

This option uses the fan cycling controls listed above in combination with a variable speed controller for the lead fans.

Variable Speed Fan Control is not available on 575-3-60 machines.  There is no motor qualified for this application.

Mounting Information

09AW,AZ001-020

All 09AW001-012 and 09AZ006-008 units are furnished with a mounting stand for either a horizontal or vertical condenser air discharge.

The 09AWH/AWL014-020, and the 09AZH/AZL012-016 are shipped with a leg kit that must be field installed.

The 09AZV/AZW012-016 can be converted from vertical discharge to horizontal discharge by completing the following steps:

1. The unit should be oriented such that the liquid tube is on the bottom of the coil.  The discharge header inlet is currently in the middle of the coil.  When the unit is rotated to horizontal discharge, the discharge gas line will need to be looped up and over the top of the coil to prevent liquid refrigerant from running back out of the inlet while the machine is off.  
2. The electrical box will need to be rotated also, so that the top of the control box in the vertical configuration is on top when the unit is reconfigured for horizontal discharge.
3. The leg orientation will need to change and a "foot" will need to be constructed.  Make the stand similar to the 09AZH.  
09AZV091-182

Mounting holes are provided at each outside leg of the machine.  The mounting hole is 0.875” (22.2 mm).

This machine can be point mounted at the legs of the machine.  No mounting rail is required between the legs.

Leg Extension Kits

09AZV091-182

The standard units provide 18” (457 mm) of clearance under the unit.  Three accessory packages are offered to raise the level of the condenser.

	Accessory Part Number
	Description
	Used on
	Clearance under unit, in (mm)

	09AZ-900---101
	30 inch Extended Leg Package
	09AZV091,101,102,122
	30 (762)

	09AZ-900---102
	
	09AZV112,132,142,151
	

	09AZ-900---103
	
	09AZV162,171,172,181,182
	

	09AZ-900---104
	48 inch Extended Leg Package
	09AZV091,101,102,122
	48 (1219)

	09AZ-900---105
	
	09AZV112,132,142,151
	

	09AZ-900---106
	
	09AZV162,171,172,181,182
	

	09AZ-900---107
	72 inch Extended Leg Package
	09AZV091,101,102,122
	72 (1829)

	09AZ-900---108
	
	09AZV112,132,142,151
	

	09AV-900---109
	
	09AZV162,171,172,181,182
	


Refrigerant Circuit Information

All coils are horizontal with an integral subcooler as standard.

	09AZV
	091
	101
	102
	112

	No. of Refrigerant Circuits
	1
	1
	2
	2

	Rows (Circuit A/B)
	3/-
	4/-
	4/3
	3/3

	Fins/Inch (Circuit A/B)
	14/-
	14/-
	14/10
	14/14

	Total Face Area (ft2)
	120.9
	120.9
	121.0
	151.0

	Circuit Split (Circuit A/B)
	100/-
	100/-
	56/44
	50/50

	Circuit Volume (ft3) (Circuit A/B)
	2.48/-
	3.31/-
	1.65/1.24
	2.84/2.84


	09AZV
	122
	132
	142
	151

	No. of Refrigerant Circuits
	2
	2
	2
	1

	Rows (Circuit A/B)
	4/4
	4/3
	4/4
	4/-

	Fins/Inch (Circuit A/B)
	14/14
	14/14
	10/10
	10/-

	Total Face Area (ft2)
	120.9
	151.0
	150.9
	150.9

	Circuit Split (Circuit A/B)
	50/50
	53/47
	50/50
	100/-

	Circuit Volume (ft3) (Circuit A/B)
	1.65/1.65
	3.79/2.84
	3.79/3.79
	7.58/-


	09AZV
	162
	171
	172
	181

	No. of Refrigerant Circuits
	2
	1
	2
	1

	Rows (Circuit A/B)
	4/4
	4/-
	4/4
	4/-

	Fins/Inch (Circuit A/B)
	12/10
	10/-
	10/10
	12/-

	Total Face Area (ft2)
	181.0
	180.9
	180.9
	180.9

	Circuit Split (Circuit A/B)
	51/49
	100/-
	50/50
	100/-

	Circuit Volume (ft3) (Circuit A/B)
	4.54/4.54
	9.08/-
	4.54/4.54
	9.08/-


	09AZV
	182

	No. of Refrigerant Circuits
	2

	Rows (Circuit A/B)
	4/4

	Fins/Inch (Circuit A/B)
	14/14

	Total Face Area (ft2)
	180.9

	Circuit Split (Circuit A/B)
	50/50

	Circuit Volume (ft3) (Circuit A/B)
	4.54/4.54


Installation

Refrigerant Piping

09AZV091-182

Starting with production in June 2006, the subcooler traps were removed from the factory installed portion of the machine assembly, due to shipping problems.  These traps are factory assembled, shipped with the machine and must  be field installed.  A Schrader valve was added to the subcooler header for pressurization during shipment.

For single circuit machines, 09AZV091, 101, 151, 171, and 181 are shipped from the factory with the parts for the discharge and liquid line manifolds for field assembly and installation.

	Unit

09AZV
	No. of Circuits
	 Tubing Assembly (Qty)

	
	
	Subcooler Trap†
	Discharge Manifold *
	Liquid Line Manifold *

	091, 101, 151, 171, 181
	1
	(2)
	Assembly consisting of:

(2) 2⅝ Elbows
(1) 2⅝ x 2⅝ x 3⅛ Tee

(2) 2⅝ Straight Pipe
	Assembly consisting of:

(2) 2⅛ Elbows
(1) 2⅛ x 2⅛ x 2⅛ Tee

(2) 2⅛ Straight Pipe

	102, 112, 122, 132, 142, 162, 172, 182
	2
	(2)
	N/A
	N/A


Note:     † - New part which requires field installation

       *  - Requires field assembly and installation


   N/A - Not Applicable
[image: image3.png]Discharge Header

Field-Installed Discharge Gas Manifold Assernbly
(Single Circuit Units Only)

TOP Subcooler nlet Header —

Condenser Outlet Header

Fieli-Installed Subcooler
Trap Assembly

Subcooler Outlet Header

Installed Liquid Line Manifold Assernbly
(Single Circutt Units Only)
(Removed from unit for clarity )





Product Bulletins pertaining to this information:

· 111-06-31 – 09AZV091-182 Piping Changes

This bulletin described the factory piping changes to Subcooler trap for these units. 

Literature

Below is a list of literature for the 09AZ Air-Cooled Condenser machines.  Shaded literature is obsolete literature.

	Form Number
	Catalog Number
	Title
	Print Date
	Reprint Date
	Superceded By

	Product Data

	09AW,AZ-1PD
	520-911
	09AW,AZ001-020 Air-Cooled Condensers
	2/99
	
	09AW,AZ-2PD

	09AW,AZ-2PD
	520-921
	09AW,AZ001-020 Air-Cooled Condensers
	4/02
	
	

	09AZ-1PD
	520-925
	09AZ091-182 Air-Cooled Condensers
	2/01
	
	

	Application Information

	
	811-20062
	Selection Guide:  Environmental Corrosion Protection
	10/2004
	
	04-581006-01

	
	04-581006-01
	Selection Guide:  Environmental Corrosion Protection
	04/2006
	
	

	Product Bulletin

	111-99-12
	
	50BZ/09AZ Combination Ratings
	03/19/99
	
	

	111-99-12
	
	1 to 20 ton 09AW & 09AZ Direct Drive Air Cooled Condensers
	03/26/99
	
	

	111-99-79
	
	NEW! Large Air Cooled Condensers for 30HXA Chillers
	12/10/99
	
	

	111-00-40
	
	Master Price Page Correction: 09AZV091-182 Motor Options
	05/19/00
	
	

	111-00-77
	
	Master Price Page Correction: 09AZV181 Coil Coating Option
	09/15/00
	
	

	111-01-24
	
	09AZV091-182 Product Data
	03/23/01
	
	

	111-01-100
	
	Discontinued: Control Transformer, 09AZV091-182
	10/12/01
	
	

	111-04-69
	
	09AZV091-182 Price Page Clarification
	12/02/04
	
	

	111-06-31
	
	09AZV091-182 Piping Changes
	06/07/06
	
	

	Submittal Bulletin

	09AW-1SB
	510-902
	09AWH,AWL001-004 Air-Cooled Condenser
	1/99
	
	09AW-8SB

	09AW-2SB
	510-903
	09AWH,AWL006-012 Air-Cooled Condenser
	1/99
	
	09AW-5SB

	09AW-3SB
	510-904
	09AWH,AWL014-020 Air-Cooled Condenser
	1/99
	
	09AW-6SB

	09AW-4SB
	510-905
	09AWV,AWV014-020 Air-Cooled Condenser
	1/99
	
	09AW-7SB

	09AW-5SB
	510-913
	09AWH,AWL006-012 Air-Cooled Condenser
	12/00
	
	

	09AW-6SB
	510-914
	09AWH,AWL014-020 Air-Cooled Condenser
	1/02
	
	

	09AW-7SB
	510-933
	09AWV,AWV014-020 Air-Cooled Condenser
	1/02
	
	

	09AW-8SB
	510-936
	09AWH,AWL001-004 Air-Cooled Condenser
	12/00
	
	

	09AZ-1SB
	510-906
	09AZH006 Air-Cooled Condenser
	1/99
	
	09AZ-8SB

	09AZ-2SB
	510-907
	09AZH008, 09AZL006,008 Air-Cooled Condenser
	1/99
	
	09AZ-9SB

	09AZ-3SB
	510-908
	09AZH,AZL012-016 Air-Cooled Condenser
	1/99
	
	09AZ-7SB

	09AZ-4SB
	510-909
	09AZV,AZW012-016 Air-Cooled Condenser
	1/99
	
	09AZ-5SB

	09AZ-5SB
	510-911
	09AZV,AZW012-016 Air-Cooled Condenser
	1/02
	
	

	09AZ-6SB
	510-912
	09AZV091-182 Air-Cooled Condenser
	11/00
	
	

	09AZ-7SB
	510-908
	09AZH,AZL012-016 Air-Cooled Condenser
	1/02
	
	

	09AZ-8SB
	510-937
	09AZH006 Air-Cooled Condenser
	1/02
	
	

	09AZ-9SB
	510-938
	09AZH008, 09AZL006,008 Air-Cooled Condenser
	1/02
	
	

	Installation Instructions

	09AW,AZ-1SI
	530-904
	09AW,AZ001-020 Air-Cooled Condensers, 1 to 20 Tons
	2/99
	
	09AW,AZ-2SI

	09AW,AZ-2SI
	530-919
	09AW,AZ001-020 Air-Cooled Condensers, 1 to 20 Tons
	1/02
	
	

	09AZ-1SI
	530-921
	09AZ091-182 Air-Cooled Condensers, 90 to 200 Tons
	2/01
	
	

	Accessory Installation Instructions

	
	
	
	
	
	

	Wiring Diagrams

	09AW,AZ-1W
	530-905
	09AW,AZ001-024 Remote Air-Cooled Condenser
	2/99
	
	


Service

Condenser Fan System, 09AZV091-182

The condenser fan system is a direct drive, vertical discharge system.  

	09AZV
	091
	101
	102
	112

	Fan Option (Position 9)
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W

	Qty…Fan Diameter (in.)
	8…30
	2…26

6…30
	8…30
	2…26

6…30
	8…30
	2…26

6…30
	10…30
	2…26

8…30

	No. of Blades
	4

	Maximum RPM
	1140

	Total Airflow, CFM
	87,600
	82,800
	86,300
	109,500

	Cir. Airflow, CFM (Cir. A/B)
	-/-
	-/-
	41,400/44,900
	54,750/54,750

	Motor Hp
	1-1/2


	09AZV
	122
	132
	142
	151

	Fan Option (Position 9)
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W

	Qty…Fan Diameter (in.)
	8…30
	2…26

6…30
	10…30
	2…26

8…30
	10…30
	2…26

8…30
	10…30
	2…26

8…30

	No. of Blades
	4

	Maximum RPM
	1140

	Total Airflow, CFM
	82,800
	106,500
	108,700
	103,500

	Cir. Airflow, CFM (Cir. A/B)
	41,400/41,400
	51,750/54,750
	54,350/54,350
	-/-

	Motor Hp
	1-1/2


	09AZV
	162
	171
	172
	181

	Fan Option (Position 9)
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W
	D or F
	V or W

	Qty…Fan Diameter (in.)
	12…30
	2…26

10…30
	12…30
	2…26

10…30
	12…30
	2…26

10…30
	12…30
	2…26

10…30

	No. of Blades
	4

	Maximum RPM
	1140

	Total Airflow, CFM
	130,450
	132,700
	132,700
	128,200

	Cir. Airflow, CFM (Cir. A/B)
	64,100/66,350
	-/-
	66,350/66,350
	-/-

	Motor Hp
	1-1/2


	09AZV
	182

	Fan Option (Position 9)
	D or F
	V or W

	Qty…Fan Diameter (in.)
	12…30
	2…26

10…30

	No. of Blades
	4

	Maximum RPM
	1140

	Total Airflow, CFM
	124,200

	Cir. Airflow, CFM (Cir. A/B)
	62,100/62,100

	Motor Hp
	1-1/2


Condenser Fan Blades

The condenser fan changes based on the head pressure control used, temperature control or variable speed.

In 2001 the 30” fan blade was changed from Lau to Hessaire fan blade.  In August 2003 (Serial Numbers ending with H03) a revised Hessaire fan was implemented with a higher efficiency.

Condenser Fan Motor

Standard fan motors are 3-phase motors.  Fan motors connected to the speed control device are single-phase motors.

A known problem with the condenser fan motor overloads was experienced by Witt production with serial numbers ending with K02 through H03.  

Troubleshooting:

If the motor overload is tripping, check the following items:

· Check the fan placement in the orifice.

· Check for the proper fan blade.

· Check for a voltage/current imbalance.

· Consider replacing the fan motor due to a faulty condenser fan motor overload. 

Head Pressure Control

There are several control schemes offered for the 09AZ091-182 condensers.

Temperature & Pressure Switch Control

The standard control is for temperature and pressure switches to control various fans.

The fans at the header end are uncontrolled.  They will start when control power is applied to the machine.  See the fan staging diagram shown below for fan numbering.  

A temperature switch controls the opposite the header end.  See the fan staging diagram shown below for fan numbering.  The switch is adjustable and should be field set for the following:


Cut-In Temperature (± 3 ºF)

70 ºF


Cut-Out Temperature (± 3 ºF)

60 ºF

A pressure switch controls the remaining fans.  See the fan staging diagram shown below for fan numbering.  The switch is adjustable and should be field set for the following:


Cut-In Pressure (± 10 psi)


175 psi


Cut-Out Pressure (± 10 psi)

145 psi

Variable Speed Head Pressure Control

Machines selected with the variable speed option, utilize the temperature and pressure switch control scheme outlined above.  However, a variable speed device controls the uncontrolled fans located at the header end in the scheme above.

On all machines, the variable head pressure control device is a Johnson P66AAB-4C controller.  This device controls the lead fans located at the header end of the machine.

The device requires 24 vac control power to function.

	Part Number
	P66AAB-4C

	Operating Range, psig (kPa) [Factory Setting]
	135-165 (931-1138)

	Effective Throttling Range, psig (kPa) [Fixed]
	30 (207)

	Pressure Range, psig (kPa) [Adjustable]
	80-200 (551-1379)

	Maximum Operating Pressure, psig (kPa) 
	450 (3103)

	Control Voltage, V-Ph-Hz
	24-1-60

	Power Consumption, VA
	1

	Capillary Length, in. (mm)
	60 (1,524)


Early production of these machines incorrectly called for the R-22 controller, P66AAB-1.  The pressure settings were to high for the device to control, causing the 30HXA machines to trip on high head pressure.

For field modification of the Fan Cycling to Variable Speed Head Pressure Control, the following parts are needed.

	Description
	Part Number (by Voltage)
	09AZV

	
	208/230-3-60
	460-3-60
	091, 101, 151, 171, 181
	102, 112, 122, 132, 142, 162, 172, 182

	Speed Controller
	08219437
	1
	2

	¼” Shut-off Valve
	08396559
	1
	2

	Transformer
	08218258
	08218259
	2
	2

	Fan Blade, 26”
	08221047
	2
	2

	Fan Guard
	08397010
	2
	2

	Fan Venturi
	08517407
	2
	2

	Fan Motor
	08216098
	2
	2

	Capacitor
	08352555
	2
	2


There are no instructions available for this change.  It is a Factory Installed Option only.  

Fan Identification

	09AZV091,101,102,122

	[image: image4.png]Control Box End
Header End






	Machine
	Fan Option (Position 9)
	Circuit
	Controlled By
	Contactor
	Fan Motor

	09AZV091, 

09AZV101
	D or F
	A
	None
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3
	3, 4, 5, 6

	
	
	
	Temperature Switch
	C4
	7, 8

	
	V or W
	A
	Variable Speed
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3
	3, 4, 5, 6

	
	
	
	Temperature Switch
	C4
	7, 8

	09AZV102,

09AZV122
	D or F
	A
	None
	C1
	1

	
	
	
	Pressure Switch
	C3, C5
	3, 5

	
	
	
	Temperature Switch
	C7
	7

	
	
	B
	None
	C2
	2

	
	
	
	Pressure Switch
	C4, C6
	4, 6

	
	
	
	Temperature Switch
	C8
	8

	
	V or W
	A
	Variable Speed
	C1
	1

	
	
	
	Pressure Switch
	C3, C5
	3, 5

	
	
	
	Temperature Switch
	C7
	7

	
	
	B
	Variable Speed
	C2
	2

	
	
	
	Pressure Switch
	C4, C6
	4, 6

	
	
	
	Temperature Switch
	C8
	8


	09AZV112,132,142,151

	[image: image5.png]O]0)
Q0
Q0
00
Qe






	Machine
	Fan Option (Position 9)
	Circuit
	Controlled By
	Contactor
	Fan Motor

	09AZV112,

09AZV132,

09AZV142
	D or F
	A
	None
	C1
	1

	
	
	
	Pressure Switch
	C3, C5
	3, 5

	
	
	
	Temperature Switch
	C7, C9
	7, 9

	
	
	B
	None
	C2
	2

	
	
	
	Pressure Switch
	C4, C6
	4, 6

	
	
	
	Temperature Switch
	C8, C10
	8, 10

	
	V or W
	A
	Variable Speed
	C1
	1

	
	
	
	Pressure Switch
	C3, C5
	3, 5

	
	
	
	Temperature Switch
	C7, C9
	7, 9

	
	
	B
	Variable Speed
	C2
	2

	
	
	
	Pressure Switch
	C4, C6
	4, 6

	
	
	
	Temperature Switch
	C8, C10
	8, 10

	09AZV151
	D or F
	A
	None
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3
	3, 4, 5, 6

	
	
	
	Temperature Switch
	C4, 5
	7, 8, 9, 10

	
	V or W
	A
	Variable Speed
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3
	3, 4, 5, 6

	
	
	
	Temperature Switch
	C4, C5
	7, 8, 9, 10


	09AZV162,171,172,181,182

	[image: image6.png]O]0]
O]0]
Q0
Q0
00
Qe






	Machine
	Fan Option (Position 9)
	Circuit
	Controlled By
	Contactor
	Fan Motor

	09AZV162,

09AZV172,

09AZV182
	D or F
	A
	None
	C1
	1

	
	
	
	Pressure Switch
	C3, C5, C7
	3, 5, 7

	
	
	
	Temperature Switch
	C9, C11
	9, 11

	
	
	B
	None
	C2
	2

	
	
	
	Pressure Switch
	C4, C6, C8
	4, 6, 8

	
	
	
	Temperature Switch
	C10, C12
	10, 12

	
	V or W
	A
	Variable Speed
	C1
	1

	
	
	
	Pressure Switch
	C3, C5, C7
	3, 5, 7

	
	
	
	Temperature Switch
	C9, C11
	9, 11

	
	
	B
	Variable Speed
	C2
	2

	
	
	
	Pressure Switch
	C4, C6, C8
	4, 6, 8

	
	
	
	Temperature Switch
	C10, C12
	10, 12

	09AZV171,

09AZV181
	D or F
	A
	None
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3, C4
	3, 4, 5, 6, 7, 8

	
	
	
	Temperature Switch
	C5, C6
	9, 10, 11, 12

	
	V or W
	A
	Variable Speed
	C1
	1, 2

	
	
	
	Pressure Switch
	C2, C3, C4
	3, 4, 5, 6, 7, 8

	
	
	
	Temperature Switch
	C5, C6
	9, 10, 11, 12


Confidential



Confidential

06/07/06

