[image: image1.png]



[image: image28.png]




[image: image30.png]



ComfortLinktm
Service Manual

30GXN/GXR Series 4 & 5, Air-Cooled Chillers

30HXA Series 4 & 5, Condenserless Chillers

30HXC Series 4 & 5, Water-Cooled Chillers
[image: image29.png]


This document is not intended for general distribution.  It is to be used by Carrier Distributor Service or Carrier Commercial Service personnel only, and may not be distributed to individuals not employed within these organizations.  This document is intended as a guide only.  There is no guarantee of the accuracy of the information contained within.

Table of Contents

9Safety Considerations

Introduction
10
Application
10
Duplex Chillers (30GXN,GXR Only)
10
Controls
11
Carrier Comfort Network
11
Alarm Routing Control
11
Communication Bus Wiring
12
Carrier Comfort Network Interface Devices
13
BacLink™
13
DataLink™
14
DataPort™
14
Cooler Heater (30GXN,GXR Only)
14
Cooler Pump Control
14
Condenser Pump Control
15
Condenser Pump Interlock
16
Demand Limit
16
4-20 Demand Limit
16
Head Pressure Control
16
30GXN/GXR
16
30HXA
17
30HXC
17
Master/Slave Operation
17
Configuration
18
Series Flow
18
Parallel Flow
18
Sequence of Operation
18
Series Flow
18
Suggested Operating Scheme
18
CCN Control
18
Troubleshooting:
18
Navigator
19
Adjusting the Contrast
20
Adjusting the Backlight Brightness
20
Changing the Password
21
Oil Heaters (30GXN,GXR Only)
21
Operating Modes
22
MD01 – FSM Controlling Chiller
22
MD02 – WSM Controlling Chiller
22
MD03 – Master/Slave Control
22
MD04 – Low Source Protection
22
MD05 – Ramp Load Limited
22
MD06 – Timed Override In Effect
23
MD07 – Low Cooler Suction TempA
23
MD08 – Low Cooler Suction TempB
23
MD09 – Slow Change Override
23
MD10 – Minimum Off Time Active
24
MD11 – Low Discharge Superheat A
24
MD12 – Low Discharge Superheat B
24
MD13 – Dual Setpoint
24
MD14 – Temperature Reset
24
MD15 – Demand Limit In Effect
24
MD16 – Cooler Freeze Protection
25
MD17 – Lo Tmp Cool/Hi Tmp Heat
25
MD18 – Hi Tmp Cool/Lo Tmp Heat
25
MD19 – Making Ice
25
MD20 – Storing Ice
26
MD21 – High SCT Circuit A
26
MD22 – High SCT Circuit B
26
MD23 – High Motor Current Cir. A
27
MD24 – High Motor Current Cir. B
27
MD25 – Ckt A Off Ref Flow Delay
27
MD26 – Ckt B Off Ref Flow Delay
27
MD27 – Circuit A Pumping Out
27
MD28 – Circuit B Pumping Out
27
MD29 – Unit OFF: No Water Flow
27
Software Revisions
27
Version 4.5
28
Version 4.3
28
Version 4.0 (CESR-131248-04-00)
29
Version 3.1 (CESR-131248-03-01)
32
Version 2.0 (CESR-131248-02-00)
33
Version 1.0 (CESR-131248-01-00)
33
Temperature Reset
34
4-20 ma Temperature Reset
34
Return Water Reset
35
Temperature Set Point
37
Single Set Point/Switch Control
37
Dual Set Point, Switch/Switch Control
37
Ice Build, Switch/Switch Control
37
Single Set Point/7 Day Schedule
38
Dual Set Point/7 Day Schedule
39
Ice Build/7 Day Schedule
40
Single Set Point/Occupancy
40
Dual Set Point/Occupancy
41
Ice Build/Occupancy
42
4 to 20 mA Input/Switch Control
42
Service
43
Alarm and Alert Codes
43
Communication Failure
44
T020 – Compressor A1 High Motor Temperature Alert
44
T021 – Compressor A2 High Motor Temperature Alert
44
T022 – Compressor B1 High Motor Temperature Alert
44
T023 – Compressor B2 High Motor Temperature Alert
44
T026 – Compressor A1 Low Oil Pressure Alert - 1
44
T026 – Compressor A1 Low Oil Pressure Alert - 2
44
T027 – Compressor A2 Low Oil Pressure Alert - 1
44
T027 – Compressor A2 Low Oil Pressure Alert - 2
44
T028 – Compressor B1 Low Oil Pressure Alert - 1
44
T028 – Compressor B1 Low Oil Pressure Alert - 2
44
T029 – Compressor B2 Low Oil Pressure Alert - 1
44
T029 – Compressor B2 Low Oil Pressure Alert - 2
44
T030 – Compressor A1 Pre-Start Oil Pressure Alert
46
T031 – Compressor A2 Pre-Start Oil Pressure Alert
46
T032 – Compressor B1 Pre-Start Oil Pressure Alert
46
T033 – Compressor B2 Pre-Start Oil Pressure Alert
46
T034 – Compressor A1 Max. Oil Delta P, Check Oil Line Alert
47
T035 – Compressor A2 Max. Oil Delta P, Check Oil Line Alert
47
T036 – Compressor B1 Max. Oil Delta P, Check Oil Line Alert
47
T037 – Compressor B2 Max. Oil Delta P, Check Oil Line Alert
47
T038 – Compressor A1 Failed Oil Solenoid Alert
48
T039 – Compressor A2 Failed Oil Solenoid Alert
48
T040 – Compressor B1 Failed Oil Solenoid Alert
48
T041 – Compressor B2 Failed Oil Solenoid Alert
48
T051 – Compressor A1 Failure Alert
49
T052 – Compressor A2 Failure Alert
49
T055 – Compressor B1 Failure Alert
49
T056 – Compressor B2 Failure Alert
49
High Pressure Switch Trip Alert
49
No Motor Current Detected Alert
50
Current Unbalance Alert
50
Single Phase Current Loss Alert
52
High Motor Current Detected Alert
52
Compressor Ground Fault Alert
53
Contactor Failure Alert
55
Current Phase Reversal Alert
55
Motor Over Temperature Alert
56
Open Thermistor Alert
57
MTA Header Fault Alert
57
MTA Alert
57
Shorted Thermistor Alert
58
A060 – Cooler Leaving Water Thermistor Failure - 1 Alarm
58
A060 – Cooler Leaving Water Thermistor Failure - 2 Alarm
58
T061 – Cooler Entering Water Thermistor Failure Alert
59
T062 – Condenser Leaving Water Thermistor Failure Alert
59
T063 – Condenser Entering Water Thermistor Failure Alert
59
T070 – Circuit A Discharge Gas Thermistor Failure Alert
59
T071 – Circuit B Discharge Gas Thermistor Failure Alert
59
T073 – Outdoor Air Temperature Thermistor Failure Alert
60
T074 – External Reset Temperature Thermistor Failure Alert
60
T079 – Lead/Lag Thermistor Failure Alert
61
T090 – Circuit A Discharge Pressure Transducer Failure Alert
61
T091 – Circuit B Discharge Pressure Transducer Failure Alert
61
T092 – Circuit A Suction Pressure Transducer Failure Alert
61
T093 – Circuit B Suction Pressure Transducer Failure Alert
61
T094 – Compressor A1 Oil Pressure Transducer Failure Alert
62
T095 – Compressor A2 Oil Pressure Transducer Failure Alert
62
T096 – Compressor B1 Oil Pressure Transducer Failure Alert
62
T097 – Compressor B2 Oil Pressure Transducer Failure Alert
62
T098 – Circuit A Economizer Pressure Transducer Failure – 1 Alert
62
T098 – Circuit A Economizer Pressure Transducer Failure – 2 Alert
62
T099 – Circuit B Economizer Pressure Transducer Failure – 1 Alert
62
T099 – Circuit B Economizer Pressure Transducer Failure – 2 Alert
62
T110 - Circuit A Loss of Charge Alert
63
T111 - Circuit B Loss of Charge Alert
63
T120 - Circuit A Low Saturated Suction Temperature Alert
63
T121 - Circuit B Low Saturated Suction Temperature Alert
63
T122 - Circuit A High Saturated Suction Temperature Alert
64
T123 - Circuit B High Saturated Suction Temperature Alert
64
T124 - Circuit A Low Oil Level
65
T125 - Circuit B Low Oil Level
65
T126 - Circuit A High Discharge Pressure Alert
66
T127 - Circuit B High Discharge Pressure Alert
66
A128 - Circuit A Condenser Freeze Protection Alarm
66
A129 - Circuit B Condenser Freeze Protection Alarm
66
T131 - Circuit A Liquid Level Sensor Failure Alert
67
T132 - Circuit B Liquid Level Sensor Failure Alert
67
T135 - Circuit A Failure to Pumpout Alert
67
T136 - Circuit B Failure to Pumpout Alert
67
T137 - Circuit A Low Discharge Superheat Alert
68
T138 - Circuit B Low Discharge Superheat Alert
68
T140 – Compressor A1 High Oil Filter Pressure Drop Alert
69
T141 – Compressor A2 High Oil Filter Pressure Drop Alert
69
T142 – Compressor B1 High Oil Filter Pressure Drop Alert
69
T143 – Compressor B2 High Oil Filter Pressure Drop Alert
69
A150 – Unit is in Emergency Stop Alarm
70
A151 – Illegal Configuration x Alarm
70
A152 – Unit Down Due to Failure
71
A153 – Real Time Clock Hardware Failure Alarm
72
A154 – Serial EEPROM Hardware Failure Alarm
72
A155 – Serial EEPROM Storage Failure Error Alarm
72
A156 – Critical Serial EEPROM Storage Failure Error Alarm
73
A157 – A/D Hardware Failure Alarm
73
A159 – Loss of Condenser Flow Alarm
73
A172 – Loss of Communication with EXV Module Alarm
73
T173 – Loss of Communications with Energy Management Module Alert
74
T174 – 4-20 mA Cool Setpoint Input Failure Alert
75
T175 – 4-20 mA Heat Setpoint Input Failure Alert
75
T176 – 4-20 mA Reset Input Failure Alert
76
T177 – 4-20 mA Demand Limit Input Failure Alert
76
A178 – Loss of Communication with Screw Chiller Module Alarm
77
A180 -  Loss of Communication with Compressor Protection Module 1 Alarm
77
A181 -  Loss of Communication with Compressor Protection Module 2 Alarm
77
T182 – Compressor Protection Module 1 Internal Diagnostic Alert
78
T183 – Compressor Protection Module 2 Internal Diagnostic Alert
78
A200 – Cooler Pump Interlock Failed at Start-Up
78
A201 – Cooler Pump Interlock Failure Contacts Open During Normal Operation Alarm
79
A202 – Cooler Pump Interlock Failure Contacts Closed While Pump is OFF Alarm
79
T203 – Loss of Communication with the Slave Chiller Alert
79
T204 – Loss of Communication with the Master Chiller Alert
80
T205 – Master and Slave Chiller with Same Address Alert
80
T206 – High Leaving Chilled Water Temperature Alert
81
A207 – Cooler Freeze Protection Alarm
81
T210 – Winterization Required Alert
82
T950 – WSM POC Communication Failure Alert
83
A951 – FSM Loss of Communication Alert
83
P998 – Pre-Alert Loss of Refrigerant Flow - Circuit A
83
T998 – Loss of Refrigerant Flow - Circuit A Alert
83
P999 – Pre-Alert Loss of Refrigerant Flow - Circuit B
83
T999 – Loss of Refrigerant Flow - Circuit B Alert
83
Resetting Alarms and Alerts
84
Chilled Water Flow Switch
85
ComfortLink Control Boards
88
ComfortLink Compressor Protection Module (CCP)
88
Interface Devices
116
Navigator
116
Energy Management Board (EMM)
118
EXV Board (EXV)
118
Main Base Board (MBB)
118
Screw Compressor Board (SCB)
119
Compressor
119
Compression
120
Discharge Check Valve
120
Suction Screen
121
Electrical
121
Motor Terminal Pins
121
Lubrication System
121
Oil Solenoid Valve
121
Condenser Fan
122
Standard Fan
122
0.4 w.g. (100 Pa) External Static Pressure Fan
123
0.8 w.g (200 Pa) External Static Pressure Fan
123
Condenser Fan Motor
123
Cooler
124
Cooler Freeze-Up/Leak Cleaning Procedure
124
Cooler Head Removal
126
Cooler Heater
126
Cooler Weights
126
Cooler Liquid Level Sensor
129
Condenser
130
Expansion Device
130
Electronic Expansion Valve
130
Economizer
131
Head Pressure Control
131
30GXN/GXR
131
MotorMaster III
131
MotorMaster V
131
Troubleshooting
131
Machine Assembly
131
Liquid Line Strainers
131
Non-Fused Disconnects
132
Oil
133
Oil Circulation Rate
134
Oil Filter
135
External Oil Filter
135
Internal Oil Filter
135
Oil Pump
136
Oil Separator
136
Oil Separator Heaters
137
Refrigerant
137
Refrigerant Moisture Limit
137
Refrigerant Charging
138
30HXA Refrigerant Charging
139
30HXA/09AZ Initial Refrigerant Charging Chart
139
Service Valves
139
Discharge Service Valves
140
Liquid Line Service Valves
140
Oil Line Service Valves
140
Suction Service Valves
140
Transducers
140
Thermistors
140
Water Analysis
141
Maintenance
142
Recommended Spare Parts List
143
30GXN,GXR Spare Parts List
144
30HXA Spare Parts List
146
30HXC Spare Parts List
148


Safety Considerations

Installing, starting up, and servicing this equipment can be hazardous due to system pressures, electrical components, and equipment location (roof, elevated structures, etc.).  Only trained, qualified installers and service mechanics should install, start-up, and service this equipment.

When working on this equipment, observe precautions in the literature, and on tags, stickers, and labels attached to the equipment and any other safety precautions that apply.  Follow all safety codes.  Wear safety glasses and work gloves.  Use care in handling, rigging, and setting this equipment, an in handling all electrical components.

	WARNING

	Electrical shock can cause personal injury and death.  Shut off all power to this equipment during installation and service.  There may be more that one disconnect switch.  Tag all disconnect locations to alert others not to restore power until work is complete.


	WARNING

	This unit uses a microprocessor-based electronic control system.  Do not use jumpers or other tools to short out components or to bypass or otherwise depart from recommended procedures.  Any short-to-ground of the control board or accompanying wiring may destroy the electronic modules or electrical components.


	WARNING

	To prevent potential damage to heat exchanger tubes always run fluid through heat exchangers when adding or removing refrigerant charge.  Use appropriate brine solutions in cooler and condenser fluid loops to prevent the freezing of heat exchangers when the equipment is exposed to temperatures below 32 (F (0 (C).

DO NOT VENT refrigerant valves within a building.  Outlet from relief valves must be vented outdoors in accordance with the latest edition of ANSI/ASHRAE (American National Standards Institute/American Society of Heating, Refrigeration and Air Conditioning Engineers) 15 (Safety Code for Mechanical Refrigeration).  The accumulation of refrigerant in an enclosed space can displace oxygen and cause asphyxiation.  Provide adequate ventilation in enclosed or low overhead areas.  Inhalation of high concentrations of vapor is harmful and may cause heart irregularities, unconsciousness or death.  Misuse can be fatal.  Vapor is heavier than air and reduces the amount of oxygen available for breathing.  Product causes eye and skin irritation.  Decomposition products are hazardous. 


	WARNING

	DO NOT attempt to unbraze factory joints when servicing this equipment.  Compressor oil is flammable and there is no way to detect how much oil may be in any of the refrigerant lines.  Cut lines with a tubing cutter as required when performing service.  Use a pan to catch any oil that may come out of the lines and as a gage for how much oil to add to the system.  DO NOT re-use compressor oil.  DO NOT leave refrigerant system open to air any longer than necessary.  Seal circuits being serviced and charge with dry nitrogen to prevent oil contamination when timely repairs cannot be completed.


Introduction

This information should be used with the Installation Instructions, and the Controls, Start-Up, Operation, Service and Troubleshooting book for these machines.  Follow all safety precautions and procedures.

ComfortLink Control Series 4 production began with Serial Number beginning with 3400F.

30GXN/GXR Series 5 production began with Serial Number 0703F.  This series change indicates the changes to a cast cooler head for most coolers.

30HXA/HXC Series 5 production began with production late in the week of Serial Number 0903Q.  As with the 30GX machines, this series change indicates the changes to a cast cooler head for most coolers.

Application

Duplex Chillers (30GXN,GXR Only)

	SIZE

30GXN,GXR
	Frequency
	Consists of (30GXN,GXR)

	
	
	MODULE A
	MODULE B

	220
	50 Hz only
	125
	090

	240
	50 Hz only
	125
	115

	275
	50 Hz only
	135
	135

	283
	60 Hz & 50 Hz
	153
	138

	300
	50 Hz only
	160
	135

	303
	60 Hz & 50 Hz
	163
	138

	320
	50 Hz only
	160
	160

	328
	60 Hz & 50 Hz
	178
	153

	345
	50 Hz only
	175
	175

	353
	60 Hz & 50 Hz
	178
	178

	365
	50 Hz only
	250
	135

	370
	60 Hz only
	225
	150

	373
	60 Hz & 50 Hz
	253
	138

	390
	60 Hz only
	264
	135

	393
	60 Hz & 50 Hz
	253
	153

	395
	50 Hz only
	264
	135

	410
	50 Hz only
	225
	205

	415
	60 Hz only
	264
	160

	418
	60 Hz & 50 Hz
	268
	153

	440
	50 Hz only
	225
	225

	450
	60 Hz only
	225
	225

	453
	60 Hz & 50 Hz
	228
	228

	470
	50 Hz only
	250
	225

	475
	60 Hz only
	249
	225

	478
	60 Hz & 50 Hz
	253
	228

	495
	50 Hz only
	250
	250

	500
	60 Hz only
	249
	249

	503
	60 Hz & 50 Hz
	253
	253

	520
	50 Hz only
	264
	264

	525
	60 Hz only
	264
	264

	528
	60 Hz & 50 Hz
	268
	268


Controls

Carrier Comfort Network

The 30GXN,R/HXA/HXC chiller units can be connected to the CCN, if desired.  

Alarm Routing Control

Alarms recorded on the chiller can be routed through the CCN.  To configure for this option, the ComfortLink Control must be configured to determine which elements will receive and process alarms sent by the ComfortLink Control.  Input for the decision consists of eight digits, each of which can be set to either 0 or 1.  Setting a digit to 1 specifies that alarms will be sent to the system element that corresponds to that digit.  Setting all digits to 0 disables alarm processing.  The factory default is 0000000.  This is based on the assumption that the unit will not be connected to a network.  If the network does not contain a ComfortView, ComfortWorks, Building Supervisor, AutoDial Gateway or Alarm Printer Interface Module (APIM), enabling this feature will only add unnecessary activity to the CCN Communication Bus.

	DESCRIPTION
	STATUS
	POINT

	
	
	

	Alarm Routing
	0
	0
	0
	0
	0
	0
	0
	0
	ALRM_CNT

	Building Supervisor, ComfortView, or ComfortWorks
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Autodial Gateway
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Unused
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Alarm Printer Interface Module

BacLink, or DataLink
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Unused
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	


Network Service Tool is required to configure the ComfortLink Control System of the chiller.  With Network Service Tool attached to the chiller, go to:

Modify> Controller>ALARMDEF and change Alarm Routing Control to the desired configuration.

Typical configuration of Alarm Routing is 11010000.  This Alarm Routing status will transmit alarms to:  

Building Supervisor, ComfortView, or ComfortWorks; 

Autodial Gateway; and

BacLink or DataLink

Communication Bus Wiring XE "Carrier Comfort Network:Communication Bus Wiring" 
The communication bus wiring is a shielded, 3‑conductor cable with drain wire and is supplied and installed in the field.  

	CCN Communication Bus Wiring

	Manufacturer
	Part Number

	
	Regular Wiring
	Plenum Wiring

	Alpha
	1895
	-

	American
	A21451
	A48301

	Belden
	8205
	884421

	Columbia
	D6451
	-

	Manhattan
	M13402
	M64430

	Quabik
	6130
	-


The system elements are connected to the communication bus in a daisy chain arrangement.  The positive pin of each system element communication connector must be wired to the positive pins of the system elements on either side of it. This is also required for the negative and signal ground pins of each system element.  Wiring connections for CCN should be made at TB3.  Consult the CCN Contractor’s Manual for further information.

NOTE: Conductors and drain wire must be 20 AWG (American Wire Gage) minimum stranded, tinned copper. Individual conductors must be insulated with PVC, PVC/nylon, vinyl, Teflon, or polyethylene.  An aluminum/polyester 100% foil shield and an outer jacket of PVC, PVC/nylon, chrome vinyl, or Teflon with a minimum operating temperature range of –20 C to 60 C is required.  Wire manufactured by Alpha (2413 or 5463), American (A22503), Belden (8772), or Columbia (02525) meets the above mentioned requirements.

It is important when connecting to a CCN communication bus that a color coding scheme be used for the entire network to simplify the installation.  It is recommended that red be used for the signal positive, black for the signal negative, and white for the signal ground.  Use a similar scheme for cables containing different colored wires.  At each system element, the shields of its communication bus cables must be tied together.  If the communication bus is entirely within one building, the resulting continuous shield must be connected to a ground at one point only.  If the communication bus cable exits from one building and enters another, the shields must be connected to grounds at the lightning suppressor in each building where the cable enters or exits the building (one point per building only).  To connect the unit to the network:

1. Turn off power to the control box.

2. Cut the CCN wire and strip the ends of the red (+), white (ground), and black (–) conductors.  Substitute appropriate colors for different colored cables.

3. Connect the red wire to (+) terminal on TB3 of the plug, the white wire to COM terminal, and the black wire to the (–) terminal.

4. The RJ14 CCN connector on TB3 can also be used, but is only intended for temporary connection (for example, a laptop computer running Service Tool).

IMPORTANT:  A shorted CCN bus cable will prevent some routines from running and may prevent the unit from starting.  If abnormal conditions occur, disconnect the machine from the CCN Network.  If conditions return to normal, check the CCN connector and cable.  Run new cable if necessary.  A short in one section of the bus can cause problems with all system elements on the bus.

Carrier Comfort Network Interface Devices

Several options for interfaces to other Building Control Systems exist and are listed below.

BacLink™
BacLink functions as a gateway between a CCN and a BacNet system.   Information from the 30RAN chiller control to support the interface is listed in ?

DataLink™

DataLink is an interface device that allows other HVAC control systems to read and change “read/Write” values in system elements connected to a CCN bus.  This device requests data from a specified CCN system element and translates this data into ASCII characters off network.  Information from the 30RAN chiller control to support the interface is listed in ?

DataPort™

DataPort is an interface device that allow other HVAC control systems to “read only” values in system elements connected to a CCN communication bus.  Information from the 30RAN chiller control to support the interface is listed in ?

Cooler Heater (30GXN,GXR Only)

The 30GXN/GXR machines can be equipped with immersion heaters in the cooler water heads.  The number of heaters depends on the size of the machine.  The control system operates the heaters in response to the saturated suction temperature of each circuits as well as Entering and Leaving Water Temperature.  

The cooler heater will be energized if the unit is OFF (no mechanical cooling) and either of the following two conditions has been met: 

· The Saturated Suction Temperature in either circuit is less than BR.FZ Brine Freeze Point (Configuration Mode, Sub-mode SERV), and the unit has been off for more than 30 seconds.

· Entering or Leaving Water Temperature is less than BR.FZ + 3 ºF (1.7 ºC).  The heaters will remain on until both Entering and Leaving Water Temperatures equal or exceed 120 ºF (48.9 ºC).  The heaters will energize again when both water temperatures are below 110 ºF (43.3 ºC).  Cooler flow must be established in order to de-energize the cooler heaters.

· If the Entering or Leaving Water Thermistor has failed, the heaters will stay on.

The cooler heaters will be de-energized if the unit is ON (mechanical cooling is ON) or if the Saturated Suction Temperature for both circuits is greater than BR.FZ + 10 ºF (5.6 ºC).

Cooler Pump Control

ComfortLink machines are configured from the factory with the CPC Cooler Pump Control (Configuration Mode, Sub-mode OPT1) ON.  It is recommended that this option be used to control the chilled water pump.   If this option is not used, a 10-minute time delay is required before the chilled water pump is turned off.  This is required to maintain water flow during the pumpout cycle of the machine.

A field-installed relay, CWPR must be installed and connected between TB5-10 and TB5-12.  The relay should have coil voltage should be either 115 or 230 volts, depending on the unit’s control voltage.  Maximum coil ratings: 75 va sealed, 360 va inrush.

With this option enabled, the cooler pump relay will be energized when the machine enters an occupied period.  Other alarms, T120/121 Circuit A/B Low Saturated Suction Temperature, A207 Cooler Freeze Protection, will energize the cooler pump relay also, as an override even if the option is not enabled.

If the machine enters into a freeze protection mode, and turns the cooler heaters on as described in Cooler Heater (30GXN,GXR Only) on page 14, the cooler pump relay will be energized 15 minutes after the heaters have been energized.  When the Entering and Leaving Water Temperature reach 120 ºF (48.9 ºC), the cooler pump relay will de-energize.  The cooler pump relay will energize again if the Entering or Leaving Water Temperature falls to 110 ºF (43.3 ºC) or below.   

For machines in parallel flow without the benefit of isolation valves or machines installed in series, Cooler Pump Control enabled will cause nuisance alarms on the off chiller when it starts.  To correct this situation, change the Chilled Water Pump Relay to a Double-pole, single throw, normally open relay.  One relay contact should be used to control the Chilled Water Pump; the other should be added in series with the Chilled Water Pump Interlock to open the circuit when the machine is to be off.

Troubleshooting:

If the cooler pump relay is cycling the chilled water pump rapidly, check the chilled water flow switch for a short to ground.

Condenser Pump Control

ComfortLink 30HXC machines can be configured to control the condenser pump.

A field-installed relay, CNP-R must be installed and connected between TB2-7 and TB2-9.  The relay should have coil voltage should be either 115 or 230 volts, depending on the unit’s control voltage.  Maximum coil ratings: 75 va sealed, 360 va inrush. 

Several control options are available and are enabled with CNPC Condenser Pump Control (Configuration Mode, Sub-mode OPT1).  Condenser Pump Control is recommended to eliminate nuisance alarms during the pumpdown routine that runs when a circuit stops.  The factory default is “NO CONTROL”.  If NO CONTROL is selected, no signal to start the condenser pump will be sent.  If this option is used, external control of the condenser pump is required.  At least a ten (10) minute condenser pump off time delay must be used to prevent nuisance alarms during pumpdown, when the unit ends an occupied period.  “ON WITH MODE” energizes the condenser pump relay when the unit enters an occupied period.  “ON WITH COMPRESSOR(S)” energizes the condenser pump relay when a call for cooling is initiated and a compressor is started.  The condenser pump relay will be de-energized when the compressor is stopped.  With the implementation of Version 3.1 software the condenser pump relay de-energized ten (10) seconds after the compressor is stopped.

If the control detects a condenser freeze condition an override signal will be sent to the condenser pump relay. This override signal will be sent even if the option is not enabled, on all units TYPE Unit Type (Configuration Mode, Sub-mode UNIT) set for Fluid Cooled or Split System with HPCT Head Pressure Control Type (Configuration Mode, Sub-mode OPT1) set for Water Cooled.

Condenser Pump Interlock

ComfortLink 30HXC machines have an option to monitor a condenser water flow switch and auxiliary contact for proof of flow.  This option is not recommended for use on machines that utilize a water regulating valve or variable frequency drive pump control for head pressure control.  The use of these devices with the Condenser Pump Interlock may result in nuisance condenser flow alarms as the condenser water flow is restricted.  The option CNP.I Condenser Pump Interlock (Configuration Mode, Sub-mode OPT1) is factory defaulted to OFF.  Changing the point to ON enables the option.  The CNPC Condenser Pump Control (Configuration Mode, Sub-mode OPT1) must be “ON WITH MODE” or “ON WITH COMPRESSOR(S)” for this option to function.

The Condenser Water Flow Switch must be wired to TB2-5 and TB2-6.  

Service Bulletins pertaining to this control option:

· SMB01?? – ComfortLink Main Base Board Software

This bulletin addressed the versions of screw software.

Demand Limit

4-20 Demand Limit

The Energy Management Module is required for this option.  This option is designed for 4-20 ma input.  Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used.

Head Pressure Control

30GXN/GXR

The early production 30GXN/GXR machines used the MotorMaster III.  Beginning with serial numbers 0702F, MotorMaster V starting in production as the head pressure control device.

In software versions prior to Version 4.0, there is no minimum fan speed for the ComfortLink Screw MotorMaster.  If the fan speed is less than 25% for 2 minutes, then a fan stage is shut off.

30HXA

The 30HXA has a number of condenser control options to choose from with the ComfortLink Control System.  

Two outputs are provided for 30HXA's so a Motormaster or Variable Frequency Drive can be used for each circuit, if desired.  This can be configured under HCPT Head Pressure Control Type (Configuration Mode, Sub-mode OPT1) to INDEPENDENT TOWER ENABLE.  

If a common condenser output is desired, configure the control under HCPT Head Pressure Control Type (Configuration Mode, Sub-mode OPT1) to COMMON TOWER ENABLE.  With this configuration the control averages the Saturated Condensing Temperatures of both circuits.  The control output is on circuit A TB2-14 and TB2-15.

30HXC

The 30HXC can control a condenser water valve from the ComfortLink Control System.  

The A circuit variable head pressure output controls the condenser water

valve, TB2-14 and TB2-15.  A milliamp signal is always provided and can be

configured for 4-20 mA, 0-20 mA,  or 20-0 mA.  The circuit with the lowest condensing temperature has control of the condenser water valve.  If either circuit’s Saturated Condensing Temperature rises above 105 ºF (39 ºC) then control of the valve is shifted to that circuit.  On 3 compressor machines, if both circuits are running, A circuit is always used.  The variable HD.P.A Head Pressure Setpoint A, and HD.P.B Head Pressure Setpoint B (Set Point Mode, Sub-mode HEAD) is the controlling set point.  Original default was 113 ºF (45 ºC).  This has been changed to 85 ºF (29 ºC).  

With the implementation of Version 4.0 software, the condenser control valve operation was modified to add a one minute delay before the Saturated Condensing Temperature of the starting circuit can contribute to the valve position, unless Saturated Condensing Temperature is greater than the running circuit's Saturated Condensing Temperature.  This was done to eliminate the nuisance High Head Pressure Trips of the operating circuit.  The problem was encountered when a circuit starts while the other is running.  The water valve closes, since the starting circuit's head pressure is low.  This causes the running circuit to fail on high head pressure.

To minimize the chance for a nuisance low oil pressure alarm, do not set the variable HD.P.A Head Pressure Setpoint A, and HD.P.B Head Pressure Setpoint B (Set Point Mode, Sub-mode HEAD) below 80 ºF (26.7 ºC).

Master/Slave Operation

ComfortLink allows the two machines to operate as one in either series or parallel flow.  Duplex machines are intended for series flow only.

Configuration

Each machine must be configured to operate as in Master/Slave Operation.

Series Flow

For Series Flow, the master chiller must be the downstream machine.

Parallel Flow

For Parallel Flow, either machine can be the Master Chiller.

Sequence of Operation 

Series Flow

When the lead machine starts in Master/Slave Control, it will load fully before the lag chiller starts after the LLDY Lead/Lag Start Delay (Configuration Mode, Sub-mode RSET).  Once the chillers are fully loaded and the load is decreasing, the Master/Slave algorithm will unload lead and lag machine circuits before shutting down a circuit.  

Suggested Operating Scheme

CCN Control

With the Master chiller configured for CCN control and the Slave chiller configured for switch control normal operation was observed when the CHIL_S_S point on the Master chiller was toggled from ON to OFF. The only operational point to be concerned about is when the Master chiller had the power turned off the Slave chiller continued to run as a stand alone machine. The only way to stop the Slave at that point was to turn the

remote-off-enable switch to off.

If both the Master and Slave Chillers are configured for CCN control both chillers must have the CHIL_S_S enabled and disabled simultaneously in order for the machines to function properly. This way if communication was lost with the Master chiller the Slave chiller could be disabled via communications.

Only the Master chiller control point should be forced. The Master controls the Slave chiller by changing the control point so a force should not be applied to the Slave chiller.

The most reliable control method to start and stop the chillers is by hard wiring a control relay to the remote start/stop termination points provided on each machine.  The master and slave chillers would be started and stopped together by a single relay.
Troubleshooting:

Master/Slave Control does not work.

· Confirm that the machines have been set up properly.  Parallel flow configuration requires a dual chiller LWT sensor installed in the common supply header connected to the Master chiller.  Series flow requires the Master chiller be the downstream machine.

· Confirm that there is not a temperature set point force imposed by a CCN device.  Imposing a force on the set point temperature disables the Master/Slave algorithm and the machines will operate as stand-alone machines.

· Software Versions prior to Main Base Board (MBB) Version 2.0 did not allow for Master/Slave Operation.

· For parallel flow, confirm that the Dual Leaving Water Temperature Thermistor is operational.  If this sensor fails, the Master/Slave Algorithm will be disabled and the machines will operate as stand-alone machines.

· Confirm that the CCN wiring between the two machines is correct and functional.

· In MBB Version 2.0 and 3.1 software, any alarm on the Master chiller, both circuits down, will cause the slave chiller to stop also.

Navigator

The Navigator module provides a mobile user interface to the ComfortLink control system.  The display has up and down arrow keys, an [ENTER] key, and an [ESCAPE] key.  These keys are used to navigate through the different levels of the display structure.  Press the [ESCAPE] key until ‘Select a Menu Item’ is displayed to move through the top 11 mode levels indicated by LEDs on the left side of the display.  

Once within a Mode or sub-mode, a “>” indicates the currently selected item on the display screen.  Pressing the [ENTER] and [ESCAPE] keys simultaneously will put the Navigator into expanded text mode where full meaning of all sub-modes, items and their values can be displayed.  Pressing the [ENTER] and [ESCAPE] keys when the display says ‘Select Menu Item’ (Mode LED level) will return the Navigator to its default menu of rotating display items (those items in the VIEW sub-mode under the Run Status mode).  In addition, the password will be disabled requiring that it be entered again before changes can be made to password protected items.  The Service Test function should be used to verify proper protected items.  Press the {ESCAPE] key to exit out of the expanded text mode.

NOTE: When the LANG Language Selection (Configuration Mode, Sub-mode DISP), variable is changed, all appropriate display expansions will immediately change to the new language.  No power-off or control reset is required when reconfiguring languages.

When a specific item is located, the item name appears on the left of the display, the value will appear near the middle of the display and the units (if any) will appear on the far right of the display.  Press the [ENTER] key at a changeable item and the value will begin to flash.  Use the up and down arrow keys to change the value, and confirm the value by pressing the [ENTER] key.

Two items, OAT Outside Air Temperature (Temperature Mode, Sub-mode UNIT) and SPT Space Temperature (Temperature Mode, Sub-mode UNIT) can be forced to a value at the Navigator.  If one of these two points has been forced, a flashing “f” indicating the force will appear next to the value.  To remove the force, select the item.  Press the [ENTER] key so that the value is flashing.  Press the up and down arrow keys simultaneously and the force will be removed.

Changing item values or testing outputs is accomplished in the same manner.  Locate and display the desired item.  Press [ENTER] so that the item value flashes. Use the arrow keys to change the value or state of an item and press the key to accept it.  Press

the [ESCAPE] key to return to the next higher level of structure.  Repeat the process as required for other items.

Items in the Configuration and Service Test modes are password protected.  The words ‘Enter Password’ will be displayed when required, with the default password also being displayed.  Use the arrow keys to change the number and press [ENTER] to enter the digit.  Continue with the remaining digits of the password.  The default password is 1111.  The password can only be changed at the Navigator or through CCN devices such as ComfortWORKS®, ComfortView™ and Service Tool.

Adjusting the Contrast

The contrast of the display can be adjusted to suit ambient conditions.  To adjust the contrast of the Navigator, press the [ESCAPE] key until the display reads, “Select a menu item.”  Using the arrow keys move to the Configuration mode.  Press [ENTER] to obtain access to this mode.  The display will read:


>
TEST 
OFF



METR 
OFF



LANG
ENGLISH

Pressing [ENTER] will cause the “OFF” to flash.  Use the up or down arrow to change “OFF” to “ON”.  Pressing [ENTER] will illuminate all LEDs and display all pixels in the view screen.  Pressing {ENTER] and {ESCAPE] simultaneously allows the user to adjust the display contrast.  The display will read:



Adjust Contrast



- - - + - - - - - - - - - - - -

Use the up or down arrows to adjust the contrast.   The screen’s contrast will change with the adjustment.  Press [ENTER] to accept the change.  The Navigator will keep this setting as along as it is plugged in to the LEN bus.

Adjusting the Backlight Brightness

The backlight of the display can be adjusted to suit ambient conditions.  The factory default is set to the highest level.  To adjust the backlight of the Navigator, press the [ESCAPE] key until the display reads, “Select a menu item.”  Using the arrow keys

move to the Configuration mode.  Press [ENTER] to obtain access to this mode.  The display will read:


>
TEST 
OFF



METR 
OFF



LANG 
ENGLISH

Pressing [ENTER] will cause the “OFF” to flash.  Use the up or down arrow keys to change “OFF” to “ON”.   Pressing [ENTER] will illuminate all LEDs and display all pixels in the view screen.  Pressing the up and down arrow keys simultaneously allows the user to adjust the display brightness.  The display will read:



Adjust Brightness

- - - - - - - - - - - - - - +

Use the up or down arrow keys to adjust the brightness.  The screen’s brightness will change with the adjustment.  Press [ENTER] to accept the change.  The Navigator will keep this setting as along as it is plugged in to the LEN bus.

Changing the Password

The password for the 30GXN/GXR and 30HXA/HXC ComfortLink machines can be changed in the field with the Navigator.  The procedure is outlined below.

1. Enter the correct password under PASS, Service Password (Configuration Mode, Sub-mode DISP).

2. Change PAS.E Password Enable (Configuration Mode, Sub-mode DISP) to DSBL.

3. Return to the PASS, Service Password, and change the password to the desired value.  For this example, 2222.  Once changed, the screen will show the desired value, 2222.

4. Return to the PAS.E Password Enable, and change the value to ENBL.  

The password has been changed.  If the password is required, the machine will show the default 1111 as the password.  Use the up or down arrow keys to change the value to the correct password.

Oil Heaters (30GXN,GXR Only)

All 30GXN/GXR machines are equipped with contact oil heaters on the oil separator.  The control system operates the heaters in response to the saturated condensing temperature.  The heater will be energized if the Discharge Gas Temperature is less than 105 (F (40.6 (C).  The heaters will be de-energized when the Discharge Gas Temperature is above 110 (F (43.3 (C).  If the oil level switch for a circuit is open, that circuit’s heater will not be energized.  If the machine is in Service Test mode [Service Test, Sub-mode Test], the oil heaters will not be active.

The 30G,H-8T Controls & Troubleshooting book and prior revisions incorrectly listed the control point as the saturated condensing temperature.

Operating Modes

ComfortLink controls provide information about capacity control overrides as indicated by Operating Modes. 

MD01 – FSM Controlling Chiller

This operating mode indicates that a Flotronic System Manager (FSM) is configured to be in charge of loading the chiller and the controller is responding to these commands.  If the FSM stops communicating with the chiller, then the mode is disabled and the chiller will operate as a stand-alone chiller.

The unit’s capacity may be reduced while this mode is in effect.

MD02 – WSM Controlling Chiller

This operating mode indicates that a Water System Manager (WSM) is configured to be in charge of loading the chiller and the controller is responding to these commands.  If the WSM stops communicating with the chiller, then the mode is disabled and the chiller will operate as a stand-alone chiller.

The unit’s capacity may be reduced while this mode is in effect.

MD03 – Master/Slave Control

This operating mode indicates that the local dual chiller algorithm is controlling the chiller.  The Master chiller will display this mode at all times, regardless of occupancy.  The Slave chiller will display this mode only when the machine is in an occupied period only.

MD04 – Low Source Protection

This operating mode is for heat machines only.   In heating mode, if the cooler Leaving Water Temperature  (LWT) is less than the smallest LWT set point, then this mode is in effect.  A stage will be removed every 30 seconds until the LWT is above the set point.

MD05 – Ramp Load Limited

This operating mode indicates that the unit’s capacity is being limited by Ramp Loading. At least one stage must be on and RL.S Ramp Load Select (Configuration Mode, Sub-mode SLCT) must be ENBL, for this mode to be in effect.  If the Leaving Water Temperature is more than 4 (F (2.2 (C) above the CTPT Control Point (Run Status Mode, Sub-mode VIEW), and the negative rate of change of LWT is less than CRMP (Configuration Mode, Sub-mode SLCT), no additional stages of capacity will be added.  

In the following example, the Ramp Load function is enabled, Cooling Ramp Loading is set for 1.0 (F/minute (0.5 (C/minute), and the Set Point is 44 (F ( 6.6 (C).  At the start of the first stage of capacity, the Leaving Water Temperature is 54 (F (12.2 (C) and 30 seconds later the leaving water temperature is 53.8 (F (12.1 (C).  The negative rate of change is 0.4 (F/minute (0.2 (C/minute).  In this example, the operating mode will be in effect, and no further stages will be added.

The unit’s capacity may be reduced while this mode is in effect.

MD06 – Timed Override In Effect

The operating mode indicates that a Carrier Comfort Network device, such as Building Supervisor or ComfortWorks has initiated a schedule override for a specified period of time.  Timed Override cannot be accessed through the Navigator.

MD07 – Low Cooler Suction TempA

MD08 – Low Cooler Suction TempB

This operating mode is a cooler freeze protection control mode.   

This operating mode is in effect if during the first three (3) minutes that the circuit is on, the Saturated Suction Temperature is less than the BR.FZ Brine Freeze Point (Configuration Mode, Sub-mode SERV). During this condition, no additional stages will be added.

If the saturated suction temperature is less than the BR.FZ Brine Freeze Point (Configuration Mode, Sub-mode SERV), then the unit will be put into close control, and the mode will be active.  Close control will allow the unit to use stages that otherwise would not be considered valid.

At any time a compressor is on in the circuit and the saturated suction temperature is at least 6 (F (3.3 (C) less than the BR.FZ Brine Freeze Point (Configuration Mode, Sub-mode SERV) for 1 minute, then the mode is active.  A capacity stage is removed from the circuit.  If both circuits have the mode at the same time, a capacity stage is alternately removed every minute.  If this condition is not remedied within a specified amount of time, the corresponding T120/T121 Circuit A/B Low Saturated Suction Temperature Alert.  

The unit’s capacity may be reduced while this mode is in effect.

MD09 – Slow Change Override

This operating mode prohibits the control from adding a capacity stage needlessly.  If the Leaving Water Temperature is near the CTPT Control Point (Run Status Mode, Sub-mode VIEW), and is not moving rapidly away from the Control Point.  This mode will be active and will prohibit the controller from adding a stage needlessly.  For instance, if EWT/LWT = 50/44.2, and the Control Point is 44, and the LWT is not changing, then the integrator would eventually call for another stage to be added.  Slow change override keeps it off.

MD10 – Minimum Off Time Active

This operating mode indicates that the unit start has been delayed by a configured time period, DELY Minutes Off Time (Configuration Mode, Sub-mode OPT2).  

MD11 – Low Discharge Superheat A

MD12 – Low Discharge Superheat B

This operating mode is a protection mode for the machine.  This mode algorithm is active only when the circuit on and has been running for at least 3 minutes.  If the discharge superheat is less than 5 degrees and decreasing, then a stage will be removed in an attempt to increase the discharge superheat, unless the control is at the last stage of the circuit.  The unit will be placed into close control.

If both circuits are in low discharge superheat, then stages will be alternately removed every 30 seconds.

If there is a request to add a stage of capacity to the circuit, and the discharge superheat is less than 15 degrees, then the stage will not be added.

The unit’s capacity may be reduced while this mode is in effect.

MD13 – Dual Setpoint

This operating mode is displayed if the control is configured and operating at a set point other than single set point control, CLSP Cooling Setpoint Select (Configuration Mode, Sub-mode SLCT).

The unit’s capacity may be reduced while this mode is in effect.

MD14 – Temperature Reset

This operating mode indicates that the unit’s capacity will be reduced due to chilled water temperature reset, either by return water, Outdoor Air, Space Temperature or from a temperature reset command from an external building automation system.

The unit’s capacity may be reduced while this mode is in effect.

MD15 – Demand Limit In Effect

This operating mode indicates that the unit’s capacity will be reduced due to a demand limit command from an external building automation system.

The unit’s capacity may be reduced while this mode is in effect.

MD16 – Cooler Freeze Protection

This operating mode occurs at the same time as the A207 - Cooler Freeze Protection Alarm is indicated.  This mode is enabled when the cooler entering or leaving water temperature is below BR.FZ, Brine Freeze Point (Configuration Mode, Sub-mode SERV) plus 2 (F (1.1 (C).  When this condition is encountered, the machine will enter Mode 16, and the Chilled Water Pump relay will be energized, even if the CPC Cooler Pump Control (Configuration Mode, Sub-mode OPT1) is OFF.  The unit will be shut down or prevented from starting.

The control disable the mode automatically if the leaving chilled water temperature rises above the CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL) plus 6 (F (3.3 (C). 

MD17 – Lo Tmp Cool/Hi Tmp Heat

This mode is not in the ComfortLink software.  The actions are taken, but the mode is not displayed.

If the Entering Water Temperature is less than the set point, then a stage of capacity is removed every 30 seconds until the Entering Water Temperature is above the set point.

If, 


[image: image2.wmf](

)

75

.

43

%

2

´

-

´

-

<

Capacity

Total

e

Temperatur

Water

Leaving

e

Temperatur

Water

Entering

e

Temperatur

Water

Leaving

and the rate of change of the Leaving Water Temperature is less than –0.5 (F/minute (‑0.28 (C/minute), or 


[image: image3.wmf](

)

75

.

43

%

3

´

-

´

-

<

Capacity

Total

e

Temperatur

Water

Leaving

e

Temperatur

Water

Entering

e

Temperatur

Water

Leaving

and the rate of change of the Leaving Water Temperature is less than 0.0 (F/minute (0.0 (C/minute), a stage will be removed.

MD18 – Hi Tmp Cool/Lo Tmp Heat

This operating mode will be displayed if the Leaving Water Temperature is above the set point and is moving away from the set point rapidly.  If this condition is detected, the control will add a stage of capacity.  

MD19 – Making Ice

This operating mode indicates that the machine is in the ice building mode.  The unit is configured to make ice, ICE.M Ice Mode Enable (Configuration Mode, Sub-mode OPT2) set to YES, the unoccupied cooling set point is in effect and the Ice Done Switch is open.  When this mode is in effect, CSP3 Cooling Setpoint 3 (Set Point Mode, Sub Mode COOL), the Ice Making Set Point is in effect.

MD20 – Storing Ice

This operating mode indicates that the machine is in the ice storing mode.  The unit is configured to make ice, ICE.M Ice Mode Enable (Configuration Mode, Sub-mode OPT2) set to YES, the unoccupied cooling set point is in effect and the Ice Done Switch is closed.  When this mode is active, CSP2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL) is in effect.

MD21 – High SCT Circuit A

MD22 – High SCT Circuit B

This operating mode is a protection mode to allow the machine to operate at a limited capacity when the Saturated Condensing Temperature (SCT) approaches a predetermined limit.  This mode will only be checked if the circuit is on.  The control will unload the affected circuit and throttle the Saturated Suction.  While in this mode, no additional capacity stages will be added to the affected circuit.  If the machine is running at the lowest stage, the High SCT mode is not utilized.  

The Maximum Condensing Temperature is a value that is a non-accessible from a LEN device and defined in the table below:

	Unit
	Maximum Condensing Temperature

	30GXN/GXR
	154 (F (68 (C)

	30HXA
	152 (F (67 (C)

	30HXC
	122 (F (50 (C)


This mode will be enabled if:  the Saturated Condensing Temperature (SCT) is greater than (Maximum Condensing Temperature – 12 (F (6.6 (C)) and the capacity is increasing; or Saturated Condensing Temperature (SCT) is greater than (Maximum Condensing Temperature – 4 (F (2.2 (C)) and the Saturated Suction Temperature (SST) is greater than the Maximum Saturated Suction Temperature, 52 (F (11.1 (C).  This mode will stay active until both of the conditions above are no longer true.

The control’s response depends on a number of conditions.  If the SCT is greater than (Maximum Condensing Temperature + 2 (F (1.1 (C)) for one (1) minute, then reduce the capacity by turning off a loader.  If the SCT is greater than (Maximum Condensing Temperature + 5 (F (2.8 (C)), turn off a loader if one is on, otherwise stop the circuit and generate the appropriate alert, T126/T127 Circuit A/B High Discharge Pressure Alert.

MD23 – High Motor Current Cir. A

MD24 – High Motor Current Cir. B

This operating mode is a protection mode to allow the machine to operate at a limited capacity when a compressor on a circuit is approaching its Must Trip Amp (MTA) value.  Compressor MTA values are listed CM.A1 Compressor A1 Must Trip Amps, CM.A2 Compressor A2 Must Trip Amps, CM.B1 Compressor B1 Must Trip Amps, and CM.B2 Compressor B2 Must Trip Amps (Configuration Mode, Sub-mode UNIT).  The mode is enabled when a compressor’s current approaches 83% of MTA.  The mode will remain in effect until the current drops below 55% of MTA or has not increased over the last 30 minutes.  While this mode is in effect, the circuit will not be allowed to stage to a higher level.

MD25 – Ckt A Off Ref Flow Delay

MD26 – Ckt B Off Ref Flow Delay

These two modes were added in MBB Version 4.0 software.  These modes indicate a Loss of Refrigerant Flow Alert condition was detected by the control.  See P998 – Pre-Alert Loss of Refrigerant Flow - Circuit A

T998 – Loss of Refrigerant Flow - Circuit A Alert
 and P999 – Pre-Alert Loss of Refrigerant Flow - Circuit B

T999 – Loss of Refrigerant Flow - Circuit B Alert
 on page 83 for alert criteria.  These modes indicate that a 15 minute time delay is in effect before another circuit start attempt is initiated.

MD27 – Circuit A Pumping Out

MD28 – Circuit B Pumping Out 

This mode was added in MBB Software Version 4.0 is active when the pumpout routine is in control before the circuit is shutdown.  See T135 - Circuit A Failure to Pumpout Alert and T136 - Circuit B Failure to Pumpout Alert on page 67 for pumpout criteria.

MD29 – Unit OFF: No Water Flow

This mode was added in MBB Software Version 4.0 and is indicated when an A201 – Cooler Pump Interlock Failure Contacts Open During Normal Operation alarm condition has been detected.  See A201 – Cooler Pump Interlock Failure Contacts Open During Normal Operation Alarm on page 79 for alarm criteria.  The control will delay indicating an A201 alarm for five (5) minutes for flow to be established again, during which time this mode will be active.  If flow has not been established within five (5) minutes, an A201 alarm will be indicated.

Software Revisions

There have been a number updates to the 30GX/HX ComfortLink Main Base Board Software.  Outlined below is a summary of the changes with its implementation date.

Version 4.5 

Serial Number Start:  Service Release

· Addition of pre-alarms for compressor no motor current while running.  The remote alarm is not turned on, no message on CCN.  Alarm is in the current alarm list for two minutes, also in alarm history.  Navigator alarm light flashes.  After two minutes, the compressor is allowed to restart (return to normal is not sent on CCN).  If on the subsequent restart, no motor current is detected by the TI board within the first 15 seconds, the failure is treated as an alarm (remote alarm is turned on, messages are sent on CCN).  

· The upper limit on current unbalance has been changed from 25 to 30%.

· Alerts 98/99 (Economizer pressure is less than 12 psi below suction pressure) have the timing changed from 6 to 15 seconds before the alarm occurs.

· Occupancy POC sends the properly formatted NACK message (this was causing problems with Data Port).

Version 4.3 

Serial Number Start:  Service Release

· Variables SIZE_DPX, SIZEADPX, CAPT_DPX, CAPA_DPX (total size of the dual chiller, available size of the dual chiller, total capacity in use by the dual chiller, and available capacity in use by the dual chiller) have been added.  They appear in the DUALCHIL table.  As with our other dual chiller parameters, they do not appear on the Navigator.  The CSM gets these values reported when it is communicating with a master chiller and the master chiller is not in standalone mode.  If the master chiller is in standalone mode, then only the master chiller size and capacities are communicated to the CSM.

· Use of the wear factor has been changed to equalize the compressor hours/starts. 

· The 10 minute low discharge superheat timer will not start during the first 3 minutes after a circuit starts.  Thus, at startup we won't fail on low discharge superheat for 13 minutes.

· Loss of water flow while pumping out will be detected if chilled water pump control is disabled. 

· Fixed a bug introduced in 4.0 that skipped the check for SST < 9 degrees prior to failing the level sensor. This eliminates liquid level sensor failure alarms in brine applications.

· Fixed a bug that if the level sensor is disabled or broken, the discharge superheat control will only override the level sensor calculation if the discharge superheat control is +/- 5 degrees away from the setpoint.  The effect of this problem is that the EXV would hunt when in DSH control. 

· MCT_SP modified for HXC to default to 118, HXA defaults to 145, GX defaults to 152 (unchanged).  MCT_SP can be lowered (down to 100 dF), but not raised above the default.  Unit stops loading at 6 dF below MCT_SP for HXC and water cooled HXA, 12 dF for GX and air cooled HXA (unchanged). Note:  For this and the previous version, make sure that you check MCT_SP.  This value will be written by the SCP file on units that leave the factory; that work will be done after the "field qualification" phase.

· Added loading on high temperature override when DT > 6, unless ramp loading is enabled.  Makes the fast load algorithm equivalent to Global Chiller fast load algorithm, and allows ramp loading to work (fixes problem Global Chiller had). 

· Navigator will now display up to 50 alarms in the alarm history buffer.

Version 4.0 (CESR-131248-04-00)

Serial Number Start:  1302F (30GXN/GXR), 1302Q (30HXA/HXC)

· The machine would not restart after a brief power interruption.  This was caused by the MBB not seeing the power loss, while the TI board did.  It has been fixed by having the MBB receive information from the TI board that it has seen a power loss.  The MBB will then restart the unit.

· In a dual chiller configuration, the slave chiller was disabled when the master chiller fails.  Now, the slave goes into standalone mode when the master chiller fails.
· To accommodate ice storage applications, the following problem is addressed:

· The unit unloads when LWT is less than the freeze variable plus two degrees F.  Freeze was previously defined as the lowest of CSP1 and CSP2, without regard to CSP3 (the ice duty set point).  This is now defined as BRN_FRZ, the brine freeze set point, which is independent of any of the cooling set points, and can be changed to reflect the amount of antifreeze that has been added to the water loop.  
· Illegal configuration descriptions have been changed from providing a number (e.g.  “Illegal Configuration – 1”) to providing a text description of the problem (“Illegal Configuration – Invalid Unit Type”).  Note that at this time, all illegal configurations except –-01 (Invalid Unit Type) have been translated into the three non-English languages that are supported.

· A problem with the oil pump coming on when the compressor alarms on a High Pressure Switch Trip has been addressed.  The logic now requires that the compressor feedback be on before the oil pump can be commanded on due to low oil pressure. 

· The alarm history buffer size has been increased to 50 and cannot be reset. RHIST has been removed.

· Compressor startup sequence modifications:

· Delay compressor start for 10 seconds after oil solenoid is energized. 

· Oil pump remains on for two minutes after startup of the lead compressor.

· The STAT point was not being displayed properly when reading point with BEST++. 

· On 3 compressor units, stray current readings (<1 amp) on B2 compressor cause high current mode 24 to occur, which did not allow the circuit to stage any higher.  Current is now ignored for compressors that are not configured. 

· Added a check for both circuits to be on prior to averaging the saturated condensing temperature readings for each circuit when Head Pressure Control Type (HPCT) is configured for COMMON EVAP.

· Algorithm added to cycle the cooler water pump when the SST is low (brine freeze setpoint – 6 (F), but the chilled water temperature is high.  Previously, the pump was left on, which was causing some jobs to experience very high water temperatures when the chiller was being started. If the machine is off and entering and leaving water temperatures are both greater than 65.5 (F for 5 continuous minutes, then the pump will be shut off for 30 minutes. The pump will then be re-energized until the water temperatures are both greater than 65.5 (F for 5 minutes. 
· The 30 minute OFF, 5 minute ON cycle will be repeated during this mode.

· Clear the Lead/Lag Thermistor Failure Alert (T079) when dual chiller mode is disabled.

· Added maintenance screen with hours and starts that can’t be modified. Accessible via CCN.

· Lead/Lag Balance Select (LLBL) and Variable Head Pressure Select (VHPT) show numbers on Navigator, changed to description.

· Active Demand Limit now displayed on Navigator.

· Minutes left for start now displayed on Navigator.

· Minutes off delay now works when last compressor cycles off and power up.

· Failure to Pumpout Alerts (T135 & T136) have been eliminated. Loaders now assist after two minutes of pumpout.  No alert generated.  Pumpout failure incidences displayed in MISCDATA table. Accessible via CCN. 

· A202 (Cooler Pump Interlock Failure Contacts Closed While Pump is OFF) does not occur if CHIL_S_S is toggled from ON to OFF then to ON before the chiller has shut down.
· Non-CCN jobs cannot configure daylight savings time. Added BCST broadcast configuration to Navigator.
· Return temperature reset now works correctly when METRIC units are selected.

· Default minimum water valve position for brine units is now 25%. (30HXC)

· Keep condenser pump on for brine units even when not running. (30HXC)

· Enable the TI boards appropriately when number of compressor in the circuit is configured.

· Added a “Winterization Required” Alert. Alert is displayed; unit is allowed to run.  Configurable (enable/disable). Software logs time of message, time winterization completed, and if the configuration has changed.

· The alarm output is now configurable. Alarm Relay Usage (ALR.C) has been added under Configuration/OPT2. Configuration options, Alerts and Alarms, Alarms only, Off.

· CCN Usage, 0 = Alerts and Alarms energize the relay, 1 = Alarms Only, 2 = Off.
· Oil pressure maximum threshold increased to 5 psi, previously 2.5 psi (to check for leaking oil solenoid).

· Fixed problem when the chiller is configured in the CSM list, but not selected as being active, repeated “FSM Loss of Communication Alert” (A951) would occur.

· Allow liquid level sensor to be disabled. Machine will operate on discharge superheat control when disabled.

· High Oil Filter Pressure Drop alert changed to manual reset. Previously it was automatic so it would not show up under current alarms.  Persistence time was increased from 60 seconds to 300 seconds.

· Change FSM references to CSM.

· Default Head Setpoint for 30HXC’s was changed from 113 ºF to 85 ºF.

· When testing compressors water pump never came on, alarm 200 was activated.

· 30HXC units configured for brine, when condenser flow is lost the cooler pump output is immediately de-energized. Condenser interlock must be enabled. A condenser flow switch must be installed. Chilled water pump control is required.

· 30HXC units configured for brine, keep the condenser pump on for 30 minutes after a normal shutdown.

· For brine 30HXC units, liquid line solenoids will be standard equipment.  When condenser flow is lost, de-energize the LLSV’s (shutting off the compressors and cooler pump simultaneously).

· Modified 30HXC water valve head pressure control algorithm. Added a one minute delay before the SCT of a starting circuit will be able to contribute to the valve position (unless SCT is higher than the running circuit’s SCT). When one circuit starts while the other is running the water valve closes, since the starting circuit’s head pressure is low.  This causes the running circuit to fail on high head pressure.

· Condenser interlock will now function correctly without condenser pump control enabled. When condenser pump control is not enabled and condenser interlock is enabled, 5 minutes is allowed at startup for the flow switch to make.  Until the flow switch makes, compressors are not allowed to run. This does not apply for CNPC = 2 (condenser pump on with compressors).

· Add Mode 25 CKT A OFF REF FLOW DELAY & Mode 26 CKT B OFF REF FLOW DELAY to indicate that a loss of refrigerant flow has been detected and a 15 minute delay is in effect.

· Add Mode 27 CIRCUIT A – PUMPING OUT & Mode 28 CIRCUIT B – PUMPING OUT to indicate that circuit is pumping out before shutting down. 

· Change wording on VHPT configuration options from (4 – 20 mA, 0 – 10 V, 10 – 0 V) to (4 – 20 mA, 0 – 20 mA, 20 – 0 mA).

· For the first no refrigerant flow failure (T998 & T999), do not generate an alarm.  Only generate an alarm if the second failure occurs after a 15 minute delay.
· If a circuit is in low discharge superheat capacity limiting and the MLV (if installed) is on, do not cycle the MLV off until low DSH is no longer in effect.
· Upgrades for Motormaster V. Changes made to head pressure control algorithms to enhance stability. Will be helpful for existing units using Motormaster III.

· Ignore the cooler flow switch for first 15 seconds.  Corrected problem where switch would momentarily make then drop out and alarm.
· Mode 1 (CSM CONTROLLING CHILLER) not set when CSM is in control of the chiller.
· Cooler heater is energized if (SST < brine freeze) or (EWT or LWT < brine freeze + 3). This corrects problem of cooler freeze protection alarm being generated before cooler heaters were energized.
· Corrected problem where Alarm 202 would occur if the unit was in SST freeze when the state transitioned from OFF to ON.
· 30HXC units configured for brine will not pump out if the brine freeze point (BR.FZ) is 25 degrees or less.
· Added SMZ to the Navigator Display.
· Added Circuit A Starts & Circuit B Starts to Navigator Display. 
· EXV minimum position has been modified so if more than one stage is on in a circuit, the EXV is not allowed to go below the configured minimum position.  MLV is not considered a stage, so you have to have at least one loader on (or two compressors) before the minimum is honored.

Version 3.1 (CESR-131248-03-01)

Serial Number Start:  1301F (30GXN/GXR), 2001Q (30HXA/HXC)

· Fast Load Algorithm implemented.  This new algorithm allows the machine to stage quicker.

· A No Refrigerant Flow Algorithm was added to the control logic.  The logic protects the compressor from no refrigerant flow conditions.  The algorithm will shut down the affected circuit if the Saturated Suction Temperature is less than 0 (F (-18 (C) and if the rate of change is negative in 5 second increments between 40 and 90 seconds.  If this condition is encountered, the machine will alert on T998 – Circuit A No Flow or T999 – Circuit B No Flow.

· Dual Chiller operation is disabled if the dual leaving chilled water sensor fails.

· Alarm 60-2 was changed to Manual reset.

· If the machine is configured for condenser pump control on with compressors, the condenser pump will remain on for 10 seconds after the compressor(s) have shut off.

· Variable Head Pressure Control algorithm for 0 to 10 vdc and 10 to 0 vdc was corrected.

· If a condenser freeze alarm, A128 (Circuit A Condenser Freeze Protection) or A129 (Circuit B Condenser Freeze Protection) is indicated, the condenser water valve will be commanded to the 100% position.

· If the machine is configured for brine operation, the motor cooling set point is set to 170 (F (76.7 (C).   If the machine is changed to water operation, the motor cooling set point is set to 200 (F (93.3 (C).

· If configured for dual chiller, if the Master chiller is commanded down, the slave chiller shuts down also.    

Version 2.0 (CESR-131248-02-00)

Serial Number Start:  5100F
· Dual Chiller Operation has been implemented.  This control feature allows for the dual chiller operation in parallel or series piping arrangements.

· Brine Freeze Point, BR.FZ (Configuration Mode, Sub-mode SERV) lower limit now matches the Controls and Troubleshooting Guide, -20 ºF (-28.8 ºC).

· Test mode now allows for the energizing of the minimum load valve when the compressors are on.  This is necessary for the proper set-up of the option.

· The pumpout routine has been changed.  Pumpout will terminate when the Saturated Suction Temperature (SST) falls by 10 ºF (5.5 ºC) or reach the Brine Freeze Set Point - 6°F (3 (C).  The control expects this to take place within 360 seconds.  If this does not occur, the alarm will not lock out the machine.

· Condenser Freeze Alarms A128 and A129 will no longer be displayed if the machine is configured for brine operation.  Condenser Pumps should be running continuously on brine operation machines in accordance with the Installation Instructions.

· Discharge Superheat Set Point, DIS.S (Configuration Mode, Sub-mode UNIT) was changed from ºF to (F.  This was causing a conversion error when the control was switched to metric units.

· Head Pressure Control, 4-20 ma and 0-10 vdc control schemes for Split Systems (30HXA) are now available.

· Revised the available capacity to account for a circuit failure.  Revised the Percent Total Capacity, CAP (Run Status Mode, Sub-mode VIEW) to account for the minimum load valve operation.

· Low Oil Level Alerts, T124 and T125 cannot be cleared until the oil level switch closes.

· Alarm 152, Circuit A & B OFF for Alerts, Unit down are no longer posted unless there is an FSM controlling the unit.  This was done to increase the alarm history buffer.

· Alerts 98-2 and 99-2 Economizer Pressure Transducer Failure (Economizer Pressure < Suction Pressure -12 psig) is only checked when a compressor on that circuit is active.

· Revised the configuration for split systems to allow for Fan Staging Select, FAN.S (Configuration Mode, Sub-mode UNIT) to be None, as stated in the Controls and Troubleshooting Book.

· When Cooler Pump Control, CPC (Configuration Mode, Sub-mode OPT1) is enabled, the cooler pumps will remain energized for 20 seconds following a compressor shut down.

· Revised the EXV algorithm to improve response to Low Discharge Superheat.

· Revised the Network Alarm  Broadcast to include Alerts

Version 1.0 (CESR-131248-01-00)

Serial Number Start:  3400F
Original Software Release.

Temperature Reset

ComfortLink offers several different control options for Temperature Reset.  Return Water, 4-20 mA Input, Space or Outside Air Temperature, can control chilled Water Reset.  Temperature Reset is programmed with the following variables:

	Sub-Mode
	Keypad Entry
	Item
	Display
	Item Expansion
	Comment

	RSET
	[ENTER]
	CRST
	X
	Cooling Reset Type
	0=No Reset

1=4-20 mA Input

2=Outdoor Air Temperature

3=Return Fluid

4=Space Temperature

	
	[▼]
	CRT1
	XXX.X (F

(XXX.X (C)
	No Cool Reset Temp
	Default: 125 (F (51.7  (C)

Range: 0 to 125 (F

           (-17.8 to 51.7  (C)

	
	[▼]
	CRT2
	XXX.X (F

(XXX.X (C)
	Full Cool Reset Temp
	Default: 0 (F (17.8  (C)

Range: 0 to 125 (F

           (-17.8 to 51.7  (C)

	
	[▼]
	DGRC
	XX.X (F

(XX.X (C)
	Degrees Cool Reset
	Default:  0 (F (0  (C)

Range:  -30 to 30 (F

             (-16.7 to 16.7 (C)


Temperature Reset applies to CSP.1, Cooling Set Point 1 (Set Point Mode, Sub-mode COOL) and CSP.2 Cooling Set Point 2 (Set Point Mode, Sub-mode COOL) only.  CSP.3 Cooling Set Point 3 (Set Point Mode, Sub-mode COOL), the ice storage set point is not affected.

4-20 ma Temperature Reset

The Energy Management Module is required for this option.  This option is designed for 4-20 ma input.  Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used.

To program this option, CRST, Cooling Reset Type (Configuration Mode, Sub-mode RSET) and DGRC, Degrees Cool Reset (Configuration Mode, Sub-mode RSET) must be set.  With a 20 ma signal, the machine will reset the temperature to the value specified in DGRC.  

For example, at 20 ma, the machine should reset by 10 (F (5.5 (C).

	Sub-Mode
	Keypad Entry
	Item
	Display
	Item Expansion
	Comment

	RSET
	[ENTER]
	CRST
	1
	Cooling Reset Type
	1=4-20 mA Input

	
	[▼]
	CRT1
	125.0 (F

(51.6 (C)
	No Cool Reset Temp
	Not required

	
	[▼]
	CRT2
	0.0 (F

(-17.8 (C)
	Full Cool Reset Temp
	Not required

	
	[▼]
	DGRC
	10.0 (F

(5.5 (C)
	Degrees Cool Reset
	Amount of Temperature Reset at 20 mA.



[image: image4.wmf]0

1

2

3

4

5

6

7

8

9

10

0

1

2

3

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

4-20 mA Signal

Reset Amount deg. F


Figure 1 - 4-20 mA Temperature Reset

0-10 or 2-10 vdc inputs cannot be used without further modification.  Failure to modify the signal will result in damage to the board.   If this is a requirement, a signal converter is recommended.  Although the signal converter is recommended, another option is to install a 226 ohm resistor must be installed in series with the input “+” lead.  The signal generating control must be limited to 2-10 vdc.  A signal lower than 2 vdc will result in an alarm that will terminate reset.

Return Water Reset

No additional hardware is required for this option.  The Energy Management Module is not required for this option.  To set up return water reset for this control system, follow these steps:

Under the Configuration Mode, these values must be set:  

CRST, Cooling Reset Type,  (Configuration Mode, Sub-mode RSET) 

CRT1, No Cool Reset Temp (Configuration Mode, Sub-mode RSET)

CRT2, Full Cool Reset Temp (Configuration Mode, Sub-mode RSET)

DGRC, Degrees Cool Reset Temp (Configuration Mode, Sub-mode RSET).

The variables CRT1 and CRT2 are based on the temperature difference across the cooler, not the actual fluid temperatures. 

The following example uses a reset value of 10 (F (5.5 (C) at full reset.  Full reset is at a 2 (F (1.1 (C) temperature difference across the cooler and no reset at 10 (F (5.5 (C) temperature difference across the cooler.  

	Sub-Mode
	Keypad Entry
	Item
	Display
	Item Expansion
	Comment

	RSET
	[ENTER]
	CRST
	3
	Cooling Reset Type
	3=Return Fluid

	
	[▼]
	CRT1
	10.0 (F

(5.5 (C)
	No Cool Reset Temp
	Entering to Leaving Water Temperature difference that has no reset.

	
	[▼]
	CRT2
	2.0 (F

(1.1 (C)
	Full Cool Reset Temp
	Entering to Leaving Water Temperature difference that has full reset.

	
	[▼]
	DGRC
	10.0 (F

(5.5 (C)
	Degrees Cool Reset
	Amount of reset required.



[image: image5.wmf]0

1

2

3

4

5

6

7

8

9

10

0

1

2

3

4

5

6

7

8

9

10

Temperature Difference (EWT-LWT) deg. F

Reset Amount deg. F

0

10

20

30

40

50

60

70

80

90

100

% Building Load

Building Load

Reset Amount


Figure 2 - Return Water Temperature Reset

There is a known problem with the metric conversion for this option.  The values for CRT1, and CRT2 are used for Outside Air and Space Temperature Reset.  Both values have units of type (F, which for OAT and Space reset is correct, but for return reset the values should be delta F.

Temperature Set Point

There are several options temperature set point options that the ComfortLink control system can utilize.  Each option will be addressed independently below with configuration and material required.

Single Set Point/Switch Control 

This is the factory default configuration.  No other devices are required for this option.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to SWITCH, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to SINGLE.  Any time the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).

Dual Set Point, Switch/Switch Control

This option allows for a dual set point control of the machine, typically an occupied and unoccupied set point.  A Dual Switch input is required connected to TB5-3 and TB5-4.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to SWITCH, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL SWITCH.  Operation with this option enabled, activates MD13 Dual Setpoint.  Any time the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, and the Dual Switch is closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  With the Dual Switch open, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).

Ice Build, Switch/Switch Control

This option allows for a triple set point control of the machine, an ice, occupied and unoccupied set point.  A Dual Switch input is required connected to TB5-3 and TB5-4.  An Ice Done Switch is required connected to TB6-9 and TB6-10.  The Energy Management Module is also required.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to SWITCH, CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL SWITCH, and ICE.M Ice Mode Enable (Configuration Mode, Sub-mode OPT2) set to YES.  As a result, the EMM EMM Installed (Configuration Mode, Sub-mode OPT1) will be set to YES automatically by the controller.  Operation with this option enabled activates MD13 - Dual Setpoint.  Any time the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, and the Dual Switch is closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  With the Dual Switch open and the Ice Done Switch open, the machine will control the set point to CSP.3 Cooling Setpoint 3 (Set Point Mode, Sub-mode COOL).  This is typically the ice build set point.  During operation at this set point, MD19 - Making Ice will be displayed.  With the Dual Switch open and the Ice Done Switch closed, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).  This is typically the unoccupied set point.  During operation at this set point, MD20 - Storing Ice will be displayed.

Single Set Point/7 Day Schedule

This option determines a set point based on an internal schedule that is accessible through the Navigator and CCN devices such as Network Service Tool.  There is no option for holiday schedules with this option.  No other devices are required for this option.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to 7 DAY SCHEDULE, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to SINGLE.

To use this option, an occupied and unoccupied schedule for each day must be programmed under (Time Clock Mode, Sub-mode SCHD).

	Item
	Expansion
	Display
	Default
	Range

	MON.O
	Monday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	MON.U
	Monday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	TUE.O
	Tuesday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	TUE.U
	Tuesday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	WED.O
	Wednesday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	WED.U
	Wednesday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	THU.O
	Thursday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	THU.U
	Thursday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	FRI.O
	Friday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	FRI.U
	Friday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	SAT.O
	Saturday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	SAT.U
	Saturday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59

	SUN.O
	Sunday Occupied Time
	XX.XX
	00.00
	00.00 – 23.59

	SUN.U
	Sunday Unoccupied Time
	XX.XX
	00.00
	00.00 – 23.59


To program a time schedule, access the appropriate day.  Enter the edit mode.  Change the time to the schedule desired.  All times are in programmed as a 24 hour clock.  Any day that is to remain unoccupied should have its unoccupied time programmed to 00.00.  Using this option, there is no way to avoid at least a 1 minute unoccupied period per day.

For this option to function properly, the HH.MM Hour and Minute (Time Clock Mode, Sub-mode TIME) and DAY Day of Week (Time Clock Mode, Sub-mode DATE) must be set.  The time clock is programmed in a 24 hour format, 00.00 to 23.59.  ComfortLink Controls cannot automatically adjust the time for day light savings time.

For example, if an occupied time from 6:00 AM to 8:00 PM is desired from Monday through Friday.  Saturday and Sunday are to remain unoccupied. 

	Item
	Expansion
	Default

	MON.O
	Monday Occupied Time
	06.00

	MON.U
	Monday Unoccupied Time
	20.00

	TUE.O
	Tuesday Occupied Time
	06.00

	TUE.U
	Tuesday Unoccupied Time
	20.00

	WED.O
	Wednesday Occupied Time
	06.00

	WED.U
	Wednesday Unoccupied Time
	20.00

	THU.O
	Thursday Occupied Time
	06.00

	THU.U
	Thursday Unoccupied Time
	20.00

	FRI.O
	Friday Occupied Time
	06.00

	FRI.U
	Friday Unoccupied Time
	20.00

	SAT.O
	Saturday Occupied Time
	00.00

	SAT.U
	Saturday Unoccupied Time
	00.00

	SUN.O
	Sunday Occupied Time
	00.00

	SUN.U
	Sunday Unoccupied Time
	00.00


During an occupied time and the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).

Dual Set Point/7 Day Schedule

This option determines a set point based on an internal schedule that is accessible through the Navigator and CCN devices such as Network Service Tool.  There is no option for holiday schedules with this option.  No other devices are required for this option.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to 7 DAY SCHEDULE, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL 7 DAY.

To use this option, an occupied and unoccupied schedule for each day must be programmed under (Time Clock Mode, Sub-mode SCHD).  Programming the 7 day schedule is shown in Single Set Point/7 Day Schedule.

Operation with this option enabled, activates MD13 Dual Setpoint.  During an occupied period with the Enable-Off-Remote Switch in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  During an unoccupied period and the Enable-Off-Remote Switch in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).

Ice Build/7 Day Schedule

This option allows for a triple set point control of the machine, an ice, occupied and unoccupied set point determined by an internal that is accessible through the Navigator and CCN devices such as Network Service Tool.  There is no option for holiday schedules with this option.  An Ice Done Switch is required connected to TB6-9 and TB6-10.  The Energy Management Module is also required.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to 7 DAY SCHEDULE, CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL 7 DAY, and ICE.M Ice Mode Enable (Configuration Mode, Sub-mode OPT2) set to YES.  As a result, the EMM EMM Installed (Configuration Mode, Sub-mode OPT1) will be set to YES automatically by the controller.  

To use this option, an occupied and unoccupied schedule for each day must be programmed under (Time Clock Mode, Sub-mode SCHD).  Programming the 7 day schedule is shown in Single Set Point/7 Day Schedule.

Operation with this option enabled activates MD13 - Dual Setpoint.  During an occupied period, with the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  During an unoccupied period and the Ice Done Switch open, the machine will control the set point to CSP.3 Cooling Setpoint 3 (Set Point Mode, Sub-mode COOL).  This is typically the ice build set point.  During operation at this set point, MD19 - Making Ice will be displayed.  Still in an unoccupied period and the Ice Done Switch closed, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).  This is typically the unoccupied set point.  During operation at this set point, MD20 - Storing Ice will be displayed.

Single Set Point/Occupancy

This option determines a set point based on an internal schedule that is only accessible through a Carrier Comfort Network (CCN) device.  This option allows for holiday schedules.  No other devices are required for this option.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to OCCUPANCY, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to SINGLE.

To use this option, an occupancy schedule for each day and holiday must be programmed.

To program a time schedule, access the appropriate day and change the time to the schedule desired.  All times are in programmed as a 24 hour clock.  Any day that is to remain unoccupied should have its unoccupied time programmed to 00.00.  24 hour operation can be programmed with this option.

For this option to function properly, the HH.MM Hour and Minute (Time Clock Mode, Sub-mode TIME), MNTH Month, DOM Day of Month, DAY Day of Week and YEAR Year (Time Clock Mode, Sub-mode DATE) must be set.  The time clock is programmed in a 24 hour format, 00.00 to 24.00.  Carrier Comfort Network cannot automatically adjust the time for day light savings time.  

Eight separate time periods are available, Period 1 through 8.  Each period has Monday through Sunday and a Holiday day flag, an occupied and unoccupied time.   For the day flags, 1 is enabled, 0 is disabled.

For example, if an occupied time from 6:00 AM to 8:00 PM is desired from Monday through Friday.  For Saturday an occupied period from 6:00 AM to 12:00 Noon is desired.  Sunday is to remain unoccupied. 

Once the machine is loaded, select Modify, Time-Sched, and OCCPC01S will be displayed.  

	
	
	M
	T
	W
	T
	F
	S
	S
	H
	
	Occupied
	
	Unoccupied

	Period 1
	
	1
	1
	1
	1
	1
	0
	0
	0
	
	06:00
	
	20:00

	Period 2
	
	0
	0
	0
	0
	0
	1
	0
	0
	
	06:00
	
	12:00

	Period 3
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00

	Period 4
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00

	Period 5
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00

	Period 6
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00

	Period 7
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00

	Period 8
	
	0
	0
	0
	0
	0
	0
	0
	0
	
	00:00
	
	00:00


During an occupied time and the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).

Dual Set Point/Occupancy

This option determines a set point based on an internal schedule that is only accessible through a Carrier Comfort Network (CCN) device.  This option allows for holiday schedules.  No other devices are required for this option.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to OCCUPANCY, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL CCN OCCUPPIED.

To use this option, an occupied and unoccupied schedule for each day must be programmed with a CCN device.  Programming the occupancy schedule is shown in Single Set Point/Occupancy.

Operation with this option enabled, activates MD13 Dual Setpoint.  During an occupied period with the Enable-Off-Remote Switch in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  During an unoccupied period and the Enable-Off-Remote Switch in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).

Ice Build/Occupancy

This option allows for a triple set point control of the machine, an ice, occupied and unoccupied set point determined by an internal schedule that is only accessible through a Carrier Comfort Network (CCN) device.  This option allows for holiday schedules.  No other devices are required for this option.  An Ice Done Switch is required connected to TB6-9 and TB6-10.  The Energy Management Module is also required.  For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to OCCUPANCY, CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to DUAL CCN OCCUPPIED, and ICE.M Ice Mode Enable (Configuration Mode, Sub-mode OPT2) set to YES.  As a result, the EMM EMM Installed (Configuration Mode, Sub-mode OPT1) will be set to YES automatically by the controller.  

To use this option, an occupied and unoccupied schedule for each day must be programmed under (Time Clock Mode, Sub-mode SCHD).  Programming the 7 day schedule is shown in Single Set Point/Occupancy.

Operation with this option enabled activates MD13 - Dual Setpoint.  During an occupied period, with the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  During an unoccupied period and the Ice Done Switch open, the machine will control the set point to CSP.3 Cooling Setpoint 3 (Set Point Mode, Sub-mode COOL).  This is typically the ice build set point.  During operation at this set point, MD19 - Making Ice will be displayed.  Still in an unoccupied period and the Ice Done Switch closed, the machine will control the set point to CSP.2 Cooling Setpoint 2 (Set Point Mode, Sub-mode COOL).  This is typically the unoccupied set point.  During operation at this set point, MD20 - Storing Ice will be displayed.

4 to 20 mA Input/Switch Control

This option requires the Energy Management Module.  Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used. 

For this option, CTRL Control Method (Configuration Mode, Sub-mode OPT2) must be set to SWITCH, and CLSP Cooling Set Point Select (Configuration Mode, Sub-mode SLCT) set to 4-20 MA INPUT. As a result, the EMM EMM Installed (Configuration Mode, Sub-mode OPT1) will be set to YES automatically by the controller.  Any time the Enable-Off-Remote Switch is in the Enable or Remote position with remote contacts closed, the machine will control the set point to CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL).  This option functions on a linear relation between 10 to 80 (F (-12.2 to 26.7 (C).   The equations are listed below:


[image: image6.wmf](

)

5

.

7

375

.

4

-

=

°

mA

F

    
[image: image7.wmf](

)

(

)

92

.

21

43

.

2

-

=

°

mA

C


The function is limited at the low end depending on the FLUD, Cooler Fluid (Configuration Mode, Sub-mode OPT1).  If FLUD is set for WATER, the lower limit is 38 (F  (3.3 (C).  If FLUD is set for MEDIUM TEMPERATURE BRINE or LOW TEMPERATURE BRINE, the lower limit is 12 (F  (-11.1 (C).  If this option is used, the chilled water loop must be protected to at least 0 (F  (-17.1 (C) to protect the loop from freezing if the signal sent incorrectly.  The function is also clamped at the upper limit not to exceed 70 (F (21.1 (C).


[image: image8.wmf]0

10

20

30

40

50

60

70

80

90

4

6

8

10

12

14

16

18

20

4-20 mA Signal

Temperature Set Point (F)

Control Equation

Fresh Water Control

Brine Control


Figure 3 - 4-20 mA Temperature Set Point
Service 

Alarm and Alert Codes

Alarm and Alert Codes are displayed as 4 digit codes.  To determine the expansion of the alarm/alert code, press the [ENTER] and [ESCAPE] keys together once the item is selected.

Communication Failure

Action taken by control:  Machine is shut down

Reset Method:  Automatic once communication is restored (MBB)

This alarm is generated any time the LEN (Local Equipment Network) communication is lost.  An A152 may be generated also.

If this condition is encountered, check the following items:

· Check the MBB Instance Jumper.  It should be set to “1”.  If it is missing or installed on “2”, this alarm will be generated.

· Check the LEN for a wiring error or short to ground.

T020 – Compressor A1 High Motor Temperature Alert

T021 – Compressor A2 High Motor Temperature Alert

T022 – Compressor B1 High Motor Temperature Alert

T023 – Compressor B2 High Motor Temperature Alert

Action taken by control:  Affected compressor is shut down

Reset Method:  Manual (MBB)

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range, for 5 consecutive readings.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

· Check the motor cooling solenoid for proper operation.

· Check the circuit for proper refrigerant charge.

· Check the motor cooling line for any restrictions

· Check the liquid line strainer to be sure that it is free of debris.

· On 2-compressor circuits, check to be sure that the economizer solenoid valve is functioning properly.

T026 – Compressor A1 Low Oil Pressure Alert - 1

T026 – Compressor A1 Low Oil Pressure Alert - 2

T027 – Compressor A2 Low Oil Pressure Alert - 1

T027 – Compressor A2 Low Oil Pressure Alert - 2

T028 – Compressor B1 Low Oil Pressure Alert - 1

T028 – Compressor B1 Low Oil Pressure Alert - 2

T029 – Compressor B2 Low Oil Pressure Alert - 1

T029 – Compressor B2 Low Oil Pressure Alert - 2

Action taken by control:  Affected compressor shut down

Reset Method:  Manual (MBB)

This alarm is generated if the oil pressure is below the set point for a specified period of time.  The “- 1” or “- 2” at the end of the alert indicates what oil set point generated the alert.  The “- 1” indicates that the alert was generated by Oil Set Point 1.  The “- 2” indicates that the alert was generated by Oil Set Point 2.  The alert criteria is listed below:

In the formulas below, 

PD is Discharge Pressure, 

PE  is Economizer Pressure, 

PO is Oil Pressure, 

PS is Suction Pressure.

There are 2 set points used for the control of the Low Oil Pressure alert trip criteria.

Oil Set Point 1 is defined as follows:


PS < 35 psig, then Oil Set Point 1 is 10 psig


35 psig ≤ PS < 51 psig, then Oil Set Point 1 is 12.5 psig


PS ≤ 51 psig, then Oil Set Point 1 is 15 psig

Oil Set Point 2 is defined as follows.


(PD – PS) <125 psig



Oil Set Point 2 = 0.235(PD – PS) + 0.588 psig


125 ( (PD – PS) <165 psig



Oil Set Point 2 = 2(PD – PS) – 220.0 psig


(PD – PS) ( 165 psig



Oil Set Point 2 = 0.6364(PD – PS) + 5.0 psig

The alert criteria is based on operating time. 

On time less than 5 seconds


Oil pressure is ignored

On time between 5 and 120 seconds 


The alert will be generated if the following condition is true for 3 consecutive readings. 

(PO – PE) < [15 psig/120 seconds] x [Compressor Run Time in seconds].

On time greater than 120 seconds


The alert will be generated if one of the following conditions is true


(PO – PE) < Oil Set Point 1 for 15 seconds


(PO – PS) < Oil Set Point 2 for 15 seconds

If this condition is encountered, check the following items:

· On 30HXC machines, consider head pressure control.  If the entering condenser water is less than 70 (F (21 (C), the machine should have a water regulating valve installed.

· Check the refrigerant charge.  Low charge conditions will reduce the discharge pressure for the machine, thereby lowering the starting point for the oil pressure.  On economized machines, this condition compounds the problem by increasing the economizer pressure as hot gas enters the economizer shell from a lack of a liquid seal.

· Check the internal and external oil filter pressure drops.  Change as necessary.

· Check all oil line service valves to be sure that they are open.

· Check the operation of oil solenoid valve.

· If the unit is equipped with a suction service valve, check to be sure that the suction service valve is open.  Check to be sure that the suction service valve is locked in place.

· If the filters are plugging rapidly, have a filter analyzed for content.  There have been reports filters plugging with filter drier media or metal particles from the discharge check valve.  The filter drier is a granular design and has been known to disintegrate. A solid core filter drier was installed starting with serial number 5200F.

· Discharge check valve failures can introduce metal filings into the oil, which are collected by the oil filters.

· Check the transducer accuracy.  Replace the transducer if necessary.  All of the transducers are used in the oil pressure set point selection.

Service Bulletins pertaining to this condition:

· SMB010008 – 06N Internal Oil Filters Plugging


This bulletin described the problem with the motor cooling filter drier disintegrating during operation.  A solid core filter drier was installed starting with serial number 5200F.

T030 – Compressor A1 Pre-Start Oil Pressure Alert

T031 – Compressor A2 Pre-Start Oil Pressure Alert 

T032 – Compressor B1 Pre-Start Oil Pressure Alert 

T033 – Compressor B2 Pre-Start Oil Pressure Alert 

Action taken by control:  Circuit not allowed to start 

Reset Method:  Manual (MBB)

This alarm is generated after three attempts at starting.  When a call for cooling is received, the oil pressure transducer is read and its value stored.  The circuit oil pump is started and operates for 20 seconds.  After the 20 second operation, the Oil Pressure Transducer reading is checked again and compared to the initial reading.    If the difference between the two readings is 2.5 psi (17 kPa) or less, the oil solenoid is opened.  The oil pressure is measured again.  The oil pressure prove criteria is 3.5 psi (23.8 kPa) minus the attempt number.  So, if at the first attempt the pressure is not greater than 2.5 psi (17 kPa), the oil solenoid is closed and the circuit is reset.  The circuit will remain off for 20 seconds.  The oil pump is started and the sequence repeated.  On the second attempt, if the oil pressure is not greater than 1.5 psi (10.3 kPa) the oil solenoid is closed and the sequence started again.  After the third attempt, if the oil pressure is not greater than 0.5 psi (3.4 kPa) the alarm is generated.  This alert algorithm is active for the lead compressor during start-up only.

For lag compressor start-up, the oil pressure is read by the control.  The oil solenoid is then opened.  To pass the oil pressure prove criteria, the oil pressure rise must be at least 2.5 psi (17 kPa) or greater than the initial pressure reading.  If the oil pressure is less than 2.5 psi (17 kPa) compared to the initial oil pressure reading, the alert is generated.

If this condition is encountered, check the following items:

· Check the internal and external oil filter pressure drops.  Change as necessary.

· Check to be sure that the bypass check valves at the oil pump are installed correctly.  The check valve should allow flow around the pump when the pump is not in operation.  Early Charlotte 30HX production machines were found to have the check valves installed backwards.  The machines will not start.  They alert on Pre-Start Oil Failure.
· Check all oil line service valves to be sure that they are open.

· Check the operation of oil solenoid valve.

· There have been reports filters plugging with filter drier media or metal particles from the discharge check valve.  The filter drier is a granular design and has been known to disintegrate. A solid core filter drier was installed starting with serial number 5200F.

· Check the calibration of the oil pressure transducer.  

Service Bulletins pertaining to this condition:

· SMB010008 – 06N Internal Oil Filters Plugging


This bulletin described the problem with the motor cooling filter drier disintegrating during operation.  A solid core filter drier was installed starting with serial number 5200F.

T034 – Compressor A1 Max. Oil Delta P, Check Oil Line Alert

T035 – Compressor A2 Max. Oil Delta P, Check Oil Line Alert 

T036 – Compressor B1 Max. Oil Delta P, Check Oil Line Alert 

T037 – Compressor B2 Max. Oil Delta P, Check Oil Line Alert 

Action taken by control:  Affected compressor shut down

Reset Method:  Manual (MBB)

This alarm is generated if the difference between the discharge pressure and the oil pressure is greater than 100 psi (683 kPa) for more than 5 seconds.

If this condition is encountered, check the following items:

· Check the internal and external oil filter pressure drops.  Change as necessary.

· Check all oil line service valves to be sure that they are open.

· Check the operation of oil solenoid valve.

· There have been reports filters plugging with filter drier media or metal particles from the discharge check valve.  The filter drier is a granular design and has been known to disintegrate. A solid core filter drier was installed starting with serial number 5200F.

· Check the transducer accuracy.  Replace the transducer if necessary.  All of the transducers are used in the oil pressure set point selection.

Service Bulletins pertaining to this condition:

· SMB010008 – 06N Internal Oil Filters Plugging


This bulletin described the problem with the motor cooling filter drier disintegrating during operation.  A solid core filter drier was installed starting with serial number 5200F.

T038 – Compressor A1 Failed Oil Solenoid Alert

T039 – Compressor A2 Failed Oil Solenoid Alert 

T040 – Compressor B1 Failed Oil Solenoid Alert 

T041 – Compressor B2 Failed Oil Solenoid Alert 

Action taken by control:  Affected compressor shut down

Reset Method:  Manual (MBB)

When a call for cooling is received, the Differential Oil Pressure, DOP (Oil Pressure – Economizer Pressure) is read and its value stored, DOPt.  The differential is used to compensate for changing water temperatures.  The circuit oil pump is started and operates for 20 seconds.  After the 20 second operation, the Oil Pressure Differential reading, DOPt+20 is checked again and compared to the initial reading.    If the difference between the two readings, (DOPt+20 - DOPt) is greater than 5 psi (34 kPa), the oil solenoid is assumed to have failed open and the alert is generated.  This alert algorithm is active during lead compressor start-up only.  It does not apply to the lag compressor of the circuit, once the lead compressor is operational.

If this condition is encountered, check the following items:

· Check the operation of oil solenoid valve.  Carlyle had a vendor problem with the oil solenoid manufacturer Parker with compressor date codes 4499J, 0700J, 0800J, 0900J.  The suspect solenoid valves have a seal that may allow oil to leak by.   Parker production dates close to these serial numbers should also be suspect.
· Check the accuracy of the economizer and oil pressure transducer.  Replace the transducer(s) if necessary.

T051 – Compressor A1 Failure Alert

T052 – Compressor A2 Failure Alert

T055 – Compressor B1 Failure Alert

T056 – Compressor B2 Failure Alert

The following alerts are ComfortLink Compressor Protection alerts.  They will be displayed as compressor failures.  Expanding the alarm will display the cause of the compressor failure.

High Pressure Switch Trip Alert

Action taken by control:  Compressor is shut down

Reset Method:  Manual (CCP and MBB)

This alarm is generated when the High Pressure Switch for the compressor opens.  The ComfortLink Compressor Protection Module will signal this alarm if the High Pressure Switch is open for at least 250-500 milliseconds.

If this condition is encountered, check the following items:

· Find the cause of high pressure switch trip.  For 30GX machines, check the condenser fan operation.  For 30HXA machines, check the condenser fan relays and condenser for proper operation.  Check to be sure that the correct fan cycling pressure switches are used.  Early Charlotte production machines were not supplied with the fan cycling pressure switches.  For 30HXC machines, check the operation of the Condenser Water Regulating Valve.  Check strainers to insure proper water flow. 

· For air systems check the coils for debris or air recirculation.

· Confirm that the machine charge is correct.

· Check for the correct High Pressure Switch.  Early 30HXA machines produced with serial numbers between 0501Q and 2701Q, were produced with the water-cooled high pressure switch, rather than the air-cooled high pressure switch.

· Check for proper connection of the High Pressure Switch to the CCP.

· Version 1.0 and 2.0 software has an error with the VHPT, Variable Head Pressure Selection (Configuration Mode, Sub-mode OPT1) option 2 (0 to 10 vdc) and option 3 (10 to 0 vdc).  When configured for one of these options, the output from the controller has a maximum output of 5 vdc.  A temporary fix to this situation is to use a 1,000 ohm, ¼ watt resistor instead of the 500 ohm, ½ watt resistor that would normally be used.

· Confirm the proper value for the HD.P.A and HD.P.B, Head Pressure Set Point A and Head Pressure Set Point B (Set Point Mode, Sub-mode HEAD).  Machines produced prior to 5100F, the factory configuration values were incorrect.   

· Check for non-condensables in the circuit.

Service Bulletins pertaining to this condition:

· SMB010007 – ComfortLink 30HXA/HXC Head Pressure Set Point Setting

This bulletin described the correct factory settings in the head pressure set points.

No Motor Current Detected Alert

Action taken by control:  Compressor is shut down

Reset Method:  Manual (CCP and MBB)

This alarm will be generated if the CCP detects less than 10% Must Trip Amps (MTA) on all three legs for greater than 3 seconds while the compressor status is “On”. 

If this condition is encountered, check the following items:

· Check the operation of the contactors.  If the contactors do not pull in, the alarm can be generated.  

· Check the Molex connectors from the CCP to the compressor contactors.   Loose connections, may create an open circuit prohibiting contactor operation.

· On Wye-Delta starters, check the auxiliary contact for proper operation.  The auxiliary contact is responsible for energizing the 2M contactor.  Check the contact pads.

· On Wye-Delta starters, be sure the shorting bars on the S contactor are installed.

· Check the Molex connectors from the toroids to the CCP.  Loose connections can cause this alarm. Some modules have had conformal coating on the CPM pin connections interfering with the harness connection. 

· Check the toroid harness connections.  Be sure that the correct toroid is connected to the appropriate CCP connection.  A connection problem at the CCP or toroid could cause the alarm.

· Check the toroid resistance. It should be 64.3-70.4 ( (30GX502786) or 38.5-42 ( (30GX504711). 

· Check for a chattering High Pressure Switch.  The High Pressure Switch is in series with the control relays of the CCP board.  If the High Pressure Switch opens momentarily, for less than 250-500 milliseconds, the control relay will open, causing the compressor contactors to open.  The CCP will detect a no motor current condition and signal that alarm.

· Check to be sure that the correct Current Transformer Module is used.  If a ½ current module (30GX504711) is installed on a compressor with a MTA of less than 314 amps, this alarm will be generated.  

Current Unbalance Alert

Action taken by control: Circuit is shut down

Reset Method:  Manual (CCP and MBB)

If the CCP detects a current imbalance greater than the set point C.UNB Current Unbalance Set Point (Configuration Mode, Sub-mode OPT2) for more than 25 minutes, the alarm is generated.   The factory default for the machine was 10% for all CCPs.  Starting 4400F, the C.UNB was increased to 25% for all ½ current CCP (HN67LM104) from the factory.  Beginning with the use of the 30GX504711 current transformer module, the C.UNB was again reduced to 10%.

If this condition is encountered, check the following items:

· Check the voltage imbalance.  Voltage imbalance has a strong relation to the current imbalance. 

· Check the toroids.  The measured resistance should be 64.3-70.4 ( (30GX502786) or 38.5-42 ( (30GX504711).  Check the toroid wiring.  Do not allow the wires to run in parallel with high voltage sources, greater than 30 volts.

· Check all wiring connections at the compressor, contactors, and terminal block.  Loose connections can cause current imbalances.

· Dry run the contactors to see that they are pulling in correctly.  Inspect the contactor pads for arcing or corrosion. Telemecanique contactors with the date codes 2T0188 (2T is the manufacturing point, 01 is the year, 18 is the week) through 2T0146 may have a binding spring in the contactor actuator that can cause the contactor not to function properly.  Contactors with date codes as early as 2T0025 have also been reported with this problem. 

· Check for power devices attached downstream of the toroid other than the compressor.

For ½ current modules, check the following additional items:

· Check for a voltage imbalance to the machine.

· Check to be sure that the parallel leads for each phase originate from the same terminal block stud.

· Check the current draw on all six conductors.  Select the three conductors, one from each phase, which has the closest current draw.  Route these leads through the toroid to sense the compressor current draw.  CAUTION – Change only one phase at a time.  Mixing the phases could result in the compressor running backwards resulting in a compressor failure.  The control system will not detect this condition. 

· For units with compressors with MTA greater than 314 that use the ½ current CCP, HN67LM104, converting to the 30GX504711 current transformer module with the full current CCP, HN67LM103 can correct many nuisance alarms.

Service Bulletins pertaining to this condition:

· SMB020027 – 30GX,HX Compressor Contactor Failures


This bulletin described the failure mode of the Telemecanique contactors with the binding actuator.

· SMB020027A – 30GX,HX Compressor Contactor Failures


This bulletin superseded SMB020027.  There was no change to the body of the document.  The revision clarified the warranty claim procedures.

· SMB020039 – 30GX/HX Ground Fault and Current Imbalance Alarms


This bulletin described the changes required to update the ½ current Compressor Protection Modules to the full current modules and new ½ current toriods.

Single Phase Current Loss Alert

Action taken by control:  Circuit is shut down

Reset Method:  Manual (CCP and MBB)

This alarm will be generated when the current imbalance reaches a programmed level. The alarm will be generated by one of two conditions.  If the running current is less than 50% of MTA and a current imbalance between phases of greater than 50% is measured for 1 second, the alarm will be generated.  If the running current is at or greater than 50% of MTA and a current imbalance between phases of 30% is measured for 1 second, the alarm will be generated.  

· Check the voltage imbalance.  Voltage imbalance has a strong relation to the current imbalance. 

· Check the voltage while the compressor is starting.  If one phase drops out or is reduced, this alarm can be generated.

· Check the toroids.  The measured resistance should be 64.3-70.4 ( (30GX502786) or 38.5-42 ( (30GX504711).  Check the toroid wiring.  Do not allow the wires to run in parallel with high voltage sources, greater than 30 volts.

· Check all wiring connections at the compressor, contactors, and terminal block.  Loose connections can cause current imbalances.

· Dry run the contactors to see that they are pulling in correctly.  Inspect the contactor pads for arcing or corrosion.  Telemecanique contactors with the date codes 2T0188 (2T is the manufacturing point, 01 is the year, 18 is the week) through 2T0146 may have a binding spring in the contactor actuator that can cause the contactor not to function properly.  Contactors with date codes as early as 2T0025 have also been reported with this problem. 

Service Bulletins pertaining to this condition:

· SMB020027 – 30GX,HX Compressor Contactor Failures


This bulletin described the failure mode of the Telemecanique contactors with the binding actuator.

· SMB020027A – 30GX,HX Compressor Contactor Failures


This bulletin superseded SMB020027.  There was no change to the body of the document.  The revision clarified the warranty claim procedures.

High Motor Current Detected Alert

Action taken by control:  Compressor is shut down

Reset Method:  Manual  (CCP and MBB)

This alarm will be generated if the motor current detected by the toroids exceeds the Must Trip Amp (MTA) setting.  No alarm will be generated if the current value is 87% of the MTA value.  The alarm may be generated if the value read by the toriod is between 97-100% of the MTA value.  The alarm will be generated if the value read is 100% or greater for 1 second.  There is a 4.0 +/- 0.5 second delay from start-up before this alarm is active to allow for locked rotor inrush.

If this condition is encountered, check the following items:

· Check for compressor operation outside of the operational envelope.  Confirm that the compressor is starting unloaded.

· Check all power connections for tightness from the terminal block to the contactors and compressor terminals.  

· Check the Must Trip Amp Configuration Header and the appropriate Must Trip Amps, CM.A1 Compressor A1 Must Trip Amps, CM.A2 Compressor A2 Must Trip Amps, CM.B1 Compressor B1 Must Trip Amps, or CM.B2 Compressor B2 Must Trip Amps, (Configuration Mode, Sub-mode UNIT), for the proper setting.    

· Check the toroid harness to be sure that the harness does not run in parallel with voltage sources greater than 30 vac.  This can induce a voltage on a leg of the harness.

· On the ½ current modules, check the power wiring to the toroid.  Be sure that only one set of leads goes through the toroid, if configured.   Consider upgrading the system to the ½ current toriod and full current CCP.

· Check to be sure that the contactors in a Wye-Delta configuration are properly operating.  A delay in the transition can cause the machine to trip on locked rotor current as the compressor starts in an Across-the-Line configuration.

· Check for a bad compressor motor.

· Check for a seized compressor.

· Check for moisture in the refrigerant circuit.

· Check for power devices attached downstream of the toroid other than the compressor.

· On 2 compressors per circuit with Wye-Delta Starters, primarily on 208 volt systems, may stall during transition if the other compressor of the circuit is operating.  This is more common with 80 ton compressors.  Currently, the only fix is to add a time delay relay to reduce the transition time from 5 to 2 seconds.  Contact Service Engineering for additional details.  

Service Bulletins pertaining to this condition:

· SMB020039 – 30GX/HX Ground Fault and Current Imbalance Alarms


This bulletin described the changes required to update the ½ current Compressor Protection Modules to the full current modules and new ½ current toriods.

Compressor Ground Fault Alert

Action taken by control: Compressor is shut down.

Reset Method: Manual  (CCP and MBB)

On the full current modules, a Ground Fault alarm will be generated by a current to ground of 2.5 +/- 2.0 amps as measured through the toroid.  On the ½ current modules HN67LM104, a Ground Fault alarm will be generated by a current to ground of 7.5 +/- 2.0 amps as measured through the toroid. 

With both modules summing the three phases together senses the current-to-ground.

If this condition is encountered, check the following items:

· If either compressor MTA is greater than 314 amps, be sure that the CPM is a ½ current module, HN67LM104.

· Check all connections from the terminal block to the compressor contactor, from the compressor contactor to the compressor.  All connections should be tight.  Inspect the connections for signs of overheating.

· Check for a grounded compressor motor.

· Check the contactors for arc marks on the contactor pads.

· Be sure the toroid harness has a good connection at both the CCP and the toroid.  Some modules have had conformal coating on the CCP pin connections interfering with the harness connection. 

· Check the toroid harness to be sure that the harness does not run in parallel with voltage sources greater than 30 vac.  This can induce a voltage on a leg of the harness.

· Check the toroid resistance.  The resistance for each phase toroid should be between 64.3-70.4 ( (30GX502786) or 38.5-42 ( (30GX504711).

· Check for power devices attached downstream of the toroid other than the compressor.

For ½ current modules, check the following additional items:

· Check for a voltage imbalance to the machine.

· Check to be sure that the parallel leads for each phase originate from the same terminal block stud.

· Check the current draw on all six conductors.  Select the three conductors, one from each phase, that have the closest current draw.  Route these leads through the toroid to sense the compressor current draw.  CAUTION – Change only one phase at a time.  Mixing the phases could result in the compressor running backwards resulting in a compressor failure.  The control system will not detect this condition. 

· For units with compressors with MTA greater than 314 that use the ½ current CCP, HN67LM104, converting to the 30GX504711 current transformer module with the full current CCP, HN67LM103 can correct many nuisance alarms.

If no problems can be found, turning DIP Switch #2 on disables the Ground Fault detection algorithm of the module.  Starting 4400F, all ½ current CCP (HN67LM104) have ground fault disabled from the factory.

Beginning with the use of the 30GX504711 current transformer module the ground fault detection DIP Switch #2 will be re-enabled from the factory.

Service Bulletins pertaining to this condition:

· SMB020039 – 30GX/HX Ground Fault and Current Imbalance Alarms


This bulletin described the changes required to update the ½ current Compressor Protection Modules to the full current modules and new ½ current toriods.

Contactor Failure Alert

Action taken by control:  Compressor is unloaded, the other circuit is disabled and further loading of the machine is prohibited.  All supporting commands will be running.

Reset Method:  Manual  (CCP and MBB)

If the CCP detects a compressor current greater than 10% of Must Trip Amps (MTA) while the compressor is off, the alarm is generated.  The affected compressor is unloaded, the other circuit is disabled and the further loading of the machine is prohibited.  All other compressors and are commanded off.   All support functions, oil solenoid, oil pump, EXV, cooler and condenser pumps are supported during this alarm.  If the compressor is not operating, it is not uncommon for the machine to alarm on a High Saturated Suction Temperature Alarm.

If this condition is encountered, check the following items:

· Check the compressor contactors to be sure that the contacts are not welded.

· Check for a wiring problem that is applying power to the compressor contactors, other than from the Compressor Protection Module.

· Check the toroid harness to be sure that the harness does not run in parallel with voltage sources greater than 30 vac.  This can induce a voltage on a leg of the harness.

· Check the toroid harness connections.  Be sure that the correct toroid is connected to the appropriate CCP connection.  A connection problem at the CCP or toroid could cause the alarm.  If this is the case there should be an additional “No Motor Current Alarm”.

· Check for power devices attached downstream of the toroid other than the compressor.

Current Phase Reversal Alert

Action taken by control: Compressor is shut down.

Reset Method: Manual  (CCP and MBB)

The alarm will be triggered if the ComfortLink Compressor Protection (CCP) detecting a current phase reversal of the incoming power supply through the toroids.

This algorithm is the primary means to detect a reverse rotation condition.  If the main power to the compressor contactors is absent at start-up, this alarm will also be generated, since phase rotation cannot be sensed.

If this condition is encountered, check the following items:

· If the compressor has not been operational, reverse two of the incoming power leads.  Do not change the internal wiring from the terminal block to the compressor contactors and compressors.  Changing these wires defeats the control systems protection.

· Check the voltage while the compressor is starting.  If one phase drops out or is reduced, this alarm can be generated.

· Check the High Pressure Switch connections to the CCP.  The HPS is connected in series with the CCP control relays, which control the compressor contactors.  Without the contactor coil energized, the control cannot sense the current rotation.

· Be sure power is available to the compressor contactors.  Check the fuses or circuit breakers supplying the machine.

· Check the toroid harness connections.  A connection problem at the CCP or toroid could cause the alarm.  Some modules have had conformal coating on the CPM pin connections interfering with the harness connection.

· Check the toroid harness to be sure that the harness does not run in parallel with voltage sources greater than 30 vac.  This can induce a voltage on a leg of the harness.

· Check to be sure that all of the toroids within the block are installed in the same orientation.

Motor Over Temperature Alert

Action taken by control:  Compressor is shut down

Reset Method:  Manual  (CCP and MBB)

The motor temperature limit is 240 (F (116 (C).  If this temperature is sensed by the motor thermistor, the alarm will be generated.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

· Check the motor cooling solenoid for proper operation.

· Check the circuit for proper refrigerant charge.

· Check the motor cooling line for any restrictions.

· Check the economizer inlet screen for debris.

· Check the liquid line strainer to be sure that it is free of debris.

· On 2-compressor circuits, check to be sure that the economizer solenoid valve is functioning properly.

Service Bulletins pertaining to this condition:

· SMB990072A – 06N Motor Temperature Operating Limits


This bulletin described the operating limits for the compressor and the actions taken by the control system at various points.

· SMB010012 – 30HXA/HXC076-146 Liquid Line Strainer Change

This bulletin advised of the new strainer assembly for the 30HXA/HXC076-146 machines.

Open Thermistor Alert

Action taken by control:  Compressor is shut down.

Reset Method:  Manual  (CCP and MBB)

The alarm is generated if the ComfortLink Compressor Protection detects an open circuit for the motor winding thermistor.

If this condition is encountered, check the following items:

· Check for a bad motor thermistor.

· Check for a loose connection in the motor winding thermistor circuit.

Each compressor is equipped with 2 motor winding thermistors connected with a common leg.  Before using the back-up thermistor, verify that there is not a wiring error.

MTA Header Fault Alert

Action taken by control:  Compressor will not be allowed to start

Reset Method:  Manual (CCP and MBB)

This alarm is generated when the CCP detects an erroneous setting of the Must Trip Amps (MTA) Configuration Header, with either all jumpers open or closed.  To reset this alarm, the power must be removed from the CCP for a minimum of 5 seconds.  The alarm reset button will not clear this alarm.

If this condition is encountered, check the following items:

· Check to be sure that the configuration header is firmly seated in the holder and that all pins are seated into their socket.

· Check to be sure that the configuration header is properly punched.

MTA Alert

Action taken by control:  Compressor will not be allowed to start

Reset Method:  Manual (CCP and MBB)

This alarm is generated when the ComfortLink Compressor Protection’s Must Trip Amp (MTA) value does not match the value stored with the controls for the appropriate compressor.  These values are stored under CM.A1 Compressor A1 Must Trip Amps, CM.A2 Compressor A2 Must Trip Amps, CM.B1 Compressor B1 Must Trip Amps, or CM.B2 Compressor B2 Must Trip Amps, (Configuration Mode, Sub-mode UNIT). 

If this condition is encountered, check the following items:

· Check to be sure that the configuration header is firmly seated in the holder and that all pins are in their socket.

· Check to be sure that the configuration header is properly punched.

· Check to be sure that the proper machine size and voltage was downloaded to the MBB.

Shorted Thermistor Alert

Action taken by control: Compressor is shut down.

Reset Method:  Manual  (CCP and MBB)

The alarm is generated if the ComfortLink Compressor Protection detects a shorted circuit for the motor winding thermistor.

If this condition is encountered, check the following items:

· Check for a bad motor thermistor.

· Check for a grounded connection in the motor thermistor circuit.

Each compressor is equipped with 2 motor winding thermistors thermistors connected with a common leg.  Before using the back-up thermistor, verify that there is not a wiring error.

A060 – Cooler Leaving Water Thermistor Failure - 1 Alarm

A060 – Cooler Leaving Water Thermistor Failure - 2 Alarm

Action taken by control: Machine is shut down.

Reset Method:  Automatic (-1 Alarm)



    Manual (-2 Alarm)

There are two conditions that will generate this alert.  

The “-1” alarm will be generated if the leaving water thermistor read by the control is outside of the ‑40 to 245 (F (-40 to 118 (C) range.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

The “-2” alarm will be generated if the leaving water temperature is greater than the entering water temperature by at least 5 ºF (2.8ºC) for at least 15 minutes.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

· Check the chilled water piping arrangement for proper flow.  Entering water should be in on the lowest nozzle.

T061 – Cooler Entering Water Thermistor Failure Alert

Action taken by control:  Machine continues to operate

Reset Method:  Automatic

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  The machine will continue to operate, with a fixed rise/ton of 0.1 (F/% Total Capacity (0.06 (C/% Total Capacity).

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

T062 – Condenser Leaving Water Thermistor Failure Alert

T063 – Condenser Entering Water Thermistor Failure Alert

Action taken by control:  Machine continues to operate

Reset Method:  Automatic

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  The machine will continue to operate.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

T070 – Circuit A Discharge Gas Thermistor Failure Alert

T071 – Circuit B Discharge Gas Thermistor Failure Alert

Action taken by control: Circuit is shut down.

Reset Method:  Manual  (MBB)

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  Since the discharge gas temperature tracks the oil temperature, if the Discharge Gas Temperature exceeds 210 (F (99 (C) the alarm will also be generated.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

· Check for a faulty oil heater relay.  

· Check the circuit’s refrigerant charge.  Low charge can cause higher than normal discharge temperatures.

· Check DIS.S Discharge Super. Setpoint (Configuration Mode, Sub-mode UNIT).  It should be set for 22 (F (-5.5 (C).  

· Check the compressor’s internal pressure relief to be sure that it is closed.

· In applications with high compression ratios, the discharge gas temperature will be elevated.  In some cases, it has been high enough to trip this alarm.  To reduce the occurrence of this situation, lower the MT.SP Motor Temp Setpoint (Configuration Mode, Sub-mode SERV) to 150 (F (65.5 (C), or raise the LVL.A Liquid Level Setpoint A or LVL.B Liquid Level Setpoint B (Set Point Mode, Sub-mode LIQ) to 2.2.  Beginning with Version 3.1 software any unit configured for Medium Temperature Brine operation FLUD Cooler Fluid, (Configuration Mode, Sub-mode OPT1) will change the Motor Temp Setpoint to 170 (F (76.7 (C).

· Check the compressor rotors.  Damage to the compressor rotors can cause an internal bypass, elevating the discharge temperature.

Service Bulletins pertaining to this condition:

· SMB01?? – ComfortLink Main Base Board Software

This bulletin addressed the versions of screw software.

T073 – Outdoor Air Temperature Thermistor Failure Alert

Action taken by control:  Machine continues to operate, Outdoor Air Reset is disabled

Reset Method:  Automatic

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  The machine will continue to operate with reset disabled under normal control set points.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

T074 – External Reset Temperature Thermistor Failure Alert

Action taken by control:  Machine continues to operate, Space Temperature Reset disabled

Reset Method:  Automatic

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  The machine will continue to operate with reset disabled under normal control set points.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

T079 – Lead/Lag Thermistor Failure Alert

Action taken by control:  Machine continues to operate

Reset Method:  Automatic

This alarm will be generated if the thermistor is read by the control outside of the –40 to 245 (F (-40 to 118 (C) range.  The machine will continue to operate with reset disabled under normal control set points.

If this condition is encountered, check the following items:

· Check for a thermistor failure.

· Check for a thermistor wiring error.

· Check the configuration of the machine.  If the machine is configured for Master/Slave control and there is no thermistor connected to the master chiller, this alarm will be generated.

· Software Version 3.1 and earlier, a software bug has been found with this alarm.  If the machine is configured for dual chiller parallel operation, LLEN Lead/Lag Enable, (Configuration Mode, Sub-mode RSET) Enable and PARA Parallel Configuration (Configuration Mode, Sub-mode RSET) Yes and the alarm is generated, the alarm cannot be cleared by disabling the parallel dual chiller operation.  To clear the alarm, enable dual chiller series control and PARA Parallel Configuration (Configuration Mode, Sub-mode RSET) No and then clear the alarm.

T090 – Circuit A Discharge Pressure Transducer Failure Alert

T091 – Circuit B Discharge Pressure Transducer Failure Alert

T092 – Circuit A Suction Pressure Transducer Failure Alert

T093 – Circuit B Suction Pressure Transducer Failure Alert

Action taken by control:  Affected circuit is shut down.

Reset Method:  Automatic

This alarm will be generated if the voltage ratio (Voltage Measured / Voltage Reference) by the Main Base Board (MBB) is greater than 99.9% or less than 0.5%.

If this condition is encountered, check the following items:

· Check for a faulty transducer.

· Check for a wiring error or problem between transducer and the MBB.

· Check for a faulty power supply from the MBB.

T094 – Compressor A1 Oil Pressure Transducer Failure Alert

T095 – Compressor A2 Oil Pressure Transducer Failure Alert

T096 – Compressor B1 Oil Pressure Transducer Failure Alert

T097 – Compressor B2 Oil Pressure Transducer Failure Alert

Action taken by control:  Affected compressor is shut down.

Reset Method:  Automatic

This alarm will be generated the voltage ratio (Voltage Measured / Voltage Reference) by the Screw Board (SCB) is greater than 99.9% or less than 0.5%.

If this condition is encountered, check the following items:

· Check for a faulty transducer.

· Check for a wiring error or problem between transducer and the SCB.

· Check for a faulty power supply from the SCB.

T098 – Circuit A Economizer Pressure Transducer Failure – 1 Alert

T098 – Circuit A Economizer Pressure Transducer Failure – 2 Alert

T099 – Circuit B Economizer Pressure Transducer Failure – 1 Alert

T099 – Circuit B Economizer Pressure Transducer Failure – 2 Alert

Action taken by control:  Affected circuit is shut down.

Reset Method:  Automatic

There are two conditions that will generate this alert.  

The “-1” alert will be generated if the voltage ratio (Voltage Measured / Voltage Reference) by the Screw Board (SCB) is greater than 99.9% or less than 0.5%.

The “-2” alert is generated if the Economizer Pressure is 12 psig (83 kPa) less than the Suction Pressure for 6 seconds.  The alarm will reset automatically if the economizer pressure is greater than the suction pressure by 5 psig (34 kPa).   MBB Software Versions starting with 4.5 increased the trip time to 15 seconds. 

If this condition is encountered, check the following items:

· Check for a faulty transducer.

· Check for a wiring error or problem between transducer and the SCB.

· Check to be sure that the Economizer and Suction Pressure Transducers are not swapped.

· Check for a faulty power supply from the SCB.

· Check to be sure that the Suction Service Valve is open, if equipped.

· Check to be sure that the EXV/EXD is opening.

· On non-economized units, consider upgrading the software to at least MBB Version 4.5.

T110 - Circuit A Loss of Charge Alert

T111 - Circuit B Loss of Charge Alert

Action taken by control:  Circuit shut down

Reset Method:  Manual (MBB)

This alert is generated if the control senses a discharge pressure less than 10 psi (68.3 kPa) for 30 seconds.  This alert criteria is active only when if no compressors are running in the circuit.

If this condition is encountered, check the following items:

· Check the discharge pressure transducer accuracy.  Replace the transducer if necessary.

· Check the refrigerant charge for the circuit.

T120 - Circuit A Low Saturated Suction Temperature Alert

T121 - Circuit B Low Saturated Suction Temperature Alert

Action taken by control:  Circuit shut down

Reset Method:  Manual (MBB)

This alert is generated by one of two conditions.  If the Saturated Suction Temperature for the circuit is sustained at 6 (F (3.3 (C) below the BR.FZ, Brine Freeze Point (Configuration Mode, Sub-mode SERV) for 3 minutes the alert will be generated.  Before the machine alerts, the control will attempt to correct the situation by opening the EXV to allow more refrigerant into the cooler to raise the suction pressure. The other condition to generate this alert is if the Saturated Suction Temperature is less than the BR.FZ - 28 (F (15.6 (C).  The control will also signal an operational mode, “Low Cooler Suction Temperature”.  In this mode, the circuit will not load further.   

With these two alerts, there is a 1 hour prohibition timer included.  The alert cannot be reset until 1 hour has elapsed.

If this condition is encountered, check the following items

· Check the liquid line strainer for restrictions.  All machines have cleanable strainers.  30HXA076-146 and 30HXC076-146 use a smaller strainer than the other machines.  This has been known to restrict the flow over time at the outlet.  There is very little flow over the outside surface of the basket.  To resolve this, a dimple was added to the basket assembly.  Starting with serial number 5200F an improved strainer and basket assembly started into production.

· Check the charge of the machine.

· Check the EXV/Economizer operation.  Check the EXV/Economizer Cable for shorts.

· In economized circuits, if the motor temperature is cold, check for a sunken float.  

· On 30HX machines, be sure that the bubbler tube shut-off valve is open.

· Check the head pressure control method, if the condition occurs during low ambients.

· Check the water flow for the cooler.  Low water flow can cause this alarm.

· Check the loop volume and flow rate.  Rapid changes in load can cause this alarm.  Consider increasing the Z.GN Deadband Multiplier (Configuration Mode, Sub-mode SLCT).

· For Brine applications, check the BR.FZ, Brine Freeze Point (Configuration Mode, Sub-mode SERV).  It should be set slightly above the temperature to which the loop is protected.  Brine has poorer heat transfer properties causing the suction temperature to decrease to maintain the capacity.

· For 30HXA machines, check to be sure that the liquid line solenoid valves are operating properly.  The solenoids are wired in parallel with the fan relays.  The fans are turned on as soon as the compressors are energized.

· Check to be sure that PRTS Pressure Transducers, (Configuration Mode, Sub-mode OPT1) are set to YES.  If this value is NO, the pressure transducers will not read a suction pressure.

· Check to be sure that the compressor loaders are sequenced properly and are operating, as they should.  Compressor Loader 1 is closest to the discharge end of the compressor.  Compressor Loader 2 is closest to the gear end of the compressor.  The Controls & Troubleshooting Book, 30G,H-7T depicted the loader position incorrectly.

· On 30HXA171 Brine Option machines the Circuit A Economizer was changed to a larger orifice EXD beginning with serial number 3602Q.  If trend data indicates that the EXV is open too much, consider replacing the orifice to the new larger one.

Service Bulletins pertaining to this condition:

· SMB010012 – 30HXA/HXC076-146 Liquid Line Strainer Change

This bulletin advised of the new strainer assembly for the 30HXA/HXC076-146 machines.

T122 - Circuit A High Saturated Suction Temperature Alert

T123 - Circuit B High Saturated Suction Temperature Alert

Action taken by control:  Circuit shut down

Reset Method:  Manual (MBB)

This alert algorithm is active only after 90 seconds of operation has elapsed.  The alert will be generated if the Saturated Suction Temperature is greater than 55 (F (12.8 (C) and the EXV position is less than 1% for 5 minutes.

If this condition is encountered, check the following items:

· Check the EXV for proper operation.

· Check the Liquid Level Sensor for proper operation.

· Check the suction pressure transducer calibration and wiring.

· If a contactor failure alert, a subset of T051, T052, T056 and T057, is indicated but the compressor is not operational, the control will assumes the circuit is operational and continues to operate the EXV.  Without the compressor operating, the cooler fills with liquid, raising the saturated suction temperature to the alert limit.

T124 - Circuit A Low Oil Level

T125 - Circuit B Low Oil Level

Action taken by control:  Circuit shut down

Reset Method:  Automatic/Manual (MBB)

The alert is generated when one of two conditions is satisfied.  If the circuit is off, the alert will be generated when the oil level switch float opens indicating not enough oil in the sump.  The alert will be generated if the circuit is active and the oil level switch opens for 10 seconds.  

On 30GXN/GXR units, if the circuit is in this alarm the oil heater will not energize even if the saturated condensing temperature is within the criteria to be on.

The control will allow the machine to reset automatically, if the level switch closes.  Up to 3 automatic resets are allowed in an 18 hour period.  The alarm is a manual reset if the fourth alarm occurs again within the 18 hour period.

If this condition is encountered, check the following items:

· Check the circuit for rapid cycling.  The system will recover the oil in the circuit more efficiently under full load.  If the machine is cycling rapidly, increase the Z.GN, Deadband Multiplier (Configuration Mode, Sub-mode SLCT).  The machine is shipped from the factory at 2.0.

· Check the oil level switch for proper operation.

· Check for a wiring error.

· Check the MBB for a bad monitoring channel.

· On 30GX machines, check the York mesh to be sure that it is not interfering with the operation of the float.

To recover the oil, use the oil recovery procedure outlined in the Service section.  Add additional oil to the circuit to close the oil level switch.  The added oil may need to be removed from the system later.

If the alert condition continues, consider adding ½ gallon of oil to the circuit.  Continue adding oil in ½ gallon increments to a maximum of 1-½ gallons.  Do not overcharge the oil system.  The extra oil will accumulate in the cooler, fouling the cooler.

Software Version 1.0 allowed the alert to reset prior to the switch closing.  Version 3.1 Software corrected this problem.  However, Version 3.1 will allow the circuit to start and operate, once for less than 30 seconds if the oil level switch is open.  

Service Bulletins pertaining to this condition:

· SMB01?? – ComfortLink Main Base Board Software

This bulletin addressed the versions of screw software.

T126 - Circuit A High Discharge Pressure Alert

T127 - Circuit B High Discharge Pressure Alert

Action taken by control:  Circuit shut down

Reset Method:  Automatic/Manual (MBB)

This alert is generated if the control senses a Saturated Condensing Temperature greater than the Maximum Condensing Temperature Set Point by more than 5 (F (2.8 (C).  If the circuit is on, it will be stopped.  If the circuit is off, it will not be allowed to start. This alarm will reset automatically if the condition corrects itself the first time.  If the alarm is indicated again within 18 hours, the alarm is a manual reset.

If this condition is encountered, check the following items:

· Check the discharge pressure transducer calibration.  Replace the transducer if necessary.

· Confirm the proper value for the HD.P.A and HD.P.B, Head Pressure Set Point (Set Point Mode, Sub-mode HEAD).  Prior to Software Version 2.0, prior Serial Numbers 5100F, the factory configuration values were set incorrectly.

· Check the refrigerant charge for the circuit.

· Check for non-condensables in the circuit.

· Check for an airside restriction for air-cooled chillers.  Check fan operation for proper airflow.

· Check for a water flow restriction for water-cooled chillers.  Check condenser pump for proper operation.

Service Bulletins pertaining to this condition:

· SMB010007 – ComfortLink 30HXA/HXC Head Pressure Set Point Setting

This bulletin described the correct factory settings required for the head pressure set points.

A128 - Circuit A Condenser Freeze Protection Alarm

A129 - Circuit B Condenser Freeze Protection Alarm

Action taken by control:
If the circuit is on, the circuit is shutdown.  If the circuit is off, it is not allowed to start.  In both cases, the condenser pump is turned on.

Reset Method:  Automatic

This alarm is valid for 30HXC or 30HXA machines with water cooled condensers only.  It is ignored if the chiller is configured for brine duty.  The alarm is generated if the control senses the discharge pressure less than or equal to 30 psig (206 kPa) for  4 seconds.  This equates to a Saturated Condensing Temperature is less than 34 (F (1 (C).  The alarm will reset, if the discharge pressure for the affected circuit is greater than 35 psig (240 kPa).

With the introduction of Main Base Board software Version 3.1, if this condition is encountered, the water regulating valve will be commanded to its 100% open position.

If this condition is encountered, check the following items:

· Check the discharge pressure transducer for accuracy.  Replace the transducer if necessary. 

· Check the discharge pressure transducer wiring for an error.

· Check the refrigerant charge for the circuit.  Loss of refrigerant charge will cause this alarm.

· If this alert has occurred on non-water cooled machine, check the unit configuration for a proper unit type.

· MBB Version 1.0 software did not have the brine exclusion for this alarm.  If this condition is encountered, upgrade the software.

T131 - Circuit A Liquid Level Sensor Failure Alert

T132 - Circuit B Liquid Level Sensor Failure Alert

Action taken by control:  Circuit continues to run under Discharge Superheat Control

Reset Method:  Automatic

This alert is generated if the liquid level sensor thermistors indicate a temperature of greater than 245 (F (118 (C) or –40 (F (-40 (C) with a saturated suction temperature greater than 9 (F (-12.8 (C).  If one of these conditions is indicated, the circuit will alert.  The circuit will continue to operate under discharge superheat control.  The alert will reset if the liquid level sensor returns to a valid range of –40 (F to 245 (F (-40 to 118 (C).

This alarm may be generated erroneously if the cooler Saturated Suction Temperature is below 9 (F (-12.8 (C) with all 3 thermistors immersed in liquid refrigerant.

If this condition is encountered, check the following items:

· Check for a faulty liquid level sensor, heater or thermistors.

· Check for a wiring error of the liquid level sensor.

T135 - Circuit A Failure to Pumpout Alert

T136 - Circuit B Failure to Pumpout Alert

Action taken by control:  None – Warning only

Reset Method:  Automatic

ComfortLink introduced a pumpout routine at shut down.  This routine has changed several times since its introduction.  The pumpout criteria is as follows:

Pumpout will terminate when the Saturated Suction Temperature (SST) falls by 10 (F (5.5 (C), reaches the Brine Freeze Set Point - 6(F (3.3 (C), or if the Saturated Suction Temperature is less than 10 (F (-12.2 (C).  Pumpout will not be initiated if the Saturated Suction Temperature is less than 10 (F (-12.2 (C) The control expects this to take place within 360 seconds.

If this condition is encountered, check the following items:

· MBB Version 1.0 Software’s criteria for pumpout termination was for the Saturated Suction Temperature must reach –15 (F (-26 (C) within 180 seconds or reach the Brine Freeze Set Point – 6 (F (3.3 (C) within 180 seconds.  This proved to be too short of a time period for brine applications.  The original release alert was a manual reset.  Beginning 5100F, MBB Version 2.0 increased the time to 360 seconds.  Version 2.0 made this alert a warning only.  Upgrade the software, if this condition is encountered.  Beginning with Version 3.1 the pumpout algorithm does not initiate pumpout if the Saturated Suction Temperature is less than 10 (F (-12.2 (C).  An additional criterion for termination if the Saturated Suction Temperature reaches 10 (F (-12.2 (C) was added.  Version 4.0 removed the alerts and used the compressor loaders after two (2) minutes of pumpout to aid in the routine.

· Check the EXV/EXD operation.

· Check the transducer calibration and wiring that may cause erratic readings.  Replace the transducer if necessary.

T137 - Circuit A Low Discharge Superheat Alert

T138 - Circuit B Low Discharge Superheat Alert

Action taken by control:  Circuit shut down

Reset Method:  Manual (MBB)

This alert is ignored for the first 3 minutes of circuit operation.  This alert is generated when the control measures a discharge superheat less than 5 (F (2.8 (C) for 10 minutes.

If this condition is encountered, check the following items:

· Check the Discharge Gas Thermistor for accuracy.  Replace the sensor if necessary.

· Check the Discharge Pressure Transducer for accuracy.  Replace the transducer if necessary.

· Check the wiring and location of the sensors to be sure that they are wired to the appropriate point, and located correctly.

· Check DIS.S Discharge Super. Setpoint (Configuration Mode, Sub-mode UNIT).  It should be set for 22 (F (-5.5 (C).

· Check the economizer EXV for proper operation.  Overfeeding can cause this alarm.

· Check the economizer for a sunken or stuck float.  This causes liquid refrigerant to enter the motor cooling port.  There is not enough heat in the motor to vaporize the liquid, depressing the discharge superheat. 

· Check the MT.SP Motor Temp Set Point, (Configuration Mode, Sub-mode SERV).  It should be set for 200 (F (93 (C) for FLUD Cooler Fluid, (Configuration Mode, Sub-mode OPT1) set to Water.  Beginning with Version 3.1 any unit configured for brine operation FLUD set to Medium Temperature Brine will change the Motor Temp Setpoint to 170 (F (76.7 (C).  The control attempts to control to set point.  If the set point is too low, more liquid refrigerant can be sent to the motor than is necessary depressing the discharge superheat and generating this alert. 

· Check the Liquid Level Set Point.  The LVL.A Liquid Level Setpoint A or LVL.B Liquid Level Setpoint B (Set Point Mode, Sub-mode LIQ) is factory defaulted to 1.8.  If the level is too high, liquid carry-over can depress the discharge superheat.

· On the 30HXC146, Circuit B is known to generate a T137 Alert.  Consider lowering the LVL.B Liquid Level Setpoint B (Set Point Mode, Sub-mode LIQ) to 1.0.  

· Check the Liquid Level Sensor for proper operation.

· Check for a failed open motor cooling solenoid.

Service Bulletins pertaining to this condition:

· SMB01?? – ComfortLink Main Base Board Software

This bulletin addressed the versions of screw software.

T140 – Compressor A1 High Oil Filter Pressure Drop Alert

T141 – Compressor A2 High Oil Filter Pressure Drop Alert 

T142 – Compressor B1 High Oil Filter Pressure Drop Alert 

T143 – Compressor B2 High Oil Filter Pressure Drop Alert 

Action taken by control:  Alert only, no action taken by the control

Reset Method:  Manual (MBB)

This alert is generated if the oil filter pressure drop (Discharge Pressure – Oil Pressure) is exceeds 25 psid (172 kPa) for 30HXC machines, or 30 psid (207 kPa) for 30GX and 30HXA machines for 1 minute.  

In Version 4.0 Software the time to trip was increased to 5 minutes.  

The value FD.A1 A1 Oil Filter Diff. Press, FD.A2 A2 Oil Filter Diff. Press, (Pressure Mode, Sub-mode PRC.A), FD.B1, B1 Oil Filter Diff. Press, FD.B2 B2 Oil Filter Diff. Press (Pressure Mode, Sub-mode PRC.B) indicate the pressure drop measured by the control.

If this condition is encountered, check the following items:

· Check the oil filter pressure drops, change as necessary. If the filters are plugging rapidly, have a filter analyzed for content.  There have been reports filters plugging with filter drier.  The filter drier is a granular design and has been known to disintegrate.

· Check the operation of oil solenoid valve.

· Check the calibration of the discharge and oil pressure transducer.

· If the pressure drop is within acceptable limits, consider upgrading the software to at least Version 4.0.  This version increased the time to trip the alert.

Service Bulletins pertaining to this condition:

· SMB000060 – 30GX/HX Replacement External Oil Filter History

This bulletin addressed the numerous changes to the external filter.

· SMB010008 – 06N Internal Oil Filters Plugging


This bulletin described the problem with the motor cooling filter drier disintegrating during operation.  A solid core filter drier was installed starting with serial number 5200F.

A150 – Unit is in Emergency Stop Alarm

Action taken by control:  Machine shut down

Reset Method:  CCN/Automatic

This alarm is generated when a CCN command for the machine to shut down is received.  This will be displayed in STAT, Control Mode (Run Status Mode, Sub-mode VIEW).

If this condition is encountered, check the following items:

· Check for an illegal configuration.

· A CCN command will be required to remove the force.

A151 – Illegal Configuration x Alarm

Action taken by control:  Machine not allowed to start

Reset Method:  Manual (MBB)

This alarm is generated if control detects an illegal configuration.  The error must be corrected before the machine can be started.  Within the alarm code will be one of the following codes to indicate the illegal configuration.

	Code Number
	Illegal Configuration Description

	1
	TYPE Unit type (Configuration Mode, Sub-mode UNIT) not one of the following:  Air Cooled, Fluid Cooled, Split System, Heat Machine, or Heat Reclaim.

	2
	CMP.A Number Circ A Compressors (Configuration Mode, Sub-mode UNIT) outside the range of 1-2

	3
	CMP.B Number Circ B Compressors (Configuration Mode, Sub-mode UNIT) outside the range of 1-2

	4
	Illegal Fan Configuration

	5
	Air-cooled chiller, TYPE=Air-Cooled with FLUD Cooler Fluid (Configuration Mode, Sub-mode OPT1) set for Low Brine 

	6
	Water-cooled chiller, TYPE=Fluid Cooled configured for HPCT Head Press. Control Type (Configuration Mode, Sub-mode OPT1) to Air-cooled

	7
	Air Cooled chiller, TYPE=Air Cooled with CNP.I Condenser Pump Interlock (Configuration Mode, Sub-mode OPT1) ON.

	8
	Air Cooled chiller, TYPE=Air Cooled with CST.S Condenser Fluid Sensors (Configuration Mode, Sub-mode OPT1) YES


If this condition is encountered, check the following items:

· Correct the configuration as noted above.

Service Bulletins pertaining to this condition:

· SMB010011 – 30HXA ComfortLink Remote Condenser Fan Configuration and Operation

This bulletin addressed the configuration steps required to configure the remote condenser fan operation based on software version.

A152 – Unit Down Due to Failure

Action taken by control:  None

Reset Method:  Automatic

This alarm will be generated if there are 1 or more alerts active on each circuit.  Alarms are only sent on the CCN bus.  Alerts are not sent on the CCN bus.  To broadcast the problem, the alarm was created.

If this condition is encountered, see the individual alerts and correct those conditions that lead to the alert.

With the introduction of Main Base Board Version 2.0, starting Serial Number 5100F, this alarm is only generated if there is a Flotronic System Manager (FSM) controlling the machine.  FSM uses the A152 alarm to mark the chiller as off-line.

Service Bulletins pertaining to this condition:

· SMB01?? – ComfortLink Main Base Board Software

This bulletin addressed the versions of screw software.

A153 – Real Time Clock Hardware Failure Alarm

Action taken by control:  Occupancy defaults to Occupied

Reset Method:  Automatic

This alarm is indicated when the time clock is not initialized or fails to increment.  The alarm will reset when the time is initialized or starts incrementing again.  If this condition is encountered, replace the Main Base Board.

If this condition is encountered, check the following items:

· Check the HH.MM, Hour and Minute, (Time Clock Mode, Sub-mode TIME).

A154 – Serial EEPROM Hardware Failure Alarm

Action taken by control:  Machine shuts down

Reset Method:  Manual

This alarm is indicated when the internal diagnostics determines an internal failure of the EEPROM.

If this condition is encountered, the Main Base Board will need to be replaced.

A155 – Serial EEPROM Storage Failure Error Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Manual

This alarm is indicated when an internal diagnostic finds an error on critical data.  The following points are critical data items:

TYPE, Unit Type (Configuration Mode, Sub-mode UNIT)

TONS, Unit Size (Configuration Mode, Sub-mode UNIT)

CMP.A, Number Circ A Compressor (Configuration Mode, Sub-mode UNIT)

CMP.B, Number Circ B Compressor (Configuration Mode, Sub-mode UNIT)

FAN.S, Fan Staging Select (Configuration Mode, Sub-mode UNIT)

FLUD, Cooler Fluid (Configuration Mode, Sub-mode OPT1)

HPCT, Head Press Control Type (Configuration Mode, Sub-mode OPT1)

CNP.I, Condenser Pump Interlock (Configuration Mode, Sub-mode OPT1)

CSP1, Cooling Set Point 1 (Set Point Mode, Sub-mode COOL)

HSP1, Heating Set Point 1 (Set Point Mode, Sub-mode HEAT)

If this condition is encountered, 

· Download the software to the module.

· Consider replacing the Main Base Board.

A156 – Critical Serial EEPROM Storage Failure Error Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Manual

This alarm is indicated when an internal diagnostic finds an error on critical data.

If this condition is encountered, 

· Consider replacing the Main Base Board.

A157 – A/D Hardware Failure Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Manual

This alarm occurs when the Analog to Digital Converter, an internal component on the Main Base Board, fails.

If this condition is encountered,

· Consider replacing the Main Base Board.

A159 – Loss of Condenser Flow Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Manual

This alarm is tested only when the condenser pump is ON.  It is generated if the condenser flow switch fails to close within 1 minute of start-up of the condenser pump, or if it opens for 10 seconds during normal operation.  If the alarm is generated, the machine will be shut down, but the condenser pump operation will not be affected.

If a water regulating valve is used, CND.I, Condenser Pump Interlock (Configuration Mode, Sub-mode OPT1) should not be used.

The CNPC Condenser Pump Control (Configuration Mode, Sub-mode OPT1) must be “ON WITH MODE” or “ON WITH COMPRESSOR(S)” for this algorithm to be active.

If this condition is encountered, check the following items:

· Check for a wiring error to the condenser flow switch.

· Check the condenser flow switch setting.

· Check for low condenser water flow.

· Check for a condenser water pump failure.

A172 – Loss of Communication with EXV Module Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Automatic

If the Main Base Board looses communication with the EXV Module, the alarm will be tripped.

The alarm will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the red LED on the board.  All red LEDs should be blinking in unison.

· Check the Local Equipment Network (LEN) for a wiring error.

· Check for a 24 volt supply to the EXV module.

· Check the EXV module address.

· Check for a grounded EXD/Economizer Cable or motor assembly.  A short to ground can disable the communications bus.

T173 – Loss of Communications with Energy Management Module Alert

Action taken by control:  EMM options are disabled.

Reset Method:  Automatic

This alarm is tested only if EMM, EMM Module Installed, (Configuration Mode, Sub-mode OPT1) is YES, or an option is configured that requires the EMM.  The alert is triggered if the MBB looses communication with the EMM.  If the alert is indicated the following actions will be taken by the control:

· CRST, Cooling Reset Type, (Configuration Mode, Sub-mode RSET) from external temperature or 4-20 ma input will be disabled.

· DMDC, Demand Limit Select, (Configuration Mode, Sub-mode RSET) Demand Limit by Switch Control or 4-20 ma input will be disabled.

· CLSP, Cooling Set Point Select, (Configuration Mode, Sub-mode SCLT) Set point by an external switch or 4-20 ma will be ignored.  Set point will be controlled by CSP1, Cooling Set Point 1, (Set Point Mode, Sub-mode COOL).

· ICE.M, Ice Mode Enable, (Configuration Mode, Sub-mode OPT2) Ice Build shall be disabled.  

The alert will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the red LED on the board.  All red LEDs should be blinking in unison.

· Check the Local Equipment Network (LEN) for a wiring error.

· Check for a 24 volt supply to the EMM module.

· Check the EMM module address.

· If there is no EMM board installed, check the configurations that would require the EMM board.  If any are enabled, and the EMM is not installed, this alarm will be generated. 

T174 – 4-20 mA Cool Setpoint Input Failure Alert

Action taken by control:  CSP.1 will be used for set point.

Reset Method:  Automatic

This alarm is tested only if EMM, EMM Module Installed, (Configuration Mode, Sub-mode OPT1) is YES, and the communication status is good.  The alert is triggered if the input signal is less than 2 mA or greater than 22 mA.  If the alert is indicated the control will use CSP.1, Cooling Set Point 1, (Set Point Mode, Sub-mode COOL).

The alert will reset automatically, once the input signal returns to the normal range of 2-22 mA. Once the signal returns to normal range, the option will function again.

Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used. 

If this condition is encountered, check the following items:

· Confirm the input signal value, CSP, 4-20 mA Cooling Set Point (Inputs Mode, Sub-mode 4-20).

· Confirm the proper polarity of the 4-20 mA signal.

· Check the input signal wiring.

T175 – 4-20 mA Heat Setpoint Input Failure Alert

Action taken by control:  HSP.1 is used for set point.

Reset Method:  Automatic

This alarm is tested only if EMM, EMM Module Installed, (Configuration Mode, Sub-mode OPT1) is YES, and the communication status is good.  The alert is triggered if the input signal is less than 2 mA or greater than 22 mA.  If the alert is indicated the control will use HSP.1, Heating Set Point 1, (Set Point Mode, Sub-mode HEAT).

The alert will reset automatically, once the input signal returns to the normal range of 2-22 mA.  Once the signal returns to normal range, the option will function again.

Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used. 

If this condition is encountered, check the following items:

· Confirm the input signal value, HSP, 4-20 mA Heating Set Point (Inputs Mode, Sub-mode 4-20).

· Confirm the proper polarity of the 4-20 mA signal.

· Check the input signal wiring.

T176 – 4-20 mA Reset Input Failure Alert

Action taken by control:  Reset option is disabled.

Reset Method:  Automatic

This alarm is tested only if EMM, EMM Module Installed, (Configuration Mode, Sub-mode OPT1) is YES, and the communication status is good.  The alert is triggered if the input signal is less than 2 mA or greater than 22 mA.  If the alert is indicated the control will terminate reset.

The alert will reset automatically, once the input signal returns to the normal range of 2-22 mA, and reset will begin again.

Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used. 

If this condition is encountered, check the following items:

· Confirm the input signal value, RSET, 4-20 mA Reset Signal (Inputs Mode, Sub-mode 4-20).

· Confirm the proper polarity of the 4-20 mA signal.

· Check the input signal wiring.

T177 – 4-20 mA Demand Limit Input Failure Alert

Action taken by control:  Reset option is disabled.

Reset Method:  Automatic

This alarm is tested only if EMM, EMM Module Installed, (Configuration Mode, Sub-mode OPT1) is YES, and the communication status is good.  The alert is triggered if the input signal is less than 2 mA or greater than 22 mA.  If the alert is indicated the control will terminate reset.

The alert will reset automatically, once the input signal returns to the normal range of 2-22 mA, and reset will begin again.

Care should be taken when interfacing with other manufacturer’s control systems, due to power supply differences, full wave bridge versus half wave rectification.  The two different power supplies cannot be mixed.  ComfortLink controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used. 

If this condition is encountered, check the following items:

· Confirm the input signal value, DMND, 4-20 mA Demand Signal (Inputs Mode, Sub-mode 4-20).

· Confirm the proper polarity of the 4-20 mA signal.

· Check the input signal wiring.

A178 – Loss of Communication with Screw Chiller Module Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Automatic

If the Main Base Board looses communication with the Screw Chiller Module (SCB), the alarm will be tripped.

The alarm will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the red LED on the board.  All red LEDs should be blinking in unison.

· Check the Local Equipment Network (LEN) for a wiring error. 

· Check for a 24 volt supply to the SCB module.

· Check the SCB module address.

A180 -  Loss of Communication with Compressor Protection Module 1 Alarm

A181 -  Loss of Communication with Compressor Protection Module 2 Alarm

Action taken by control:  Machine is shut down.

Reset Method:  Automatic

If the Main Base Board looses communication with the ComfortLink Compressor Protection (CCP) Module, the alarm will be tripped.  Any compressor controlled by the affected CCP, will be considered unavailable.

On software versions earlier than 4.0 the machine would not restart after a brief power interruption.  This was caused by the MBB not seeing the power loss, while the TI board did.  It has been fixed by having the MBB receive information from the TI board that it has seen a power loss.  The MBB will then restart the unit.

The alarm will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the red LED on the board.  All red LEDs should be blinking in unison.

· Check the Local Equipment Network (LEN) for a wiring error.

· Check for a 24 volt supply to the CCP module.

· Check the CCP module address.

· Consider upgrading the software, if the software version is 3.1 or earlier.

T182 – Compressor Protection Module 1 Internal Diagnostic Alert

T183 – Compressor Protection Module 2 Internal Diagnostic Alert

Action taken by control:  Affected compressors are shut down.

Reset Method:  Manual (CCP, MBB)

This alert is generated if the Main Base Board receives an internal diagnostic alert from a ComfortLink Compressor Protection (CCP) Module.  This failure will require the power to the CCP to be removed in order to reset the alert.  Clear the alert from the CCP first, before clearing it from the Main Base Board. 

If this condition is encountered, 

· Check for EMI sources around the module.

· Consider replacing the CCP module if the module continues to trip on this alert.

A200 – Cooler Pump Interlock Failed at Start-Up

Action taken by control:  Unit prevented from starting.

Reset Method:  Manual

This alarm is signaled by one of two conditions.  If the cooler pump interlock does not close within 5 minutes of the unit transitioning from OFF to ON, or after the start of the cooler pump, the alarm will be generated.

If this condition is encountered, check the following items:

· Check the operation of the cooler pump.

· Check the operation of the chilled water flow switch.

· Check the wiring of the chilled water pump interlock, flow switch, auxiliary contacts, etc.  On early 30HX machines produced with the thermal dispersion flow switch, the wiring diagram was incorrect.  The diagram showed the ORN wires to FSR connected to terminals FSR-1 and FSR-8 rather than FSR-1 and FSR-3.

· Check to be sure that any isolation valves are open or are functioning properly.

· Check the chilled water strainer for any restriction.

A201 – Cooler Pump Interlock Failure Contacts Open During Normal Operation Alarm

Action taken by control:  Unit shut down.

Reset Method:  Manual

This alarm is tested only after the criteria for A200 has been satisfied.  This alarm is signaled if the cooler pump interlock opens for 15 seconds continuously.

If this condition is encountered, check the following items:

· Check the operation of the cooler pump.

· Check the operation of the chilled water flow switch.

· Check the wiring of the chilled water pump interlock, flow switch, auxiliary contacts, etc.

· Check to be sure that any isolation valves are open or are functioning properly.

· Check the chilled water strainer for any restriction.

A202 – Cooler Pump Interlock Failure Contacts Closed While Pump is OFF Alarm

Action taken by control:  Unit shut down.

Reset Method:  Manual

This alarm is signaled only if the cooler pump interlock is closed for 10 seconds just before the cooler pump is started.

If this condition is encountered, check the following items:

· Check the operation of the cooler pump.  Be sure that it is not in a manual mode, running continuously.

· Check the cooler pump relay and starter for proper operation.

· Check the operation of the chilled water flow switch, or other device installed in series.

· Check the wiring of the chilled water pump interlock, flow switch, auxiliary contacts, etc.

· In Main Base Board (MBB) Version 2.0 and 3.1 software, if the machine is a duplex module or arranged in parallel flow and pump control is enabled, the machine will alarm when it is started.  See Cooler Pump Control on 14 for information on how to address this situation.

T203 – Loss of Communication with the Slave Chiller Alert

Action taken by control:  Master becomes the lead chiller.

Reset Method:  Automatic

This alarm is tested only on the master chiller when LLEN, Lead/Lag Chiller Enable (Configuration Mode, RSET Sub- mode) is set to ENBL.  The master chiller initiates all communication.  If there is no response, or the response is no acknowledgement for 3 minutes, the alert will be generated.  The master chiller will act as a stand alone machine.  The master chiller will continue to re-establish the communication.

The alarm will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the Carrier Comfort Network (CCN) wiring.

· Be sure the Slave Chiller has control power.

· Be sure that the Slave Chiller CCNA, CCN Address (Configuration Mode, Sub-mode OPT2) matches the SLVA, Slave Address (Configuration Mode, Sub-mode RSET) in the Master Chiller.

T204 – Loss of Communication with the Master Chiller Alert

Action taken by control:  Slave operates as a stand alone chiller.

Reset Method:  Automatic

This alarm is tested only on the master chiller when LLEN, Lead/Lag Chiller Enable (Configuration Mode, Sub-mode RSET) is set to ENBL.  The master chiller initiates all communication.  If there is no communication from the master chiller for 3 minutes, the alert will be generated.  The slave chiller will become a stand alone machine.  The master chiller will continue to re-establish the communication.

The alarm will reset automatically, once communication is re-established.

If this condition is encountered, check the following items:

· Check the Carrier Comfort Network (CCN) wiring.

· Be sure the Master Chiller has control power.

· Be sure that the Slave Chiller CCNA, CCN Address (Configuration Mode, Sub-mode OPT2) matches the SLVA, Slave Address (Configuration Mode, Sub-mode RSET) in the Master Chiller.

T205 – Master and Slave Chiller with Same Address Alert

Action taken by control:  Dual Chiller control disabled.

Reset Method:  Automatic

This alarm is tested only on the master chiller when LLEN, Lead/Lag Chiller Enable (Configuration Mode, Sub-mode RSET) is set to ENBL, and MSSL, Master/Slave Select (Configuration Mode, Sub-mode RSET) is MAST.  The master chiller checks its CCN address, CCNA, CCN Address (Configuration Mode, Sub-mode OPT2) against the slave address entered in SLVA, Slave Address (Configuration Mode, Sub-mode RSET).  If the two addresses are the same, the alert will be generated.

The alarm will reset automatically, once the address conflict is corrected.

If this condition is encountered, check the following items:

· Be sure that the Slave Chiller CCNA, CCN Address (Configuration Mode, Sub-mode OPT2) matches the SLVA, Slave Address (Configuration Mode, Sub-mode RSET) in the Master Chiller.  Check the Master Chiller CCNA, CCN Address (Configuration Mode, Sub-mode OPT2) to be sure that it is not the same as the Slave chiller address.

T206 – High Leaving Chilled Water Temperature Alert

Action taken by control:  None

Reset Method:  Automatic

The criterion for this alert is checked when the unit is ON and the total available capacity is 100%.  The alert is generated when the leaving chilled water temperature is greater than the LCWT, High LCW Alert Limit (Configuration Mode, Sub-mode OPT2) plus the control point and the leaving chilled water temperature is higher than it was 1 minute before the current reading.  The LCWT is a delta temperature, not an absolute value.  The alert will automatically reset when the leaving water temperature is less than the control point, or is less than the control point plus LCWT minus 5 (F (2.8 (C).

If this condition is encountered,

· Check building load

· Check the LCWT, High LCW Alert Limit (Configuration Mode, Sub-mode OPT2) value

· Check compressor operation

· Check water flow

A207 – Cooler Freeze Protection Alarm

Action taken by control:  Chiller shut down or prevented from starting

Reset Method: Automatic/Manual (MBB)

This alarm will be generated when the entering or leaving water temperature is below BR.FZ, Brine Freeze Point (Configuration Mode, Sub-mode SERV) plus 2 (F (1.1 (C).  When this condition is encountered, the machine will enter Mode 16, and the Chilled Water Pump relay will be energized, even if the CPC Cooler Pump Control (Configuration Mode, Sub-mode OPT1) is OFF.  The unit will be shut down or prevented from starting.

The control will allow the machine to reset automatically if the leaving chilled water temperature rises above the CSP.1 Cooling Setpoint 1 (Set Point Mode, Sub-mode COOL) plus 6 (F (3.3 (C).   If the alarm is generated again within an 18 hour period, it shall be a manual reset.

If this condition is encountered, check the following items:

· Check the entering or leaving water thermistor for accuracy.

· Check water flow rate.

· Check for freezing conditions.

· Check the heat tape and other freeze protection means for proper operation.

· Check glycol concentration and adjust BR.FZ accordingly.

T210 – Winterization Required Alert

Action taken by control:  None

Reset Method:  Manual (MBB)

This alert was added in Version 4.0 software.  This alert is generated when the unit is off and the Saturated Condensing Temperature on either circuit is less than 32 ºF (0 ºC).  The Alert is displayed and the unit is allowed to run.  The purpose of the alert is to notify the owner of the potential cooler freeze condition.  Once the winterization is complete, the alert criteria is reset after 15 consecutive days where the outdoor ambient temperature remains at or above 45 ºF (7.2 ºC) as sensed by the discharge pressure transducer while the compressor(s) are off.

If sub-freezing conditions have not been encountered, check the following items:

· Check the Discharge Pressure Transducer calibration, replace as necessary.

· Check the refrigerant charge on the machine.

· If this is a new start-up, or new software has been downloaded, the alert can be generated if the initial pressure scan has not connected with the transducer indicating an open circuit.

In order to reset this alert even if subfreezing conditions have not been encountered, the W.DNE Winterization Performed (Configuration Mode, Sub-mode SERV) must be set to YES to reset the alert.

If sub-freezing conditions have been encountered, the following issues must be accomplished.

· The chilled water loop must be winterized, in accordance with the instructions provided in the Controls, Start-Up, Operation and Troubleshooting Book.  Once this has been completed, W.DNE Winterization Performed (Configuration Mode, Sub-mode SERV) must be set to YES to reset the alert.

This alert is configurable, WM.SG Winterize Alert Config (Configuration Mode, Sub-mode OPT2).  The factory default is ENBL. 

The software logs the date and time of the alert, the time winterization was completed, and if the configuration has changed.

Service Bulletins pertaining to this condition:

T950 – WSM POC Communication Failure Alert

Action taken by control:  Unit is allowed to operate as a stand alone machine

Reset Method: Automatic

This alert will be generated if the Main Base Board has not received any communications from the WSM for 5 minutes after a transmission.  This is condition is encountered, the WSM forces are removed and the unit is allowed to operate as a stand alone machine.

The alert will reset once communications are re-established.

If this condition is encountered, check the following items:

· Check the configuration of the WSM, be sure that the addresses agree.

· Check the CCN wiring for a proper connection and wiring.  Be sure that the plugs are securely seated and connections are tight.

· Check for a faulty WSM or Main Base Board.

· Check for proper power to the devices.

A951 – FSM Loss of Communication Alert

Action taken by control: Unit is allowed to operate as a stand alone machine

Reset Method:  Automatic

This alert will be generated if the Main Base Board has not received any communications from the CSM (Chiller System Manager) or FSM (Flotronic System Monitor) for more than 20 seconds.  This is condition is encountered, the FSM forces are removed and the unit is allowed to operate as a stand alone machine.

The alert will reset once communications are re-established.

If this condition is encountered, check the following items:

· Check the configuration of the CSM/FSM, be sure that the addresses agree.

· Check the CCN wiring for a proper connection and wiring.  Be sure that the plugs are securely seated and connections are tight.

· Check for a faulty CSM/FSM or Main Base Board.

· Check for proper power to the devices.

· If there is no CSM/FSM connected to the machine, check for noise sources on the CCN communication bus.  

P998 – Pre-Alert Loss of Refrigerant Flow - Circuit A

T998 – Loss of Refrigerant Flow - Circuit A Alert

P999 – Pre-Alert Loss of Refrigerant Flow - Circuit B

T999 – Loss of Refrigerant Flow - Circuit B Alert

Action taken by control: Circuit is shutdown

Reset Method:  Manual

With the introduction of MBB Software Version 3.1, a no refrigerant flow algorithm was added to the software logic.  At compressor start, if SST is less than 0 (F (-18 (C) and if Saturated Suction Temperature rate of change is negative (in 5 second increments) at any time between 40 and 90 seconds of runtime, the compressor will shut off.  If the circuit started above 0 (F (-18 (C), the algorithm will not start until the circuit goes below 0 (F (-18 (C) for at least 5 seconds and trending negative.  After 15 minutes, the compressor start will be attempted again.  If the pass criterion is not met, the compressor will be shutdown and the control will generate a no flow alarm.

With MBB Software Version 4.?, a Pre-alert was implemented.  The alert criterion is identical to the T998/T999 criteria for the first start attempt.  The Pre-Alert is written to the Alarm History, the appropriate Mode 26 or Mode 27 is initiated as the 15 minute time delay clock is initialized before the second circuit start attempt is made.

If this condition is encountered, check the following items:

· Check the liquid line strainer to be sure that it is not causing a restriction

· Check the liquid line service valve to be sure that it is open

· Check the liquid line solenoid valves for proper operation, if equipped.

· Check the EXV motor for proper operation.

· Check the Economizer Float/Motor for proper operation.

· Check the circuit refrigerant charge.  Low refrigerant charge conditions can lead to this alarm. 

· The Close Control Algorithm has sometimes contributed to this alarm.  If it is enabled, disable it.

· Check the Suction Pressure Transducer for accuracy.

· Check the Head Pressure Control device for proper operation.

Although this alert was created to protect the compressor, the alert can be disabled.  NO.FL, Enable No Flow Protection, (Configuration Mode, Sub-mode OPT2) is factory defaulted to “1”, Enable.  To disable the algorithm, change the value to “0”, Disable.

Resetting Alarms and Alerts

The method to reset any alarm or alert depends upon the device that generated the alarm and the type of alarm or alert, automatic or manual.  Before any alarm or alert is reset, first find the cause of the alarm or alert and correct the situation

Automatic Alarm or Alert:

An automatic alarm or alert will reset itself, without operator intervention if the condition corrects itself.

Manual Alarm or Alert:

One or more of the following methods must be used to reset the manual alarm or alert.

MBB Alarms and Alerts

To reset a MBB alarm or alert, once the condition has been corrected, from the Navigator.  Changing the RCRN Reset All Current Alarms (Alarms Mode, Sub-mode RCRN) from NO to YES.  Another method is to move the LOCAL-OFF-REMOTE switch from “LOCAL” or “REMOTE” to “OFF” for less than four (4) seconds and back to the its original position to reset the alarm or alert.

Alerts T120 Circuit A Low Saturated Suction Temperature and T121 Circuit B Low Saturated Suction Temperature have a 1 hour prohibition timer.  Once the alert is generated, 1 hour of time must elapse before the alert can be reset.

ComfortLink Compressor Protection Alarms and Alerts:

Alarms and alerts generated by the ComfortLink Compressor Protection Module (CCP) require an additional step to reset.  The alarm must be cleared from the CCP first and then the MBB.

HN67LM103 and HN67LM104 ComfortLink Compressor Protection Module:  Correct the condition that caused the alarm or alert first before resetting the alarm.

For all alarms and alerts other than MTA Header Fault – 9.5, press and hold the reset button on the CPM circuit board for a minimum of 3 seconds.  This action will clear the alarm or alert from the affected circuit without shutting down the active circuit. Then follow the instructions for resetting the MBB alarm.

For CCP alarm MTA Header Fault – 9.5, move the LOCAL-OFF-REMOTE switch to “OFF”.   Turn off the control power for a minimum of 5 seconds.  This action will remove power to the CCP.  Restore the control power and reset the MBB alert as noted above.  

Chilled Water Flow Switch

A factory provided chilled water flow switch has always been part of the ComfortLink machines.  A paddle switch was provided for this purpose since it’s introduction.  This paddle switch was required to be field installed and wired.  

The factory-supplied, vapor-proof, paddle-type flow switch is preferred over the differential pressure switches.  The factory provided flow switch is Carrier Part Number, HR81LG005 (McDonnell & Miller P/N: FS8-W).  The switch is rated for waterside pressures of 150 psig (1034 kPa), fluid and ambient temperatures down to 32 (F (0 (C) during operation.   This switch is acceptable in lower ambients, if the chilled water loop is drained and winterized.  If the application is outside of this range, a different flow switch must be field installed, Carrier Part Number, HR81LG010 (McDonnell & Miller P/N: FS7-4W) with a rating of 300 psig (2068 kPa), fluid and ambient temperatures down to -65 (F (-53 (C) must be purchased and installed.  With both switches, the conduit connection to the flow switch must be sealed.  Failure to do so will allow water to accumulate on the switch head.  The flow switch still requires that the paddle be trimmed for the appropriate size pipe.  See the manufacturer’s instructions supplied with the switch.

Beginning with Serial Numbers 1201F71080 (30GXN/GXR), 4401Q (30HXA/HXC) a factory installed and calibrated thermal dispersion flow switch HR81LG015 is supplied.  The flow switch is located in the entering water nozzle.  The flow switch is connected to the control system by a special cable with a watertight connector.  This device uses a triac output that cannot be connected directly to the Main Base Board.  As a result, a control relay, HN61KK025 is used to signal the Main Base Board that chilled water flow is detected.

When power is supplied to the device, a warm-up period is initiated.  During this period, the right-most green LED is lit and turned off as each LED to the left is successively lit until the left-most red LED is lit.  The warm-up period may take up to 30 seconds.  When some flow is detected but not enough for machine operation, a red LED at the far left will be illuminated.  With increasing flow, successive red LEDs illuminate.  When the switch determines flow is present, the amber LED illuminates indicating the output has closed.  This is not an indication of minimum flow.  Increasing flow above the amber LED output indication illuminates the first green LED.  Each successive green LED indicates greater flow.  The switch closure does not indicate minimum flow for the machine.  With one green LED lit, minor fluctuations in water flow may cause nuisance alarms.  Additional green LEDs indicate higher flow rates, and can avoid the nuisance alarms.   

[image: image9.png]Red  Amber Green

ooooooooood
e s

Flow below OUIPUl  Flow above
set point set point




Figure 4 - Chilled Water Flow Switch LED Display

The switch is calibrated to light the amber LED at a fluid velocity of 0.8 ft/sec (0.24 m/sec).  The flow rate will depend on the nozzle size.

	Schedule 40 Pipe

	Size
	O.D., in
	Wall Thickness, in 
	I.D., in
	Area, ft2
	GPM (l/s)

	4
	4.500
	0.237
	4.026
	0.09
	32 (2.02)

	5
	5.563
	0.258
	5.047
	0.14
	50 (3.15)

	6
	6.625
	0.280
	6.065
	0.20
	72 (4.54)

	8
	8.625
	0.322
	7.981
	0.35
	125 (7.89)


[image: image10.png]|« 24 Valts »]

e @rse &

F— BLu ———————<3 ) Logie < 4— Brv —]

Rermove Jumper if ORN

CWPI Installed

TE5 | cwpl | TBS

—A+ ORN —¢

®
C Ak — i@

CWPI - Chilled Water Pump Interlock MBB
FSR - Flow Switch Relay, (Extemal Relay) ~ ————





Figure 5 - Chilled Water Flow Switch Simplified Wiring

On early 30HX machines produced with the thermal dispersion flow switch, the wiring diagram was incorrect.  The diagram showed the ORN wires to FSR connected to terminals FSR-1 and FSR-8 rather than FSR-1 and FSR-3.

If the switch is removed, tighten the switch in the fitting to 10 ft-lbs (13.55 N-m).

Troubleshooting:

There is very little troubleshooting that can be done with this device.  For reference, the cable pin connection is shown below.

[image: image11.png]



Figure 6 - Chilled Water Flow Switch Cable Pin Designation

No display or output from the flow sensor:

· Check for 24 vac across pins 1 and 3.  These are small pins and caution should be used when measuring the voltage in the harness so as not to damage the connector.

· Check flow switch pin connections for damage.

Flow sensor indicates zero flow when flow is present:

· Check for air in the chilled water system.

· Check for 24 vac across pins 1 and 3.  These are small pins and caution should be used when measuring the voltage in the harness so as not to damage the connector.

· Check for fouling on the sensor switch, inhibiting the dissipation of heat from the probe.

· Consider replacing the flow switch.  It could be out of calibration, the internal heater was damaged from extreme temperatures, pressure or vibration, or mechanical damage to the tip of the device has occurred.

Flow Sensor indicates flow when no flow is present:

· Check for 24 vac across pins 1 and 3.  These are small pins and caution should be used when measuring the voltage in the harness so as not to damage the connector.  Low voltage can lead to less heat generated by the internal heater.

· Consider replacing the flow switch.  It could be out of calibration, the internal heater was damaged from extreme temperatures, pressure or vibration, or mechanical damage to the tip of the device has occurred.

Service Bulletins pertaining to this issue:

· SMB000001 – 30GX/HX Installation Review/Flow Switch

This bulletin provided a installation checklist to check for proper installation of the machines and noted the factory provided flow switch.

ComfortLink Control Boards

All connections to the Comfortlink Control Boards are made with trifurcated crimp terminals in board connectors.  Use the following tool to make the crimp connections for the board connector for all connections other than thermistors.  For thermistor connections, see Thermistors on page 140.

	Description
	Manufacturer
	Part Number

	Crimper, Micro Pin
	Packard Electric
	3157075

	
	Paladin Tools
	1631


ComfortLink Compressor Protection Module (CCP)

This device monitors the high pressure switch, running current and motor temperature for its compressor. One module is used to control two compressors.  The ComfortLink Compressor Protection Module (CCP) controls the compressor contactors, compressor oil solenoid and motor cooling solenoid.  The CPM controls the compressor contactors, compressor oil solenoid and motor cooling solenoid. 

During the initialization period of the module, the Must Trip Amp (MTA) value as determined by the Configuration Header is transmitted to the Main Base Board as a feedback voltage signal.  After the initialization period, the feedback voltage signals an alarm condition.  A feedback voltage of zero (0), signals a normal operating condition.  The feedback voltage signal can only be accessed through Network Service Tool.

The Must Trip Amp (MTA) value is configured with the use of an eight (8) position programmable header.  The header defines a binary equivalent of the MTA value for each compressor based on the following formula and the table below.  


[image: image12.wmf]2

)

50

(

-

=

Amps

Trip

Must

Value

ion

Configurat

Header


[image: image13.png]gooooooo




	Jumper Position
	1
	2
	3
	4
	5
	6
	7
	8

	Binary Equivalent
	27
	26
	25
	24
	23
	22
	21
	20

	Value
	128
	64
	32
	16
	8
	4
	2
	1


To use an example, Compressor A1 in a 30GXN174-A-540-- has a MTA setting of 522 amps.  The punchouts corresponding to 522 amps is 4, 7, and 8.  This leaves jumpers 1, 2, 3, 5, and 6 intact.  

Manipulating the formula above to find the MTA, results in the following equation:


[image: image14.wmf][

]

50

2

)

(

+

´

=

Value

ion

Configurat

Header

Amps

Trip

Must


Adding the results of the intact jumpers: ((128+64+32+8+4) + 50) * 2



[image: image15.wmf][

]

522

50

2

)

4

8

32

64

128

(

=

+

´

+

+

+

+

=

Amps

Trip

Must




[image: image16.wmf]522

=

Amps

Trip

Must


Table 1 - 30GXN Compressor MTA Settings, 115 ºF (46 ºC) Ambient

	115 ºF (46 ºC) Ambient (Model Number Position 10: “-“, “E”, “S”, or “U”)

	30GXN30GXR
	Voltage

V-Hz
	Compressor MTA Header Punch Outs
	Compressor MTA

	
	
	A1
	A2
	B1
	B2
	A1
	A2
	B1
	B2

	080
	575-60
	1,2,3,5,6
	-
	1,2,3,4,7,8
	-
	88
	-
	74
	-

	
	380-60
	1,2,4,6,8
	-
	1,2,3
	-
	134
	-
	112
	-

	
	230-60
	1,3,5,7
	-
	1,3,4,5,6
	-
	220
	-
	184
	-

	
	208/230-60
	1,4,5,6,7
	-
	1,3,4,7
	-
	244
	-
	204
	-

	
	460-60
	1,2,3,8
	-
	1,2,3,5,7
	-
	110
	-
	92
	-

	
	230-50
	1,3,8
	-
	1,3,4,6
	-
	238
	-
	200
	-

	
	380/415-50
	1,2,4
	-
	1,2,4,5,6
	-
	144
	-
	120
	-

	083
	575-60
	1,2,3,4,7,8
	-
	1,2,3,4,6,7,8
	-
	74
	-
	66
	-

	
	380-60
	1,2,4,5,6,7,8
	-
	1,2,3,6,8
	-
	114
	-
	102
	-

	
	230-60
	1,3,4,5,7
	-
	1,2,6
	-
	188
	-
	168
	-

	
	208/230-60
	1,3,4
	-
	1,3,4,5,7,8
	-
	208
	-
	186
	-

	
	460-60
	1,2,3,5,8
	-
	1,2,3,5,6,7
	-
	94
	-
	84
	-

	
	230-50
	1,3,4,8
	-
	1,2,7
	-
	206
	-
	172
	-

	
	380/415-50
	1,2,4,5,8
	-
	1,2,3,6
	-
	126
	-
	104
	-

	090

220B
	575-60
	1,2,3
	-
	1,2,3,4,7,8
	-
	112
	-
	74
	-

	
	380-60
	1,2,6
	-
	1,2,3
	-
	168
	-
	112
	-

	
	230-60
	1,5,6,7
	-
	1,3,4,5,6
	-
	276
	-
	184
	-

	
	208/230-60
	2,3,4,5,6,7,8
	-
	1,3,4,7
	-
	306
	-
	204
	-

	
	460-60
	1,2,4,7,8
	-
	1,2,3,5,7
	-
	138
	-
	92
	-

	
	230-50
	1,6,8
	-
	1,3,4,6
	-
	294
	-
	200
	-

	
	380/415-50
	1,3,4,5,6,7,8
	-
	1,2,4,5,6
	-
	178
	-
	120
	-

	093
	575-60
	1,2,3,5
	-
	1,2,3,4,6,7,8
	-
	96
	-
	66
	-

	
	380-60
	1,2,4
	-
	1,2,3,6,8
	-
	144
	-
	102
	-

	
	230-60
	1,3
	-
	1,2,6
	-
	240
	-
	168
	-

	
	208/230-60
	1,4,7,8
	-
	1,3,4,5,7,8
	-
	266
	-
	186
	-

	
	460-60
	1,2,4,5,6
	-
	1,2,3,5,6,7
	-
	120
	-
	84
	-

	
	230-50
	1,4,5,6
	-
	1,2,7
	-
	248
	-
	172
	-

	
	380/415-50
	1,2,5,6,8
	-
	1,2,3,6
	-
	150
	-
	104
	-

	106
	575-60
	1,2,4,7,8
	-
	1,2,3,4,7,8
	-
	138
	-
	74
	-

	
	380-60
	1,3,5,6,7,8
	-
	1,2,3
	-
	210
	-
	112
	-

	
	230-60
	2,3,5,6
	-
	1,3,4,5,6
	-
	344
	-
	184
	-

	
	208/230-60
	2,4,5,8
	-
	1,3,4,7
	-
	382
	-
	204
	-

	
	460-60
	1,2,7
	-
	1,2,3,5,7
	-
	172
	-
	92
	-

	
	230-50
	2,3
	-
	1,3,4,6
	-
	368
	-
	200
	-

	
	380/415-50
	1,3,5,8
	-
	1,2,4,5,6
	-
	222
	-
	120
	-

	108
	575-60
	1,2,4,5,6,8
	-
	1,2,3,4
	-
	118
	-
	80
	-

	
	380-60
	1,3,4,5,6,7,8
	-
	1,2,4,5,6
	-
	178
	-
	120
	-

	
	230-60
	2,3,4,5,7
	-
	1,3,4,6
	-
	316
	-
	200
	-

	
	208/230-60
	2,3,4,6,8
	-
	1,3,5,8
	-
	326
	-
	222
	-

	
	460-60
	1,2,5,6,7,8
	-
	1,2,3,6,7
	-
	146
	-
	100
	-

	
	230-50
	2,3,4,5,7
	-
	1,3,4
	-
	316
	-
	208
	-

	
	380/415-50
	1,3,4,5,7,8
	-
	1,2,4,5,8
	-
	186
	-
	126
	-

	114
	575-60
	1,2,4,7,8
	-
	1,2,3,5,6
	-
	138
	-
	88
	-

	
	380-60
	1,3,5,6,7,8
	-
	1,2,4,6,8
	-
	210
	-
	134
	-

	
	230-60
	2,3,5,6
	-
	1,3,5,7
	-
	344
	-
	220
	-

	
	208/230-60
	2,4,5,8
	-
	1,4,5,6,7
	-
	382
	-
	244
	-

	
	460-60
	1,2,7
	-
	1,2,3,8
	-
	172
	-
	110
	-

	115

240B
	230-50
	2,4,8
	-
	1,3,5,8
	-
	398
	-
	222
	-

	
	380/415-50
	1,3
	-
	1,2,4,6,8
	-
	240
	-
	134
	-

	118
	575-60
	1,2,4,5,6,8
	-
	1,2,3,5,8
	-
	118
	-
	94
	-

	
	380-60
	1,3,4,5,6,7,8
	-
	1,2,4,8
	-
	178
	-
	142
	-

	
	230-60
	2,3,4,5,7
	-
	1,3,7
	-
	316
	-
	236
	-

	
	208/230-60
	2,3,4,6,8
	-
	1,4,6,7
	-
	326
	-
	260
	-

	
	460-60
	1,2,5,6,7,8
	-
	1,2,4,5,6,8
	-
	146
	-
	118
	-

	
	230-50
	2,3,4,5,7
	-
	1,4,5,7,8
	-
	316
	-
	250
	-

	
	380/415-50
	1,3,4,5,7,8
	-
	1,2,5,6
	-
	186
	-
	152
	-

	125

220A

240A
	575-60
	1,2,5,7,8
	-
	1,2,3,7,8
	-
	154
	-
	106
	-

	
	380-60
	1,3,7,8
	-
	1,2,6,7,8
	-
	234
	-
	162
	-

	
	230-60
	2,4,6,7
	-
	1,4,6
	-
	388
	-
	264
	-

	
	208/230-60
	2,7
	-
	1,6,8
	-
	428
	-
	294
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,2,4,6,7
	-
	194
	-
	132
	-

	
	230-50
	2,4,8
	-
	1,4
	-
	398
	-
	272
	-

	
	380/415-50
	1,3
	-
	1,2,6,7
	-
	240
	-
	164
	-

	128
	575-60
	1,2,4,6
	-
	1,2,3,5,8
	-
	136
	-
	94
	-

	
	380-60
	1,3,4,7
	-
	1,2,4,8
	-
	204
	-
	142
	-

	
	230-60
	2,3,5,6,7,8
	-
	1,3,7
	-
	338
	-
	236
	-

	
	208/230-60
	2,4,5,6,8
	-
	1,4,6,7
	-
	374
	-
	260
	-

	
	460-60
	1,2,7,8
	-
	1,2,4,5,6,8
	-
	170
	-
	118
	-

	
	230-50
	2,3,6,7,8
	-
	1,4,5,7,8
	-
	354
	-
	250
	-

	
	380/415-50
	1,3,5,6,8
	-
	1,2,5,6
	-
	214
	-
	152
	-

	138

283B

303B

373B
	575-60
	1,2,4,6
	-
	1,2,4,5,6,8
	-
	136
	-
	118
	-

	
	380-60
	1,3,4,7
	-
	1,3,4,5,6,7,8
	-
	204
	-
	178
	-

	
	230-60
	2,3,5,6,7,8
	-
	2,3,4,5,7
	-
	338
	-
	316
	-

	
	208/230-60
	2,4,5,6,8
	-
	2,3,4,6,8
	-
	374
	-
	326
	-

	
	460-60
	1,2,7,8
	-
	1,2,5,6,7,8
	-
	170
	-
	146
	-

	
	230-50
	2,3,6,7,8
	-
	2,3,4,5,7
	-
	354
	-
	316
	-

	
	380/415-50
	1,3,5,6,8
	-
	1,3,4,5,7,8
	-
	214
	-
	186
	-

	153

283A

328B

393B

418B
	575-60
	1,2,7,8
	-
	1,2,4,5,6,8
	-
	170
	-
	118
	-

	
	380-60
	1,4,6,7,8
	-
	1,3,4,5,6,7,8
	-
	258
	-
	178
	-

	
	230-60
	2,7
	-
	2,3,4,5,7
	-
	428
	-
	316
	-

	
	208/230-60
	3,5,6
	-
	2,3,4,6,8
	-
	472
	-
	326
	-

	
	460-60
	1,3,5,6,8
	-
	1,2,5,6,7,8
	-
	214
	-
	146
	-

	
	230-50
	3,4,5,6
	-
	2,3,4,5,7
	-
	440
	-
	316
	-

	
	380/415-50
	1,4,7,8
	-
	1,3,4,5,7,8
	-
	266
	-
	186
	-

	163

303A
	575-60
	1,2,7,8
	-
	1,2,4,6
	-
	170
	-
	136
	-

	
	380-60
	1,4,6,7,8
	-
	1,3,4,7
	-
	258
	-
	204
	-

	
	230-60
	2,7
	-
	2,3,5,6,7,8
	-
	428
	-
	338
	-

	
	208/230-60
	3,5,6
	-
	2,4,5,6,8
	-
	472
	-
	374
	-

	
	460-60
	1,3,5,6,8
	-
	1,2,7,8
	-
	214
	-
	170
	-

	
	230-50
	3,4,5,6
	-
	2,3,6,7,8
	-
	440
	-
	354
	-

	
	380/415-50
	1,4,7,8
	-
	1,3,5,6,8
	-
	266
	-
	214
	-

	178

328A

353A/B
	575-60
	1,2,7,8
	-
	1,2,7,8
	-
	170
	-
	170
	-

	
	380-60
	1,4,6,7,8
	-
	1,4,6,7,8
	-
	258
	-
	258
	-

	
	230-60
	2,7
	-
	2,7
	-
	428
	-
	428
	-

	
	208/230-60
	3,5,6
	-
	3,5,6
	-
	472
	-
	472
	-

	
	460-60
	1,3,5,6,8
	-
	1,3,5,6,8
	-
	214
	-
	214
	-

	
	230-50
	3,4,5,6
	-
	3,4,5,6
	-
	440
	-
	440
	-

	
	380/415-50
	1,4,7,8
	-
	1,4,7,8
	-
	266
	-
	266
	-

	208
	575-60
	1,2,4,6
	1,2,4,6
	1,2,4,5,6,8
	-
	136
	136
	118
	-

	
	380-60
	1,3,4,7
	1,3,4,7
	1,3,4,5,6,7,8
	-
	204
	204
	178
	-

	
	230-60
	2,3,5,6,7,8
	2,3,5,6,7,8
	2,3,4,5,7
	-
	338
	338
	316
	-

	
	208/230-60
	2,4,5,6,8
	2,4,5,6,8
	2,3,4,6,8
	-
	374
	374
	326
	-

	
	460-60
	1,2,7,8
	1,2,7,8
	1,2,5,6,7,8
	-
	170
	170
	146
	-

	
	230-50
	2,3,6,7,8
	2,3,6,7,8
	2,3,4,5,7
	-
	354
	354
	316
	-

	
	380/415-50
	1,3,5,6,8
	1,3,5,6,8
	1,3,4,5,7,8
	-
	214
	214
	186
	-

	228

453A/B

478B
	575-60
	1,2,7,8
	1,2,4,6
	1,2,4,5,6,8
	-
	170
	136
	118
	-

	
	380-60
	1,4,6,7,8
	1,3,4,7
	1,3,4,5,6,7,8
	-
	258
	204
	178
	-

	
	230-60
	2,7
	2,3,5,6,7,8
	2,3,4,5,7
	-
	428
	338
	316
	-

	
	208/230-60
	3,5,6
	2,4,5,6,8
	2,3,4,6,8
	-
	472
	374
	326
	-

	
	460-60
	1,3,5,6,8
	1,2,7,8
	1,2,5,6,7,8
	-
	214
	170
	146
	-

	
	230-50
	3,4,5,6
	2,3,6,7,8
	2,3,4,5,7
	-
	440
	354
	316
	-

	
	380/415-50
	1,4,7,8
	1,3,5,6,8
	1,3,4,5,7,8
	-
	266
	214
	186
	-

	253

373A

393A

478A

503A/B
	575-60
	1,2,7,8
	1,2,7,8
	1,2,4,6
	-
	170
	170
	136
	-

	
	380-60
	1,4,6,7,8
	1,4,6,7,8
	1,3,4,7
	-
	258
	258
	204
	-

	
	230-60
	2,7
	2,7
	2,3,5,6,7,8
	-
	428
	428
	338
	-

	
	208/230-60
	3,5,6
	3,5,6
	2,4,5,6,8
	-
	472
	472
	374
	-

	
	460-60
	1,3,5,6,8
	1,3,5,6,8
	1,2,7,8
	-
	214
	214
	170
	-

	
	230-50
	3,4,5,6
	3,4,5,6
	2,3,6,7,8
	-
	440
	440
	354
	-

	
	380/415-50
	1,4,7,8
	1,4,7,8
	1,3,5,6,8
	-
	266
	266
	214
	-

	268

418A

528A/B
	575-60
	1,2,7,8
	1,2,7,8
	1,2,7,8
	-
	170
	170
	170
	-

	
	380-60
	1,4,6,7,8
	1,4,6,7,8
	1,4,6,7,8
	-
	258
	258
	258
	-

	
	230-60
	2,7
	2,7
	2,7
	-
	428
	428
	428
	-

	
	208/230-60
	3,5,6
	3,5,6
	3,5,6
	-
	472
	472
	472
	-

	
	460-60
	1,3,5,6,8
	1,3,5,6,8
	1,3,5,6,8
	-
	214
	214
	214
	-

	
	230-50
	3,4,5,6
	3,4,5,6
	3,4,5,6
	-
	440
	440
	440
	-

	
	380/415-50
	1,4,7,8
	1,4,7,8
	1,4,7,8
	-
	266
	266
	266
	-


Table 2 - 30GXN Compressor MTA Settings, 125 ºF (51.6 ºC) Ambient

	125 ºF (51.6 ºC) Ambient (Model Number Position 10: “A“, “F”, “T”, or “V”)

	30GXN30GXR
	Voltage

V-Hz
	Compressor MTA Header Punch Outs
	Compressor MTA

	
	
	A1
	A2
	B1
	B2
	A1
	A2
	B1
	B2

	080
	575-60
	1,2,3,5,8
	-
	1,2,3,4,8
	-
	94
	-
	78
	-

	
	380-60
	1,2,4,8
	-
	1,2,4,5,6,8
	-
	142
	-
	118
	-

	
	230-60
	1,3,6
	-
	1,3,4,5
	-
	232
	-
	192
	-

	
	208/230-60
	1,4,6,7,8
	-
	1,3,5,6,8
	-
	258
	-
	214
	-

	
	460-60
	1,2,4,5,6,7
	-
	1,2,3,5
	-
	116
	-
	96
	-

	
	230-50
	1,4,5,6
	-
	1,3,4,8
	-
	248
	-
	206
	-

	
	380/415-50
	1,2,5,6,8
	-
	1,2,4,5,7
	-
	150
	-
	124
	-

	083
	575-60
	1,2,3,5,6,7
	-
	1,2,3,4,6,8
	-
	84
	-
	70
	-

	
	380-60
	1,2,4,5
	-
	1,2,3,7
	-
	128
	-
	108
	-

	
	230-60
	1,3,5,6,7
	-
	1,2
	-
	212
	-
	176
	-

	
	208/230-60
	1,3,7,8
	-
	1,3,4,6,7
	-
	234
	-
	196
	-

	
	460-60
	1,2,3,7,8
	-
	1,2,3,5,6
	-
	106
	-
	88
	-

	
	230-50
	1,3,5
	-
	1,3,4,5,6,8
	-
	224
	-
	182
	-

	
	380/415-50
	1,2,4,6,8
	-
	1,2,3,8
	-
	134
	-
	110
	-

	090

220B
	575-60
	1,2,4,5,6,7
	-
	1,2,3,4,8
	-
	116
	-
	78
	-

	
	380-60
	1,2
	-
	1,2,4,5,6,8
	-
	176
	-
	118
	-

	
	230-60
	1,5
	-
	1,3,4,5
	-
	288
	-
	192
	-

	
	208/230-60
	2,3,4,5,7,8
	-
	1,3,5,6,8
	-
	314
	-
	214
	-

	
	460-60
	1,2,4
	-
	1,2,3,5
	-
	144
	-
	96
	-

	
	230-50
	2,3,4,5,6,7
	-
	1,3,4,8
	-
	308
	-
	206
	-

	
	380/415-50
	1,3,4,5,7,8
	-
	1,2,4,5,7
	-
	186
	-
	124
	-

	093
	575-60
	1,2,3,6
	-
	1,2,3,4,6,8
	-
	104
	-
	70
	-

	
	380-60
	1,2,5,8
	-
	1,2,3,7
	-
	158
	-
	108
	-

	
	230-60
	1,4,6,7
	-
	1,2
	-
	260
	-
	176
	-

	
	208/230-60
	1,5
	-
	1,3,4,6,7
	-
	288
	-
	196
	-

	
	460-60
	1,2,4,6,7,8
	-
	1,2,3,5,6
	-
	130
	-
	88
	-

	
	230-50
	1,4,7
	-
	1,3,4,5,6,8
	-
	268
	-
	182
	-

	
	380/415-50
	1,2,6,7,8
	-
	1,2,3,8
	-
	162
	-
	110
	-

	106
	575-60
	1,2,4,7
	-
	1,2,3,4,8
	-
	140
	-
	78
	-

	
	380-60
	1,3,5,6,7
	-
	1,2,4,5,6,8
	-
	212
	-
	118
	-

	
	230-60
	2,3,5,7
	-
	1,3,4,5
	-
	348
	-
	192
	-

	
	208/230-60
	2,4,5
	-
	1,3,5,6,8
	-
	384
	-
	214
	-

	
	460-60
	1,2,8
	-
	1,2,3,5
	-
	174
	-
	96
	-

	
	230-50
	2,4,5,6,7
	-
	1,3,4,8
	-
	372
	-
	206
	-

	
	380/415-50
	1,3,5
	-
	1,2,4,5,7
	-
	224
	-
	124
	-

	108
	575-60
	1,2,4,5
	-
	1,2,3,5,6
	-
	128
	-
	88
	-

	
	380-60
	1,3,4,6,7,8
	-
	1,2,4,6,7
	-
	194
	-
	132
	-

	
	230-60
	2,3,4,5
	-
	1,3,5,7
	-
	320
	-
	220
	-

	
	208/230-60
	2,3,6,7,8
	-
	1,4,5,6,7
	-
	354
	-
	244
	-

	
	460-60
	1,2,5
	-
	1,2,3,8
	-
	160
	-
	110
	-

	
	230-50
	2,3,4,6,7
	-
	1,3,6,7
	-
	324
	-
	228
	-

	
	380/415-50
	1,3,4,7,8
	-
	1,2,4,7,8
	-
	202
	-
	138
	-

	114
	575-60
	1,2,4,7
	-
	1,2,3,5,8
	-
	140
	-
	94
	-

	
	380-60
	1,3,5,6,7
	-
	1,2,4,8
	-
	212
	-
	142
	-

	
	230-60
	2,3,5,7
	-
	1,3,6
	-
	348
	-
	232
	-

	
	208/230-60
	2,4,5
	-
	1,4,6,7,8
	-
	384
	-
	258
	-

	
	460-60
	1,2,8
	-
	1,2,4,5,6,7
	-
	174
	-
	116
	-

	115

240B
	230-50
	2,4,8
	-
	1,3,6,7
	-
	398
	-
	228
	-

	
	380/415-50
	1,3
	-
	1,2,4,7,8
	-
	240
	-
	138
	-

	118
	575-60
	1,2,4,5
	-
	1,2,3,6
	-
	128
	-
	104
	-

	
	380-60
	1,3,4,6,7,8
	-
	1,2,5,8
	-
	194
	-
	158
	-

	
	230-60
	2,3,4,5
	-
	1,4,6,8
	-
	320
	-
	262
	-

	
	208/230-60
	2,3,6,7,8
	-
	1,5
	-
	354
	-
	288
	-

	
	460-60
	1,2,5
	-
	1,2,4,6,7,8
	-
	160
	-
	130
	-

	
	230-50
	2,3,4,6,7
	-
	1,5,6,8
	-
	324
	-
	278
	-

	
	380/415-50
	1,3,4,7,8
	-
	1,2,6
	-
	202
	-
	168
	-

	125

220A

240A
	575-60
	1,2,5,7,8
	-
	1,2,3,7
	-
	154
	-
	108
	-

	
	380-60
	1,3,7,8
	-
	1,2,6,7
	-
	234
	-
	164
	-

	
	230-60
	2,4,6,7
	-
	1,4,7
	-
	388
	-
	268
	-

	
	208/230-60
	2,7
	-
	1,7,8
	-
	428
	-
	298
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,2,4,6,8
	-
	194
	-
	134
	-

	
	230-50
	2,4,8
	-
	1,5,6,7
	-
	398
	-
	276
	-

	
	380/415-50
	1,3
	-
	1,2,6,8
	-
	240
	-
	166
	-

	128
	575-60
	1,2,5,7,8
	-
	1,2,3,6
	-
	154
	-
	104
	-

	
	380-60
	1,3,7,8
	-
	1,2,5,8
	-
	234
	-
	158
	-

	
	230-60
	2,4,6,7
	-
	1,4,6,8
	-
	388
	-
	262
	-

	
	208/230-60
	2,7
	-
	1,5
	-
	428
	-
	288
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,2,4,6,7,8
	-
	194
	-
	130
	-

	
	230-50
	2,4,8
	-
	1,5,6,8
	-
	398
	-
	278
	-

	
	380/415-50
	1,3
	-
	1,2,6
	-
	240
	-
	168
	-

	135

275A/B

300B 365B

390B

395B
	575-60
	1,2,5,7,8
	-
	1,2,4,5
	-
	154
	-
	128
	-

	
	380-60
	1,3,7,8
	-
	1,3,4,6,7,8
	-
	234
	-
	194
	-

	
	230-60
	2,4,6,7
	-
	2,3,4,5
	-
	388
	-
	320
	-

	
	208/230-60
	2,7
	-
	2,3,6,7,8
	-
	428
	-
	354
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,2,5
	-
	194
	-
	160
	-

	
	230-50
	2,4,8
	-
	2,3,4,6,7
	-
	398
	-
	324
	-

	
	380/415-50
	1,3
	-
	1,3,4,7,8
	-
	240
	-
	202
	-

	138

283B

303B

373B
	575-60
	1,2,5,7,8
	-
	1,2,4,5
	-
	154
	-
	128
	-

	
	380-60
	1,3,7,8
	-
	1,3,4,6,7,8
	-
	234
	-
	194
	-

	
	230-60
	2,4,6,7
	-
	2,3,4,5
	-
	388
	-
	320
	-

	
	208/230-60
	2,7
	-
	2,3,6,7,8
	-
	428
	-
	354
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,2,5
	-
	194
	-
	160
	-

	
	230-50
	2,4,8
	-
	2,3,4,6,7
	-
	398
	-
	324
	-

	
	380/415-50
	1,3
	-
	1,3,4,7,8
	-
	240
	-
	202
	-

	150 370B
	575-60
	1,2,4,5
	-
	1,3,4,5,7
	-
	128
	-
	188
	-

	
	380-60
	1,3,4,6,7,8
	-
	1,5,8
	-
	194
	-
	286
	-

	
	230-60
	2,3,4,5
	-
	3,5,6
	-
	320
	-
	472
	-

	
	208/230-60
	2,3,6,7,8
	-
	4,7,8
	-
	354
	-
	522
	-

	
	460-60
	1,2,5
	-
	1,3,7
	-
	160
	-
	236
	-

	
	230-50
	2,3,5,7
	-
	2,5,6,7
	-
	348
	-
	404
	-

	
	380/415-50
	1,3,5,6,7,8
	-
	1,4,5,6,8
	-
	210
	-
	246
	-

	153

283A

328B

393B

418B
	575-60
	1,3,4,5,7
	-
	1,2,4,5
	-
	188
	-
	128
	-

	
	380-60
	1,5,8
	-
	1,3,4,6,7,8
	-
	286
	-
	194
	-

	
	230-60
	3,5,6
	-
	2,3,4,5
	-
	472
	-
	320
	-

	
	208/230-60
	4,7,8
	-
	2,3,6,7,8
	-
	522
	-
	354
	-

	
	460-60
	1,3,7
	-
	1,2,5
	-
	236
	-
	160
	-

	
	230-50
	3,6,7
	-
	2,3,5,7
	-
	484
	-
	348
	-

	
	380/415-50
	1,6,8
	-
	1,3,5,6,7,8
	-
	294
	-
	210
	-

	160 300A 320A/B 415B
	575-60
	1,2,5,7,8
	-
	1,3,4,5,7
	-
	154
	-
	188
	-

	
	380-60
	1,3,7,8
	-
	1,5,8
	-
	234
	-
	286
	-

	
	230-60
	2,4,6,7
	-
	3,5,6
	-
	388
	-
	472
	-

	
	208/230-60
	2,7
	-
	4,7,8
	-
	428
	-
	522
	-

	
	460-60
	1,3,4,6,7,8
	-
	1,3,7
	-
	194
	-
	236
	-

	
	230-50
	2,4,8
	-
	3,6
	-
	398
	-
	488
	-

	
	380/415-50
	1,3
	-
	1,6,8
	-
	240
	-
	294
	-

	163

303A
	575-60
	1,3,4,5,7
	-
	1,2,5,7,8
	-
	188
	-
	154
	-

	
	380-60
	1,5,8
	-
	1,3,7,8
	-
	286
	-
	234
	-

	
	230-60
	3,5,6
	-
	2,4,6,7
	-
	472
	-
	388
	-

	
	208/230-60
	4,7,8
	-
	2,7
	-
	522
	-
	428
	-

	
	460-60
	1,3,7
	-
	1,3,4,6,7,8
	-
	236
	-
	194
	-

	
	230-50
	3,6,7
	-
	2,4,8
	-
	484
	-
	398
	-

	
	380/415-50
	1,6,8
	-
	1,3
	-
	294
	-
	240
	-

	174
	575-60
	1,3,4,5,7
	-
	1,3,4,5,7
	-
	188
	-
	188
	-

	
	380-60
	1,5,8
	-
	1,5,8
	-
	286
	-
	286
	-

	
	230-60
	3,5,6
	-
	3,5,6
	-
	472
	-
	472
	-

	
	208/230-60
	4,7,8
	-
	4,7,8
	-
	522
	-
	522
	-

	
	460-60
	1,3,7
	-
	1,3,7
	-
	236
	-
	236
	-

	175 345A/B
	230-50
	3,6
	-
	3,6
	-
	488
	-
	488
	-

	
	380/415-50
	1,6,8
	-
	1,6,8
	-
	294
	-
	294
	-

	178

328A

353A

353B
	575-60
	1,3,4,5,7
	-
	1,3,4,5,7
	-
	188
	-
	188
	-

	
	380-60
	1,5,8
	-
	1,5,8
	-
	286
	-
	286
	-

	
	230-60
	3,5,6
	-
	3,5,6
	-
	472
	-
	472
	-

	
	208/230-60
	4,7,8
	-
	4,7,8
	-
	522
	-
	522
	-

	
	460-60
	1,3,7
	-
	1,3,7
	-
	236
	-
	236
	-

	
	230-50
	3,6,7
	-
	3,6,7
	-
	484
	-
	484
	-

	
	380/415-50
	1,6,8
	-
	1,6,8
	-
	294
	-
	294
	-

	204
	575-60
	1,3,4,5,7
	1,2,3,5,7,8
	1,2,5,7,8
	-
	188
	90
	154
	-

	
	380-60
	1,5,8
	1,2,4,6
	1,3,7,8
	-
	286
	136
	234
	-

	
	230-60
	3,5,6
	1,3,6,7
	2,4,6,7
	-
	472
	228
	388
	-

	
	208/230-60
	4,7,8
	1,4,5,7
	2,7
	-
	522
	252
	428
	-

	
	460-60
	1,3,7
	1,2,4,5,6,7,8
	1,3,4,6,7,8
	-
	236
	114
	194
	-

	205 410B
	230-50
	2,4,8
	1,3,6,7
	3,6
	-
	398
	228
	488
	-

	
	380/415-50
	1,3
	1,2,4,7,8
	1,6,8
	-
	240
	138
	294
	-

	208
	575-60
	1,2,5,7,8
	1,2,5,7,8
	1,2,4,5
	-
	154
	154
	128
	-

	
	380-60
	1,3,7,8
	1,3,7,8
	1,3,4,6,7,8
	-
	234
	234
	194
	-

	
	230-60
	2,4,6,7
	2,4,6,7
	2,3,4,5
	-
	388
	388
	320
	-

	
	208/230-60
	2,7
	2,7
	2,3,6,7,8
	-
	428
	428
	354
	-

	
	460-60
	1,3,4,6,7,8
	1,3,4,6,7,8
	1,2,5
	-
	194
	194
	160
	-

	
	230-50
	2,4,8
	2,4,8
	2,3,5,7
	-
	398
	398
	348
	-

	
	380/415-50
	1,3
	1,3
	1,3,5,6,7,8
	-
	240
	240
	210
	-

	225 370A 410A 440A/B 450A/B 470B 475B
	575-60
	1,3,4,5,7
	1,2,3,7
	1,3,4,5,7
	-
	188
	108
	188
	-

	
	380-60
	1,5,8
	1,2,6,7
	1,5,8
	-
	286
	164
	286
	-

	
	230-60
	3,5,6
	1,4,7
	3,5,6
	-
	472
	268
	472
	-

	
	208/230-60
	4,7,8
	1,7,8
	4,7,8
	-
	522
	298
	522
	-

	
	460-60
	1,3,7
	1,2,4,6,8
	1,3,7
	-
	236
	134
	236
	-

	
	230-50
	3,6
	1,5,6,7
	3,6
	-
	488
	276
	488
	-

	
	380/415-50
	1,6,8
	1,2,6,8
	1,6,8
	-
	294
	166
	294
	-

	228

453A/B

478B
	575-60
	1,3,4,5,7
	1,2,5,7,8
	1,2,4,5
	-
	188
	154
	128
	-

	
	380-60
	1,5,8
	1,3,7,8
	1,3,4,6,7,8
	-
	286
	234
	194
	-

	
	230-60
	3,5,6
	2,4,6,7
	2,3,4,5
	-
	472
	388
	320
	-

	
	208/230-60
	4,7,8
	2,7
	2,3,6,7,8
	-
	522
	428
	354
	-

	
	460-60
	1,3,7
	1,3,4,6,7,8
	1,2,5
	-
	236
	194
	160
	-

	
	230-50
	3,6,7
	2,4,8
	2,3,5,7
	-
	484
	398
	348
	-

	
	380/415-50
	1,6,8
	1,3
	1,3,5,6,7,8
	-
	294
	240
	210
	-

	249 475A 500A/B
	575-60
	1,3,4,5,7
	1,3,4,5,7
	1,2,5,7,8
	-
	188
	188
	154
	-

	
	380-60
	1,5,8
	1,5,8
	1,3,7,8
	-
	286
	286
	234
	-

	
	230-60
	3,5,6
	3,5,6
	2,4,6,7
	-
	472
	472
	388
	-

	
	208/230-60
	4,7,8
	4,7,8
	2,7
	-
	522
	522
	428
	-

	
	460-60
	1,3,7
	1,3,7
	1,3,4,6,7,8
	-
	236
	236
	194
	-

	250 365A 470A 495A/B
	230-50
	3,6
	2,4,8
	3,6
	-
	488
	398
	488
	-

	
	380/415-50
	1,6,8
	1,3
	1,6,8
	-
	294
	240
	294
	-

	253

373A

393A

478A

503A

503B
	575-60
	1,3,4,5,7
	1,3,4,5,7
	1,2,5,7,8
	-
	188
	188
	154
	-

	
	380-60
	1,5,8
	1,5,8
	1,3,7,8
	-
	286
	286
	234
	-

	
	230-60
	3,5,6
	3,5,6
	2,4,6,7
	-
	472
	472
	388
	-

	
	208/230-60
	4,7,8
	4,7,8
	2,7
	-
	522
	522
	428
	-

	
	460-60
	1,3,7
	1,3,7
	1,3,4,6,7,8
	-
	236
	236
	194
	-

	
	230-50
	3,6,7
	3,6,7
	2,4,8
	-
	484
	484
	398
	-

	
	380/415-50
	1,6,8
	1,6,8
	1,3
	-
	294
	294
	240
	-

	264 390A 395B 415A 520A/B 525A/B
	575-60
	1,3,4,5,7
	1,3,4,5,7
	1,3,4,5,7
	-
	188
	188
	188
	-

	
	380-60
	1,5,8
	1,5,8
	1,5,8
	-
	286
	286
	286
	-

	
	230-60
	3,5,6
	3,5,6
	3,5,6
	-
	472
	472
	472
	-

	
	208/230-60
	4,7,8
	4,7,8
	4,7,8
	-
	522
	522
	522
	-

	
	460-60
	1,3,7
	1,3,7
	1,3,7
	-
	236
	236
	236
	-

	
	230-50
	3,6
	3,6
	3,6
	-
	488
	488
	488
	-

	
	380/415-50
	1,6,8
	1,6,8
	1,6,8
	-
	294
	294
	294
	-

	268

418A

528A

528B
	575-60
	1,3,4,5,7
	1,3,4,5,7
	1,3,4,5,7
	-
	188
	188
	188
	-

	
	380-60
	1,5,8
	1,5,8
	1,5,8
	-
	286
	286
	286
	-

	
	230-60
	3,5,6
	3,5,6
	3,5,6
	-
	472
	472
	472
	-

	
	208/230-60
	4,7,8
	4,7,8
	4,7,8
	-
	522
	522
	522
	-

	
	460-60
	1,3,7
	1,3,7
	1,3,7
	-
	236
	236
	236
	-

	
	230-50
	3,6,7
	3,6,7
	3,6,7
	-
	484
	484
	484
	-

	
	380/415-50
	1,6,8
	1,6,8
	1,6,8
	-
	294
	294
	294
	-

	281
	575-60
	1,3,4,5,7
	1,2,3,7
	1,3,4,5,7
	1,2,3,7
	188
	108
	188
	108

	
	380-60
	1,5,8
	1,2,6,7
	1,5,8
	1,2,6,7
	286
	164
	286
	164

	
	460-60
	1,3,7
	1,2,4,6,8
	1,3,7
	1,2,4,6,8
	236
	134
	236
	134

	
	380/415-50
	1,6,8
	1,2,6,8
	1,6,8
	1,2,6,8
	294
	166
	294
	166

	301
	575-60
	1,3,4,5,7
	1,2,4,5
	1,3,4,5,7
	1,2,4,5
	188
	128
	188
	128

	
	380-60
	1,5,8
	1,3,4,6,7,8
	1,5,8
	1,3,4,6,7,8
	286
	194
	286
	194

	
	460-60
	1,3,7
	1,2,5
	1,3,7
	1,2,5
	236
	160
	236
	160

	
	380/415-50
	1,6,8
	1,3,4,7,8
	1,6,8
	1,3,4,7,8
	294
	202
	294
	202

	325
	575-60
	1,3,4,5,7
	1,2,5,7,8
	1,3,4,5,7
	1,2,5,7,8
	188
	154
	188
	154

	
	380-60
	1,5,8
	1,3,7,8
	1,5,8
	1,3,7,8
	286
	234
	286
	234

	
	460-60
	1,3,7
	1,3,4,6,7,8
	1,3,7
	1,3,4,6,7,8
	236
	194
	236
	194

	
	380/415-50
	1,6,8
	1,3
	1,6,8
	1,3
	294
	240
	294
	240

	350
	575-60
	1,3,4,5,7
	1,3,4,5,7
	1,3,4,5,7
	1,3,4,5,7
	188
	188
	188
	188

	
	380-60
	1,5,8
	1,5,8
	1,5,8
	1,5,8
	286
	286
	286
	286

	
	460-60
	1,3,7
	1,3,7
	1,3,7
	1,3,7
	236
	236
	236
	236

	
	380/415-50
	1,6,8
	1,6,8
	1,6,8
	1,6,8
	294
	294
	294
	294


There are two modules, a full current (HN67LM103) and a ½ current (HN67LM104) module.  The full current module is used if the two compressors have a Must Trip Amps (MTA) rating less than 314 amps.  If either compressor’s MTA is above 314 amps, the ½ current module is used.

With the implementation of the new current transformer module, all compressors regardless of MTA value use the full current ComfortLink Compressor Protection module, HN67LM103.

A current transformer module, 30GX502786 is used to sense the current phase rotation and over current conditions for each compressor.  The device consists of 3 toroids, with a resistance of 64.3-70.4 (.  A 0-15 vac signal is sent from this module, corresponding to a 0 to 900 amp current value.

Beginning with Serial Number 2401F (30GXN,R) and 1102Q (30HX), a new current transformer module was used for machines with compressor MTA’s greater than 314 amps.  The current transformer module, 30GX504711 is used to sense the current phase rotation and over current conditions for each compressor.  The device consists of 3 toroids, with a resistance of 38.5-42 (.  A 0-15 vac signal is sent from this module, corresponding to a 0 to 900 amp current value.

Both current transformer modules have three (3) toroids in a molded plastic case.  A four (4) wire board connector, one for each toroid and a common, is used to connect the toroids to the CCP. 

DIP Switches 3 and 4 address each module.  The addresses are as follows:

	Compressor Protection Module
	DIP Switch 1
	DIP Switch 3
	DIP Switch 4

	CPM1
	L
	0
	0

	CPM2
	L
	1
	1


With the introduction of ComfortLink to the 30GX/HX products, the old CPM was changed to be able to communicate on the LEN bus.  The new CPMs were renamed to ComfortLink Compressor Protection (CCP) to note the change. The software label located on the EPROM indicates the software installed.  The software is “100233-1R3 V1 REV x” where “x” is the revision listed below. 

Revision 22E 
This EPROM is the original production release of the CCP module.

Revision 23 
This EPROM is the original production release of the CCP module, but since the Local Equipment Network (LEN) could not handle the letter suffixes, the EPROM revision was changed to 23.

The new modules, HN67LM103 (full current) and HN67LM104 (½ current) modules are backward compatible with the HN67LM101 (full current) and 30GX503191 (½ current) modules.  In order for a CCP to be used on a non-ComfortLink machine, DIP Switch #1 must be set to “S”.

The following table describes the CPM usage and lead configuration.

	Serial Number Reference
	30GXN/GXR:  3400F-2301F

30HXA/HXC:  3400F-0702Q

	Unit
	Compressor Protection Module
	Compressor Lead Configuration

(See notes following table)

	
	CPM1
	CPM2
	A1
	A2
	B1
	B2

	30GXN,R080---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---4
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---5
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---8
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R080---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R090---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R090---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R090---4
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R090---5
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R090---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R090---8
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R090---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R106---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R106---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R106---4
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R106---5
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R106---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R106---8
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R106---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R114---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R114---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R114---4
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R114---5
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R114---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R115---8
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R115---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R125---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R125---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R125---4
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R125---5
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R125---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R125---8
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R125---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R135---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R135---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R135---4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R135---5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R135---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R135---8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R135---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R150---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R150---2
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R150---4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R150---5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R150---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R150---8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R150---9
	HN67LM103
	-
	A
	-
	B
	-

	30GXN,R160---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R160---2
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R160---4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R160---5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R160---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R160---8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R160---9
	HN67LM103
	-
	A
	-
	B
	-

	30GXN,R174---1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R174---2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R174---4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R174---5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R174---6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R175---8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R175---9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R204---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R204---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R204---4
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R204---5
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R204---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R205---8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R205---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R220A--8
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R220A--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R220B--8
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R220B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R225---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R225---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R225---4
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R225---5
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R225---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R225---8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R225---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R240A--8
	HN67LM104
	-
	C
	-
	B
	-

	30GXN,R240A--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R240B--8
	HN67LM104
	-
	C
	-
	A
	-

	30GXN,R240B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R249---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R249---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R249---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R249---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R249---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R250---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R250---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R264---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R264---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R264---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R264---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R264---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R264---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R264---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R275A--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R275A--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R275B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R275B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R281---1
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R281---2
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R281---6
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R281---9
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R300A--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R300A--9
	HN67LM103
	-
	A
	-
	B
	-

	30GXN,R301---1
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R301---2
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R301---6
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R301---9
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R300B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R300B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R320A--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R320A--9
	HN67LM103
	-
	A
	-
	B
	-

	30GXN,R320B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R320B--9
	HN67LM103
	-
	A
	-
	B
	-

	30GXN,R325---1
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R325---2
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R325---6
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R325---9
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R345A--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R345A--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R345B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R345B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R350---1
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R350---2
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R350---6
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R350---9
	HN67LM103
	HN67LM103
	A
	A
	A
	A

	30GXN,R365A--8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R365A--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R365B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R365B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R370A--1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R370A--2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R370A--4
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R370A--5
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R370A--6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R370B--1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R370B--2
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R370B--4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R370B--5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R370B--6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R390A--1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R390A--2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R390A--4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R390A--5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R390A--6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R390B--1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R390B--2
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R390B--4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R390B--5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R390B--6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R395A--8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R395A--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R395B--8
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R395B--9
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R410A--8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R410A--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R410B--8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R410B--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R415A--1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R415A--2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R415A--4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R415A--5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30GXN,R415A--6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R415B--1
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R415B--2
	HN67LM103
	-
	B
	-
	A
	-

	30GXN,R415B--4
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R415B--5
	HN67LM104
	-
	C
	-
	C
	-

	30GXN,R415B--6
	HN67LM103
	-
	A
	-
	A
	-

	30GXN,R440A--8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R440A--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R440B--8
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R440B--9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450A--1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450A--2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450A--4
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R450A--5
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R450A--6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450B--1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450B--2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30GXN,R450B--4
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R450B--5
	HN67LM104
	HN67LM103
	C
	A
	C
	-

	30GXN,R450B--6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA076---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXA076---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXA086---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA096---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA096---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA096---4
	HN67LM104
	-
	C
	-
	A
	-

	30HXA096---5
	HN67LM104
	-
	C
	-
	A
	-

	30HXA096---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA096---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXA096---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA106---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA106---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA106---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXA106---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXA106---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA106---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXA106---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA116---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA116---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA116---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXA116---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXA116---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA116---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXA116---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA126---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA126---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA126---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXA126---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXA126---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA126---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXA126---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA136---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA136---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA136---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXA136---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXA136---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA136---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXA136---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA146---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA146---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA146---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXA146---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXA146---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA146---8
	HN67LM104
	-
	C
	-
	C
	-

	30HXA146---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA161---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA161---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA161---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXA161---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXA161---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA161---8
	HN67LM104
	-
	C
	-
	C
	-

	30HXA161---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA171---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA171---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA171---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXA171---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXA171---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA171---8
	HN67LM104
	-
	C
	-
	C
	-

	30HXA171---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA186---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXA186---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXA186---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXA186---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXA186---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXA186---8
	HN67LM104
	-
	C
	-
	C
	-

	30HXA186---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXA206---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA206---2
	HN67LM103
	HN67LM103
	B
	A
	B
	-

	30HXA206---4
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXA206---5
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXA206---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA206---8
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXA206---9
	HN67LM103
	HN67LM103
	B
	A
	B
	-

	30HXA246---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA246---2
	HN67LM103
	HN67LM103
	B
	A
	B
	-

	30HXA246---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA246---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA246---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA246---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA246---9
	HN67LM103
	HN67LM103
	B
	B
	B
	-

	30HXA261---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA261---2
	HN67LM103
	HN67LM103
	B
	B
	B
	-

	30HXA261---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA261---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA261---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA261---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA261---9
	HN67LM103
	HN67LM103
	B
	B
	B
	-

	30HXA271---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA271---2
	HN67LM103
	HN67LM103
	B
	B
	B
	-

	30HXA271---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA271---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA271---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXA271---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXA271---9
	HN67LM103
	HN67LM103
	B
	B
	B
	-

	30HXC076---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC076---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC086---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC096---9
	HN67LM103
	-
	A
	-
	A
	--

	30HXC106---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC106---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---4
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---5
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC116---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC126---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC126---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC126---4
	HN67LM103
	-
	B
	-
	B
	-

	30HXC126---5
	HN67LM103
	-
	B
	-
	B
	-

	30HXC126---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC126---8
	HN67LM103
	-
	A
	-
	A
	-

	30HXC126---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC136---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC136---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC136---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXC136---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXC136---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC136---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXC136---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC146---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC146---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC146---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXC146---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXC146---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC146---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXC146---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC161---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC161---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC161---4
	HN67LM104
	-
	C
	-
	B
	-

	30HXC161---5
	HN67LM104
	-
	C
	-
	B
	-

	30HXC161---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC161---8
	HN67LM104
	-
	C
	-
	A
	-

	30HXC161---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC171---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC171---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC171---4
	HN67LM104
	-
	A
	-
	C
	-

	30HXC171---5
	HN67LM104
	-
	A
	-
	C
	-

	30HXC171---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC171---8
	HN67LM104
	-
	A
	-
	C
	-

	30HXC171---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC186---1
	HN67LM103
	-
	A
	-
	A
	-

	30HXC186---2
	HN67LM103
	-
	A
	-
	A
	-

	30HXC186---4
	HN67LM104
	-
	C
	-
	C
	-

	30HXC186---5
	HN67LM104
	-
	C
	-
	C
	-

	30HXC186---6
	HN67LM103
	-
	A
	-
	A
	-

	30HXC186---8
	HN67LM104
	-
	C
	-
	C
	-

	30HXC186---9
	HN67LM103
	-
	A
	-
	A
	-

	30HXC206---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC206---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC206---4
	HN67LM104
	HN67LM103
	B
	A
	C
	-

	30HXC206---5
	HN67LM104
	HN67LM103
	B
	A
	C
	-

	30HXC206---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC206---8
	HN67LM104
	HN67LM103
	B
	A
	C
	-

	30HXC206---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC246---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC246---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC246---4
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC246---5
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC246---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC246---8
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC246---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC261---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC261---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC261---4
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC261---5
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC261---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC261---8
	HN67LM104
	HN67LM103
	C
	B
	C
	-

	30HXC261---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC271---1
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC271---2
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC271---4
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXC271---5
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXC271---6
	HN67LM103
	HN67LM103
	A
	A
	A
	-

	30HXC271---8
	HN67LM104
	HN67LM104
	C
	C
	C
	-

	30HXC271---9
	HN67LM103
	HN67LM103
	A
	A
	A
	-


Configuration A:  1 set of leads, all through the toroid.  See Figure 7 on page 107.

Configuration B:  2 sets of leads, all through the toroid.  See Figure 8 on page 107.

Configuration C:  2 sets of leads, 1 set through the toroid, the other around it.  See Figure 9 on page 107.

[image: image17.png]



Figure 7 - Configuration A


[image: image18.png]E5R)..





Figure 8 - Configuration B

[image: image19.png]



Figure 9 - Configuration C

The following table describes the toroid usage and lead configuration for 30GXN/GXR produced with starting serial number 2401F and 30HXA/HXC produced with starting serial number 0802Q.  These units use the HN67LM103 ComfortLink Compressor Protection Module, with the 30GX502783 Compressor Current Toroid for compressors with Rated Load Amps less than 314 amps.  For compressors with Rated Load Amps greater than or equal to 314, the 30GX504711 Compressor Current Toroid is used.

If the field conversion to the ½ current Compressor Current Toriod 30GX504711 is made, the Compressor Protection module should be changed to HN67LM103 to lower the ground fault settings.

	Serial Number Reference
	30GXN/GXR:  2401F

30HXA/HXC:  0802Q

	Unit
	Compressor Current Toroid Module
	Compressor Lead Configuration

(See notes following table)

	
	A1
	A2
	B1
	B2
	A1
	A2
	B1
	B2

	30GXN,R080---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R080---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R090---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R090---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R090---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R090---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R090---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R090---8
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R090---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R106---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R106---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R106---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R106---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R106---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R106---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R106---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R114---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R114---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R114---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R114---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R114---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R115---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R115---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R125---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R125---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R125---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R125---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R125---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R125---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R125---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R135---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R135---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R135---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R135---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R135---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R135---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R135---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R150---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R150---2
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R150---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R150---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R150---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R150---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R150---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	B
	-

	30GXN,R160---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R160---2
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R160---4
	30GX504711
	
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R160---5
	30GX504711
	
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R160---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R160---8
	30GX504711
	
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R160---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	B
	-

	30GXN,R174---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R174---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R174---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R174---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R174---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R175---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R175---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R204---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R204---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R204---4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R204---5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R204---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R205---8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R205---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R220A--8
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R220A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R220B--8
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R220B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R225---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R225---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R225---4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R225---5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R225---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R225---8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R225---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R240A--8
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30GXN,R240A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R240B--8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R240B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R249---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R249---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R249---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R249---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R249---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R250---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R250---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R264---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R264---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R264---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R264---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R264---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R264---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R264---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R275A--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R275A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R275B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R275B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R281---1
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R281---2
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R281---6
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R281---9
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R300A--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R300A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	B
	-

	30GXN,R301---1
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R301---2
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R301---6
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R301---9
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R300B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R300B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R320A--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R320A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	B
	-

	30GXN,R320B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R320B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	B
	-

	30GXN,R325---1
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R325---2
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R325---6
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R325---9
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R345A--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R345A--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R345B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R345B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R350---1
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R350---2
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R350---6
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R350---9
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	A

	30GXN,R365A--8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R365A--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R365B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R365B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R370A--1
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	-

	30GXN,R370A--2
	30GX502786
	30GX502786
	30GX502786
	30GX502786
	A
	A
	A
	-

	30GXN,R370A--4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R370A--5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R370A--6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R370B--1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R370B--2
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R370B--4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R370B--5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R370B--6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R390A--1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R390A--2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R390A--4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R390A--5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R390A--6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R390B--1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R390B--2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R390B--4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R390B--5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R390B--6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R395A--8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R395A--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R395B--8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R395B--9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R410A--8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R410A--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R410B--8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R410B--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R415A--1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R415A--2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R415A--4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R415A--5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30GXN,R415A--6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R415B--1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R415B--2
	30GX502786
	-
	30GX502786
	-
	B
	-
	A
	-

	30GXN,R415B--4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R415B--5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30GXN,R415B--6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30GXN,R440A--8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R440A--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R440B--8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R440B--9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450A--1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450A--2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450A--4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R450A--5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R450A--6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450B--1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450B--2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30GXN,R450B--4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R450B--5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30GXN,R450B--6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA076---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA076---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA086---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA096---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA096---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA096---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA096---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA096---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA096---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA096---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA106---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA106---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA106---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA106---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA106---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA106---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA106---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA116---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA116---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA116---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA116---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA116---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA116---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA116---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA126---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA126---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA126---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA126---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA126---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA126---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA126---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA136---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA136---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA136---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA136---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA136---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA136---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXA136---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA146---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA146---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA146---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA146---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA146---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA146---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA146---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA161---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA161---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA161---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA161---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXA161---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA161---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA161---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA171---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA171---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA171---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA171---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA171---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA171---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA171---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA186---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA186---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA186---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA186---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA186---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA186---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXA186---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXA206---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA206---2
	30GX502786
	30GX502786
	30GX502786
	-
	B
	A
	B
	-

	30HXA206---4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXA206---5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXA206---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA206---8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXA206---9
	30GX502786
	30GX502786
	30GX502786
	-
	B
	A
	B
	-

	30HXA246---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA246---2
	30GX502786
	30GX502786
	30GX502786
	-
	B
	A
	B
	-

	30HXA246---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA246---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA246---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA246---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA246---9
	30GX502786
	30GX502786
	30GX502786
	-
	B
	B
	B
	-

	30HXA261---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA261---2
	30GX502786
	30GX502786
	30GX502786
	-
	B
	B
	B
	-

	30HXA261---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA261---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA261---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA261---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA261---9
	30GX502786
	30GX502786
	30GX502786
	-
	B
	B
	B
	-

	30HXA271---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA271---2
	30GX502786
	30GX502786
	30GX502786
	-
	B
	B
	B
	-

	30HXA271---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA271---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA271---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXA271---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXA271---9
	30GX502786
	30GX502786
	30GX502786
	-
	B
	B
	B
	-

	30HXC076---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC076---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC086---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC096---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	--

	30HXC106---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC106---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---4
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---5
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC116---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC126---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC126---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC126---4
	30GX502786
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC126---5
	30GX502786
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC126---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC126---8
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC126---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC136---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC136---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC136---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC136---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC136---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC136---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXC136---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC146---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC146---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC146---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC146---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC146---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC146---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXC146---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC161---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC161---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC161---4
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC161---5
	30GX504711
	-
	30GX502786
	-
	B
	-
	B
	-

	30HXC161---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC161---8
	30GX504711
	-
	30GX502786
	-
	B
	-
	A
	-

	30HXC161---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC171---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC171---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC171---4
	30GX502786
	-
	30GX504711
	-
	A
	-
	B
	-

	30HXC171---5
	30GX502786
	-
	30GX504711
	-
	A
	-
	B
	-

	30HXC171---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC171---8
	30GX502786
	-
	30GX504711
	-
	A
	-
	B
	-

	30HXC171---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC186---1
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC186---2
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC186---4
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXC186---5
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXC186---6
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC186---8
	30GX504711
	-
	30GX504711
	-
	B
	-
	B
	-

	30HXC186---9
	30GX502786
	-
	30GX502786
	-
	A
	-
	A
	-

	30HXC206---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC206---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC206---4
	30GX502786
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30HXC206---5
	30GX502786
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30HXC206---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC206---8
	30GX502786
	30GX502786
	30GX504711
	-
	B
	A
	B
	-

	30HXC206---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC246---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC246---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC246---4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC246---5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC246---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC246---8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC246---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC261---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC261---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC261---4
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC261---5
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC261---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC261---8
	30GX504711
	30GX502786
	30GX504711
	-
	B
	B
	B
	-

	30HXC261---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC271---1
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC271---2
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC271---4
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXC271---5
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXC271---6
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-

	30HXC271---8
	30GX504711
	30GX504711
	30GX504711
	-
	B
	B
	B
	-

	30HXC271---9
	30GX502786
	30GX502786
	30GX502786
	-
	A
	A
	A
	-


Configuration A:  1 set of leads, all through the toroid.  See Figure 7 on page 107.

Configuration B:  2 sets of leads, all through the toroid.  See Figure 8 on page 107.

Troubleshooting:

CCP CR1 or CR5 Failure

Chattering relays can cause arcing and burning of the contacts.  If this condition is encountered, check the following items:

· Check the High Pressure Switch.  If the pressure switch is chattering, consider adding a snubber to the HPS.  Replace the HPS.  You will need to use the existing fitting, a 1/4" flare to 1/4" NPT and use a 50EQ400532.

CCP FR14 Failure

If this condition is encountered, check the following items:

· If the J3 connection is made 2 pins off toward the relay, it can cause the resistor to fail.  
· Check for a grounded high pressure switch.
Interface Devices

Navigator

Cleaning 

The Navigator can be cleaned with a mild detergent.  Isopropyl alcohol or a glass cleaner can be used on all Navigator surfaces.

Connection Cord/Plug Assembly Replacement

If the RJ14 plug is damaged, it can be replaced.  If it is replaced, the wiring to the plug must be as shown below:

	
	Pin

	
	1
	2
	3
	4
	5
	6

	Wire Color
	Black
	Green
	Blue
	Yellow
	Red
	White


[image: image20.png]LTI





Figure 10 - Navigator Connection Diagram

The connection cable can be replaced if damaged.  Replacement cables are available from Replacement Components Division.  Remove the Navigator from the LEN connection before proceeding.

1. Remove the 6 screws from the back of the case to gain access to the internal plug for the device, and keep them for installation later.

2. The back cover is connected to the touch pad by a ribbon cable.  The ribbon cable is not long enough to allow the two halves to be completely separated.  To be able to access the plug connection, slightly offset the back cover.  Be careful not to damage the ribbon cable.

3. Unplug the damaged cable.

4. Plug in the new cable.

5. Insert the rubber grommet (included with new cable assembly) into the cable entrance hole.

6. Realign the two halves of the Navigator.  Be sure that the grommet is properly seated in the cable entrance hole.  

7. Reinstall the 6 screws previously removed.

NOTE: Failure to properly seal the Navigator with the screws and grommet will compromise the watertight integrity of the device.

Energy Management Board (EMM)

Troubleshooting:

Communications

The following table has the design resistance in ohms as measured between the pins of the connector listed.  Values to as little as half of the listed resistance can be expected to perform without any problems.  All measurements are to be made with power removed from the board and no connections to either the LEN or CCN ports.

	Part Number
	Serial Number
	(LEN) Resistance between Pins / Connector

	With Software
	Without

Software
	Vendor
	
	Pins 1 to 3
	Pins 1 to 2
	Pins 2 to 3

	30GT515218
	HK50AA028
	CEPL130351-01
	Prior to

4902N
	40K Ω
J3 & J4
	20K Ω
J3 & J4
	20K Ω
J3 & J4

	
	
	
	Starting

4902N
	287K Ω
J3 & J4
	7.25M Ω
J3 & J4
	5.9M Ω
J3 & J4


EXV Board (EXV)

Troubleshooting:

Communications

The following table has the design resistance in ohms as measured between the pins of the connector listed.  Values to as little as half of the listed resistance can be expected to perform without any problems.  All measurements are to be made with power removed from the board and no connections to either the LEN or CCN ports.

	Part Number
	Serial Number
	(LEN) Resistance between Pins / Connector

	With Software
	Without

Software
	Vendor
	
	Pins 1 to 3
	Pins 1 to 2
	Pins 2 to 3

	30GT515217
	HK50AA026
	CEPL130349-01
	Prior to

4802N
	40K Ω
J3 & J4
	20K Ω
J3 & J4
	20K Ω
J3 & J4

	
	
	
	Starting

4802N
	287K Ω
J3 & J4
	7.25M Ω
J3 & J4
	5.9M Ω
J3 & J4


Main Base Board (MBB)

Troubleshooting:

Communications

The following table has the design resistance in ohms as measured between the pins of the connector listed.  Values to as little as half of the listed resistance can be expected to perform without any problems.  All measurements are to be made with power removed from the board and no connections to either the LEN or CCN ports.

	Part Number
	Serial Number
	(LEN) Resistance between Pins / Connector

	With Software
	Without

Software
	Vendor
	
	Pins 1 to 3
	Pins 1 to 2
	Pins 2 to 3

	30HX501314
	HK50AA029
	CEPL130346-01
	Prior to

4702N
	15K Ω
J3, J4, & J5
	7.5K Ω

J3, J4, & J5
	7.5K Ω

J3, J4, & J5

	
	
	
	Starting

4702N
	18.9K Ω 

J3, J4, & J5
	9.9K Ω

J3, J4, & J5
	9.9K Ω

J3, J4, & J5


	Part Number
	Serial Number
	(CCN) Resistance between Pins / Connector

	With Software
	Without

Software
	Vendor
	
	Pins 5 to 7
	Pins 5 to 6
	Pins 6 to 7

	30HX501314
	HK50AA029
	CEPL130346-01
	Prior to

4702N
	15K Ω
J5
	7.5K Ω

J5
	7.5K Ω

J5

	
	
	
	Starting

4702N
	18.9K Ω 

J5
	9.9K Ω

J5
	9.9K Ω

J5


Screw Compressor Board (SCB)

Troubleshooting:

Communications

The following table has the design resistance in ohms as measured between the pins of the connector listed.  Values to as little as half of the listed resistance can be expected to perform without any problems.  All measurements are to be made with power removed from the board and no connections to either the LEN or CCN ports.

	Part Number
	Serial Number
	(LEN) Resistance between Pins / Connector

	With Software
	Without

Software
	Vendor
	
	Pins 1 to 3
	Pins 1 to 2
	Pins 2 to 3

	30HX501316
	HK50AA032
	CEPL130427-01
	Prior to 

4802N
	15K Ω
J3 & J4
	7.5K Ω

J3 & J4
	7.5K Ω

J3 & J4

	
	
	
	Starting

4802N
	18.9K Ω 

J3 & J4
	9.9K Ω

J3 & J4
	9.9K Ω

J3 & J4


Compressor

Service Bulletins pertaining to this issue:

· SMB0200?? –06N Compressor Return Procedures

This bulletin describes the procedure for field return of 06N compressors and a procedure for a teardown analysis.

· SMB990037 – 06N Replacement Compressors

This bulletin advised of an error printed in the Controls, Start-Up, Operation, Service, and Troubleshooting Book, previous to and including 30G,H-4T, and a sticker on the compressor which advises the servicer to contact Carlyle at a toll free phone number to obtain a replacement compressor.  The telephone number listed does not connect the servicer to Carlyle Compressor Company.

· SMB960072 – Carlyle 06N Compressor Failure in 30GX & 30HX Chillers

This bulletin described the field return procedure for the 06N compressors.

· PMB02-105 – Authorized Field Repairs and Parts Kits for 06N Screw Compressors

This bulletin included a description of all authorized field repairs and part numbers.

Compression

Discharge Check Valve

The discharge check valve is located in the muffler casing of the compressor between the discharge port and the muffler assembly.  The check valve is installed to prevent pressure equalization through a non-operating compressor.

The check valve is a mushroom-shaped part located in the internal muffler/discharge cavity.  It is guided on a hardened dowel via a hole in the stem.  The seal is achieved between the spherical top surface of the check valve and a conical seat in the outlet casing.  

Troubleshooting:

· Compressor whine at shutdown.

The refrigerant gas spinning the rotors backwards as the system pressures equalize through the compressor causes this whine.  This backward rotation, unlike powered reverse rotation, is not detrimental to the compressor.  However, in multiple compressor circuits, check valve leakage will significantly reduce capacity.  

Check the following items:

· Check the discharge check valve for wear.

· Rapidly Plugging Oil Filters

See “Compressor whine at shutdown.

· Ticking Noise at the compressor

See “Compressor whine at shutdown.

If a worn check valve is encountered, replace the check valve.  If there is additional damage to the mating surface, RCD has the bearing cover with all necessary o-rings in a kit for field replacement.

Service Bulletins pertaining to this issue:

· PMB02-105 – Authorized Field Repairs and Parts Kits for 06N Screw Compressors

This bulletin included a description of all authorized field repairs and part numbers.

Suction Screen

Compressors starting with Serial Number 3501J do not include the suction screen.  The screen was removed as an efficiency improvement.  If a screen is desired, it can be added.

Electrical

Motor Terminal Pins
Service Bulletins pertaining to this issue:

· SMB990001 – 06N Terminal Pin Field Torquing Procedure

This bulletin described the process for the field to follow when tightening the Motor Terminal Pin on the 06N compressors.  The bulletin also included the instruction sheet for upgrading to the new style valve.

· PMB02-105 – Authorized Field Repairs and Parts Kits for 06N Screw Compressors

This bulletin included a description of all authorized field repairs and part numbers.

Lubrication System

Oil Solenoid Valve

An oil solenoid valve on the compressor controls the oil flow to the compressor internal components.  The oil solenoid valve has an integral check valve used to allow for the oi filter change without removing the charge.

Service Bulletins pertaining to this issue:

· SMB990003 – 06N Oil Solenoid Valve Changes

This bulletin described the oil solenoid valve changes implemented with the 06N compressors.  The bulletin also included the instruction sheet for upgrading to the new style valve.

· PMB02-105 – Authorized Field Repairs and Parts Kits for 06N Screw Compressors

This bulletin included a description of all authorized field repairs and part numbers.

Condenser Fan

Several condenser fan options are available for the 30GXN/GXR machines:  Standard fans, 0.4 and 0.8 w.g. (100 and 200 Pa) External Static Pressure Fans.

Standard Fan

The 30GX machines use the “Flying Bird Fan”.  This fan is made from a UV stable molded plastic with a brass hub.  The fan is secured with set screws and a keyway to the motor shaft.  

Several modifications have been made to the fan.  Starting Serial Numbers are approximations of the implementation of the improvement.

The ComfortLink 30GX machines were being assembled with a spacer was installed between the motor and the fan to stop the fan from sliding down the motor shaft.  The part can be obtained from McMaster-Carr, part number 6432K21.  This spacer remained in production until the hub improvements noted in 5200F were implemented.

Starting with serial numbers 4200F, additional hub improvements were made.  The set screw torque was changed to 240 in-lbs (27.1 N-m).

Beginning with serial numbers 5200F, the hub was redesigned to have pins to better capture the plastic to the hub.  A spun-in washer was added to the hub to stop the fan from sliding down the shaft as shown in the figure below.  

[image: image21.jpg]



Figure 11 - Fan Hub

(Prior Serial Number 5200F)


[image: image22.jpg]



Figure 12 - Fan Hub

(Starting Serial Number 5200F)

The fan cover was redesigned slightly to secure the cover better.  Larger drain holes were molded into the fan as shown below.  The view shown is from the under side of the fan.

[image: image23.jpg]



Figure 13 - Fan Drain

(Prior Serial Number 5200F)


[image: image24.jpg]



Figure 14 - Fan Drain

(Starting Serial Number 5200F)

.

Beginning with Serial Number 4201F, the set screw torque was changed from 160 in‑lbs. (14.2 N-m) to 192 in-lbs (17.1 N-m).

0.4 w.g. (100 Pa) External Static Pressure Fan

The 0.4 w.g. (100 Pa) external static fan uses a 12 blade adjustable pitch fan blade with a 5 horsepower fan motor.  The fan deck is strengthened to support the extra weight of the fan motor.  The pitch of the fan blades for 50 Hz applications is 15(, 10( for 60 Hz applications.  The fan pitch requires a special protractor, available from Chicago Blower.  This option uses an external overload for motor protection.  

The 30GXN/GXR250 and 264 (230-3-50) models were produced with the wrong pitch blades called out on an assembly drawing error.

0.8 w.g (200 Pa) External Static Pressure Fan

The 0.8 w.g. (200 Pa) external static fan uses a 12 blade adjustable pitch fan blade with a 5 horsepower fan motor.  The fan deck is strengthened to support the extra weight of the fan motor.  The pitch of the fan blades for 50 Hz applications is 22(, 12( for 60 Hz applications.  The fan pitch requires a special protractor, available from Chicago Blower.  This option uses an external overload for motor protection.  

The 30GXN/GXR150, 160 and 174 (230-3-60) models and the 30GXN/GXR175 (230-3-50) models were produced with the wrong pitch blades called out on an assembly drawing error.

Condenser Fan Motor 

Early ComfortLink production may have been produced with the HD56AK651 (Non-Motormaster III) motors being controlled by the Motormaster III controller.

Cooler

The 30GX/HX product uses a flooded cooler design.  Two separate refrigerant circuits are contained within one vessel adjacent to each other.  A center tube sheet separates the two circuits.  The cooler tubes are rolled into the center tubesheet to create a refrigerant seal.

Cooler Freeze-Up/Leak Cleaning Procedure

There are several questions that should be asked when investigating the cause of a cooler failure.

1. How is the machine on-off cycle being controlled?

2. How are the pumps controlled?

3. Is there a flow switch installed?

4. Is the flow switch properly located?

5. Is the flow switch wired in to the proper terminals?

6. Is the machine control configured to accept the switch input?  

7. What type of switch is installed, differential pressure or paddle?  

8. If a differential pressure switch is installed, what was the differential pressure switch set for? 

9. Does the chiller have control of the pumps? 

10. Are there any isolation valves on the waterside or automatic control valves?

11. What type of fluid is in the chilled water loop?

12. What concentration of brine is used?

13. Are there any refrigerant leaks or a history of refrigerant leaks?

14. What are the design conditions: leaving water temperature, design rise, and water flow rate?

15. What is the loop volume? 

16. Is this a simple system or a primary-secondary loop system? 

17. Is the water flow variable?

18. Check all thermistors for proper installation in the wells?

19. Check to see if all thermistors are reading properly.

20. Check pressure transducers to make sure they are reading properly and are located in the proper positions.  

21. Inspect the economizer plug and replace it if necessary. 

22. Is there a strainer in the water system?  

23. Where is the water strainer located?

24. What size mesh is the water strainer?

Record or download all the alarm codes in history, and get as many details on the operation and status prior to the failure.

The most important part of this investigation is trying to figure out why the cooler has failed.  There have been a number of reasons that have contributed to the cooler failures.  In colder climates an ambient freeze is one.  There is a lot more refrigerant in these vessels than what everyone is used to as compared with a DX system.  With the DX systems, the cooler heaters are in direct contact with the cooler shell.  In the 30GX/HX, the cooler heaters are insertion heaters in the heads only.  There must be a means to move the heat into the center of the bundle.

Cooler strainers are important and required items for the installation.  The machine will run at lower than freeing saturated suctions, which should not be a problem as long as there is the required flow of water.  The next is the cooler flow switch.  Version 12 software no longer allows for the user to disable the cooler flow switch.  A conscious decision to jumper this input must be made.  The switch must be installed and properly configured to assure proper flow.

The construction of the cooler is such that one water tube serves both circuits.  The freeze failure must be checked to be sure that it does not affect both circuits.  If the tube failure is in both circuits, an internal plug must be used to stop a circuit to circuit by-pass.  It is strongly recommended that an eddy current test be completed to determine the extent of the damage.

So far as the clean-up, other than the normal removing the water and/or glycol, we have been recommending the following:

The system should be dehydrated as soon as possible.

Follow all local, EPA (Environmental Protection Agency, USA) and EH & S (Environmental, Health & Safety) codes when handling and disposing of the discarded materials.  Open, lock out and tag the electrical power disconnects for the machine.  Follow all other safety warnings in the literature, on tags and labels on the machine.

Determine the number of tubes that have failed.  If the number of tubes is less than 10% per pass, plug the tubes.  No more than 10% of the total tubes of the vessel should be plugged.  If more than the limit of tubes have failed, consider replacing the vessel.  Retubing the cooler may be difficult due to the nature of the failure.  Freeze bulges can tear away from the tube as it is pulled through the tubesheet leaving sharp debris in the cooler, which eventually could fail another cooler tube.  Plug and pin part numbers are listed in the Controls and Troubleshooting book.

If the compressor has been filled with water or glycol it is probably not salvageable. There is no guarantee that the compressor is free of contaminates. Replace the compressor per the instructions in the Controls and Troubleshooting book. Drain the oil from the cooler and oil separator.  Replace the sight glass, external muffler, motor cooling filter drier, and the external oil filter. 

To aid in the water removal in the system, pierce the low points of the coil headers (30GX) and/or refrigerant lines.  Pressurize and blow out the system with dry nitrogen until water droplets stop coming from the holes.

Plug the cooler tubes as required.  

Remove the factory installed strainer and install a four core filter drier in the liquid line ahead of the EXV/Economizer.  Be sure that the shell includes a strainer and the cores are R-134a and POE compatible. The filter-driers should be removed once the clean-up is complete on 30HXC machines.  Failure to remove the filter driers will result in a system performance loss.  Check the refrigerant system for leaks.  Evacuate and dehydrate the circuit using standard refrigeration techniques.

Recharge the machine with new oil and refrigerant.  Change the motor cooling filter drier and the liquid line filter drier cores 24 hours after operation.  Obtain an oil sample and test for water.  If the system is wet, consider changing the oil again.  Oil test limits are listed in the Service Section under Oil on page 133.

Service Bulletins pertaining to this issue:

· SMB990061 –30GX/HX cooler and 30HXC Condenser Tube ID Dimensions

This bulletin noted the incorrect tube post-roll tube dimensions listed in 30G,H‑3T.

· SMB000001 – 30GX/HX Installation Review/Flow Switch

This bulletin provided a installation checklist to check for proper installation of the machines and noted the factory provided flow switch.

· SMB000013 - 30GX/HX Cooler and 30HXC Condenser Tube Plug Pin Number

This bulletin noted the incorrect tube plug pin part numbers listed in 30G,H-5T.

Cooler Head Removal

A 1/2-13 x 3/4 deep hole is provided on top of the Cooler Head to allow for installation of an eye bolt.

Cooler Heater

For the 30GX machines, the Cooler Protection Option includes both the cooler heaters and the pump out solenoids.  This feature was made standard on all machines shipped within North America in Product Bulletin 111-01-50, dated June 15, 2001.

On units with cooler heaters, the number of heaters changes with the number of compressors.  On the 30GXN/GXR080-178 and their associated modular units, there are two 500 watt heaters, one in each water head.  On all other units, there are four 500 watt heaters, two in each water head. 

There are two cooler heaters, based on control voltage.

	Cooler Heater
	Control Voltage
	Resistance @ 70 ± 5 ºF
	Watts

	30GX404235
	120 VAC
	26.1 – 28.1 ohms
	500 ± 5%

	30GX404236
	240 VAC
	104.2 – 115.2 ohms
	


Cooler Weights

	Cooler
	lbs
	kg

	10HX400003
	1430
	650

	10HX400005
	1650
	750

	10HX400009
	1694
	770

	10HX400011
	1925
	875

	10HX400014
	1749
	795

	10HX400156
	3740
	1700

	10HX400157
	3300
	1500

	10HX400170
	3300
	1500

	10HX400252
	4180
	1900


	30GX COOLER

	30GX 
	Pass
	Part No.
	Nozzle Size
	No. of Passes
	Shell O.D.
	Tube P/N
	No. of Tubes

	
	
	
	
	
	
	
	

	080
090
	-1P
	10HX400174
	4"
	2
	14"
	10HX500094
	116

	
	STD
	10HX400003
	4"
	3
	
	
	

	
	+1P
	10HX400208
	4"
	4
	
	
	

	106
114
115
	-1P
	10HX400176
	5"
	2
	16”
	10HX500094
	135

	
	STD
	10HX400009
	5"
	3
	
	
	

	
	+1P
	10HX400212
	5"
	4
	
	
	

	125
135
	-1P
	10HX400178
	5"
	2
	16"
	10HX500094
	163

	
	STD
	10HX400014
	5"
	3
	
	
	

	
	+1P
	10HX400217
	5"
	4
	
	
	

	150

	-1P
	10HX400175
	5"
	1
	14"
	10HX500096
	116

	
	STD
	10HX400005
	4"
	2
	
	
	

	
	+1P
	10HX400209
	4"
	3
	
	
	

	160
174
175
	-1P
	10HX400177
	5"
	1
	16"
	10HX500096
	135

	
	STD
	10HX400011
	5"
	2
	
	
	

	
	+1P
	10HX400214
	5"
	3
	
	
	

	204
205
	-1P
	10HX400171
	8"
	1
	18"
	10HX500142
	163

	
	STD
	10HX400170
	6"
	2
	
	
	

	
	+1P
	10HX400223
	
	3
	
	
	

	225
	-1P
	10HX400168
	8"
	1
	18"
	10HX500142
	187

	
	STD
	10HX400156
	6"
	2
	
	
	

	
	+1P
	10HX400221
	
	3
	
	
	

	249
250
264
	-1P
	10HX400169
	8"
	1
	18"
	10HX500142
	208

	
	STD
	10HX400157
	6"
	2
	
	
	

	
	+1P
	10HX400222
	
	3
	
	
	

	281
301
325
350
	-1P
	10HX400254
	8”
	1
	20"
	10HX500259
	263

	
	STD
	10HX400252
	
	2
	
	
	

	
	+1P
	10HX400253
	
	3
	
	
	


	 30HX COOLER

	30HX 
	Pass
	Part No.
	Nozzle Size
	No. of Passes
	Shell O.D.
	Tube P/N
	No. of Tubes

	076

086
	-1
	10HX400187
	4"
	2
	14"
	10HX500095
	101

	
	STD
	10HX400001
	
	3
	
	
	

	
	+1
	10HX400206
	
	4
	
	
	

	96
	-1
	10HX400189
	4"
	2
	14"
	10HX500094
	116

	
	STD
	10HX400002
	
	3
	
	
	

	
	+1
	10HX400207
	
	4
	
	
	

	106
	-1P
	10HX400193
	5"
	2
	16"
	10HX500094
	135

	
	STD
	10HX400010
	
	3
	
	
	

	
	+1P
	10HX400213
	
	4
	
	
	

	116

126
	-1P
	10HX 400192
	5"
	1
	14"
	10HX500105
	101

	
	STD
	10HX 400007
	4"
	2
	
	
	

	
	+1P
	10HX 400211
	4"
	3
	
	
	

	136

146
	-1P
	10HX 400191
	5"
	1
	14"
	10HX500105
	116

	
	STD
	10HX 400006
	4"
	2
	
	
	

	
	+1P
	10HX 400210
	4"
	3
	
	
	

	161
	-1P
	10HX 400196
	5"
	1
	16"
	10HX500105
	135

	
	STD
	10HX 400104
	
	2
	
	
	

	
	+1P
	10HX 400218
	
	3
	
	
	

	171
	-1P
	10HX 400194
	5"
	1
	16"
	10HX500096
	135

	
	STD
	10HX 400012
	
	2
	
	
	

	
	+1P
	10HX 400215
	
	3
	
	
	

	186
	-1P
	10HX 400195
	5"
	1
	16"
	10HX500096
	163

	
	STD
	10HX 400013
	
	2
	
	
	

	
	+1P
	10HX 400216
	
	3
	
	
	

	206
	-1P
	10HX 400197
	6"
	1
	18"
	10HX500142
	187

	
	STD
	10HX 400125
	
	2
	
	
	

	
	+1P
	10HX 400219
	
	3
	
	
	

	246

261

271
	-1P
	10HX 400198
	6"
	1
	18"
	10HX500142
	208

	
	STD
	10HX 400126
	
	2
	
	
	

	
	+1P
	10HX 400220
	
	3
	
	
	


Cooler Liquid Level Sensor

This device provides the control system with an operating level of liquid refrigerant in the cooler.  The device uses an 18-watt heater to heat three (3) 5 k( @ 77 (F (25 (C) thermistors wired in series.

Troubleshooting:

To check the Cooler Liquid Level Sensor’s heater, disconnect the Cooler Liquid Level Sensor from the control system, disabling the internal heater.  Measure the heater’s resistance.  The resistance should be 31.4 (.  

To check the thermistors, disconnect the Cooler Liquid Level Sensor from the control system, disabling the internal heater.  Allow the sensor to come to equilibrium with the cooler.  Measure the resistance of the three thermistors.  With a refrigerant gage, measure the cooler pressure and convert the pressure to a saturated temperature.  On a 5 k( thermistor chart, find the resistance corresponding to the saturated temperature and multiply the resistance by 3.  The multiplied value should be close to the measured resistance.

Condenser

	30HXC CONDENSER

	30HXC
	Part Number
	Shell O.D.
	Tube Number
	No. of Tubes
	No. of Passes
	Nozzle
	Liquid Line

	076

086
	09RX400173
	18”
	09RX500086
	84
	2
	5”
	1-1/8”

	096

106
	09RX400174
	18”
	09RX500085
	96
	2
	5”
	1-1/8”

	116

126
	09RX400175
	18”
	09RX500088
	105
	2
	5”
	1-1/8”

	136

146
	09RX400176
	18”
	09RX500088
	126
	2
	5”
	1-1/8”

	161
	09RX400177
	20”
	09RX500088
	136
	2
	5”
	1-3/8”

	171

186
	09RX400178
	20”
	09RX500087
	177
	2
	5”
	1-3/8”

	206
	09RX400179
	22”
	09RX500134
	197
	2
	6”
	1-5/8”

	246

261

271
	09RX400180
	22”
	09RX500134
	242
	2
	6”
	1-5/8”


Expansion Device

There are two types of expansion devices that are used across the product line, an Electronic Expansion Valve or an Economizer.

Electronic Expansion Valve

The Electronic Expansion Valve or EXV is used on the 30GXN/GXR080, 083, 090, 093, 106, 114, 220B, 30HXA,HXC076-146.  The EXV is the EXV-II style valve.  It is a 1500 step, non-bottom seal valve.

Economizer

The Economizer is a 2-stage expansion device with an Electronic Expansion Valve and low side float.  This device is used on the 30GXN,GXR108,115-528 with the exception of the 220B model, 30HXA/HXC161-271.

A change to the 30HXA171 Brine Option Circuit A Economizer was made beginning with serial number 3602Q.  The new economizer 32GB403794, has a larger EXD Orifice.

Head Pressure Control

30GXN/GXR

MotorMaster III

ComfortLink machines were introduced with MotorMaster III as the device of choice for head pressure control for these machines.

MotorMaster V

MotorMaster V was introduced as the device of choice for head pressure control for these machines starting with serial numbers 0802F.

MotorMaster V requires the use of a jeweler’s screwdriver.  A standard control screwdriver is too large for the controller’s screw terminal block.

Troubleshooting

Condenser Fan speed does not modulate.

If the condenser fan speed does not modulate, check the following items:

· Check the polarity of the drive speed signal

Machine Assembly

To aid in the communication of leak locations, an bulletin was written with piping diagrams attached.

Service Bulletins pertaining to this condition:

· SMB020059 – 30GX Piping Diagrams

This bulletin included a piping diagram for the 30GX machines.

Liquid Line Strainers

All ComfortLink 30GX/HX machines use cleanable liquid line strainers.

On 30HXA/HXC076-146 machines produced before 5200F, the strainer frequently filled a small area of the screen with debris causing a restriction of refrigerant flow.  This can result in low saturated suction temperature alarms.   A factory investigation found insufficient space between the strainer body and screen for annular refrigerant flow.  As a result of the low clearance space, all of the refrigerant flow exited the screen through one spot.  An early attempt to increase the flow area was made by dimpling the screen.  This requires that the screen be properly installed with the dimple at the exit of the strainer body.

As a result, beginning with machines produced with serial number 5200F, the factory began using a new strainer assembly with improved flow characteristics without a part number change.  The part number remained KH12HN210.  The new part has the same connection points.  The only indication of the new strainer is the vendor part number, S-4211 Rev. D, and the machine serial number cut-off.  The new screen cannot be installed in the old strainer.   RCD continued to stock the old replacement screen and gasket assembly, 3-010-310 until the stock is depleted.  Additionally, RCD will offer the new screen and gasket assembly replacement for this new strainer assembly.  The part number is 3-010-312 and includes the gasket.  If the old screen is restricted and cannot be cleaned, replace the screen.  Once the screen assemblies are depleted, it will be necessary to replace the entire strainer assembly with the new design.

Replacement Strainer and Gasket Kits have been set-up in RCD.  Confirm these part numbers on EPIC before ordering the parts:

	Strainer Assembly Part Number
	Screen and Gasket Part Number

	KH12HN200
	3-010-311

	KH12HN210 (Henry P/N: S-4211 Rev. C.) 
	3-010-310

	KH12HN210 (Henry P/N: S-4211 Rev. D.) 
	3-010-312

	KH12HN240
	3-010-311

	KH12HN280
	3-010-311


Service Bulletins pertaining to the condition:

· SMB000015 – 30GX/HX Refrigerant Strainers

This bulletin announced the use of cleanable strainers in the 30GX/HX line and listed the replacement screen and gasket part number.

· SMB010012 – 30HXA/HXC076-146 Liquid Line Strainer Change

This bulletin announced a design change to cleanable strainers in the 30HXA/HXC076-146 machines line and listed the replacement screen and gasket part number for the new style.

Non-Fused Disconnects

Carrier 30 Series Chillers can be supplied with Non-Fused Disconnects.  These are factory installed devices that provide an electrical disconnect at the machine.  In accordance with good safety practices and regulations, always check with a voltmeter to insure that the power is OFF to all phases, even though the switch handle may indicate OFF.  Electrical shock can cause personal injury and death.  All power sources should be open and tagged before any service work is started.

With the Non-Fused Disconnects, the actuating shaft extends from the body to the door where the handle is installed.  For proper installation, the Shaft Nut & Screw should be aligned with the 0 – OFF position on the body.  The Handle Interlock Pins must be in a horizontal position to engage the handle in the OFF position when installed on the panel door.  If the shaft/handle assembly is not installed correctly, the handle can indicate that the power is OFF, yet the disconnect will still be closed with voltage applied.  The Shaft Nut & Screw indicates the status of the Non-Fused Disconnect.

[image: image25.png]Shaft Nut & Screw Handle Interlock Pins




Figure 15 - Non-Fused Disconnect
Oil

Only Carrier-approved POE oil may be used in Carlyle 06N compressors.  The only approved oil listed under Carrier Material Specification PP47-32 is Castrol Icematic SW220.  It can be obtained from RCD under the following part numbers:

	Quantity
	Totaline Part Number
	RCD Part Number

	1 quart
	P903-1225
	-

	1 gallon
	P903-1201
	PP23BZ104-001

	5 gallons
	P903-1205
	PP23BZ104-005

	55 gallons
	-
	PP23BZ104-055


RCD was selling under the Totaline brand name a “Screw Compressor Oil.”   This oil was less viscous SW68, than the SW220 called out above, and should not be used in the 30GX/HX machines.  Be sure to use only Carrier approved oils in these machines.

Since POE oils have an affinity for water, open containers of oil should not be used when recharging or adding oil to the system.  Water and heat can reverse the manufacturing process that creates the oil.  A by-product of the break down is acid.  As a result, three criteria can be used to check the acceptability of the oil.  They are: Total Acid Number (TAN), Moisture Content, and Viscosity.   The table below shows what Carrier requires for new POE oil, as well as the acceptable limits Carlyle has placed on the oil in an operational system.

The original bulletin, SMB990028, stated a moisture upper limit of 500 ppm.  SMB000056 reduced the moisture level to 100 ppm.

	Criteria
	Specification Requirement*
	Acceptable Limit

	Total Acid Number (TAN)
	0.10 mg KOH/g
	(0.35 mg KOH/g

	Moisture
	50 ppm
	(100 ppm

	Viscosity @ 40 (C
	198-242 cSt
	198 cSt<Sample Viscosity< 242 cSt


Note:  * - The specification requirement refers to the acceptability criteria for new oil based on Carrier Material Specification PP47-32.

Caution must be exercised in preparing an oil sample for testing.  Refrigerant dissolved in the oil will dilute the sample reducing its viscosity.  If an independent laboratory is contracted to perform the analysis, be sure to inform the laboratory the sample contains refrigerant that must be removed prior to the oil viscosity test.

If any of the parameters are outside of the acceptable limits, the oil should be changed.

Service Bulletins pertaining to this condition:

· SMB990028 – 06N POE Oil Guidelines

This bulletin was superceded by SMB000056.

· SMB000056 – 06N POE Oil Guidelines

This bulletin advised of the POE oil guidelines.

Oil Circulation Rate

It is normal to have some oil in circulation.  A normal oil circulation rate is 300-500 ppm.  A refrigerant sample should have no more than 1000 ppm of oil in circulation.

If higher oil circulation rates are found, check the following items:

· Check for an overcharge of oil.  Too much oil in the system will not allow the oil separator to function properly.  A history of repeated oil additions might indicate an oil overcharge.  A high cooler approach would also indicate excess oil in the circuit.  

· Check to be sure that the mesh is in the proper location.   This can only be completed with a scope.

Oil Filter

There are 2 oil filters used for the ComfortLink Chillers.  Installed in the oil lubrication line is a canister filter, referred to as the external filter.  Internal to the compressor is another filter, commonly referred to as the internal filter.

External Oil Filter

The external oil filter is a 4 micron oil filter in line with the oil piping from the oil separator to the compressor.  

Internal Oil Filter

The internal oil filter is a 4 micron oil filter located inside of the compressor housing.  An RCD kit, 06NA6600016 includes the internal oil filter and the o-ring needed for the access cap.

On machines built prior to 0101F, a beaded desiccant motor cooling filter drier was used.  On some machines, due to the loading conditions, the desiccant could break down.  As a result, the internal oil filter would plug with the desiccant material.  A solid core filter drier was used in production starting 0101F.

06NA660016 filter kits assembled during the period May through October 2002,  (Date Codes E/2, F/2, G/2, H/2, J/2, and K/2, or may not have a date code) may not have the correct size hole for mounting the filter on to the compressor brass fitting that holds the oil filter.  If one of these is encountered, the filter will not slide onto the fitting.  All parts were put on hold.  A new kit was set-up with the correct filter included.  The new kit number is 06NA660028.  

After the Internal Oil Filter Kit was changed to the 06NA660028 part number, several filters again exhibited the same problem found in the 06NA660016.  Suspect packages have a K-2 date code stamped on the package label in the upper right hand corner.  Packages stamped with the K-2 date code printed as part of the label in the lower right hand corner will be correct.

Additionally, several reports were received indicating the oil filter plugs were found leaking during extreme cold weather.  These reports indicated that the internal oil filters were changed with the 06NA660016 kits and had been operational for some time without a problem.  After an investigation, the oil plug o-ring cross section was found to be undersized.  The o-ring should measure 0.118 +/- 0.004".  The undersized o-ring was inserted randomly, but it is contained within the 06NA660016 filter kit with no date code.  These are the same filter packages that were recalled under PMB02-137.  There is an alternate o-ring that can be installed, 8TB0847, available through RCD.

The instruction sheet 99TA516075, packaged with the oil filter kits, 06NA660016 and 06NA660028 incorrectly called out the wrong o-ring for the oil filter access plug.  The correct o-ring part number is 8TB0847.  This information was corrected on Instruction Sheet 99TA516075, Revision D.
Service Bulletins pertaining to this component:

· SMB010008 – 06N Internal Oil Filters Plugging


This bulletin described the problem with the motor cooling filter drier disintegrating during operation.  A solid core filter drier was installed starting with serial number 5200F.

· PMB02-137 – Oil Filter Kit Recall Used On 06N Compressors

This bulletin described the problem of the undersized mounting and the new kit part number for the correct filter. 

Oil Pump

The 30GX/HX machines use an external oil pump to provide pre-start lubrication to the compressor and supplemental pressure assistance during operation.  The ComfortLink machines have always used a Magnetic Drive Oil Pump.

For the 30GX machines, the original pump 30GX503303 was used from the initial production run until serial numbers beginning with 1701F.  With serial numbers beginning with 1801F, a new pump 30GX504591 was used.

For the 30HX machines, the original pump 30GX503303 was used from the initial production run until serial numbers beginning with 4201Q.  With serial numbers beginning with 4301Q, a new pump 30GX504591 was used.

The two pumps are electrically the same.  The pump connections are made with o-ring face seal fittings.  The only difference between the 30GX503303 and the 30GX504591 pumps are the height of the oil pump connection fittings.  The 30GX503303 used the same connection for the oil inlet and outlet.  The 30GX504591 used two different height fittings for the oil inlet and outlet.  In both cases, the seal of the fitting to pump body is accomplished by an SAE o-ring fitting.

Oil Separator

Oil separators are used on these machines to collect the oil on the high side of the machine.  Separate ASME vessels are used with the 30GX and 30HXA machines.  On the 30HXC, the oil separator is internal with the condenser.  Two separation techniques are used in these vessels.  First, the discharge gas is directed to the wall.  The force of the gas striking the wall causes most of the oil to cling to the wall and drain into the reservoir.  The secondary method is a York mesh.  This is a steel mesh inserted into the vessel.  Small airborne droplets of oil collect in the mesh.  As the droplets increase in 

size, they eventually fall into the reservoir.

For oil circulation rates, see Oil Circulation Rate on page 134.

AC&R produced oil separators were used on the 30GX machines until 3602F.  Beginning with serial numbers starting with 3102F and fully implemented starting with 3602F, the 30GX oil separators are supplied by Carrier Mexico.

If the York mesh breaks free from its mounting, the refrigerant flow through the vessel causes the mesh to move toward the level switch.  Eventually, the mesh will cause the float to bind.  An external oil level switch can be installed to take the place of the bound level switch.

Troubleshooting:

30GX:  Caution must be used when confirming an oil level in the separator.  Refrigerant will be dissolved in the oil, artificially elevating the level.

Oil Separator Heaters

The 30GX machines use 2 oil separator heaters, one for each circuit.  These heaters are flexible strip heaters that are attached to the under side of the oil separator.  The heaters have a rating of 500 +5/-10% watts.  The heaters are wired for either 120 or 230 vac.  

	Heater
	Voltage, vac
	Resistance (ohms) @ 75 ºF (24 ºC)

	HT38KN011
	120
	28.8 +2.94/-1.47

	
	230
	115.2 +11.76/-5.88

	HT38KN012
	120
	28.8 +2.94/-1.47

	
	230
	115.2 +11.76/-5.88


Refrigerant

The 30GXN/GXR and 30HXA/HXC machines all use R-134a. 

Refrigerant Moisture Limit

The upper limit for moisture in a system is based on the water saturation limit at 35 (F (1.6 (C).  This was carried through for HFC/POE systems as well.  R-134a has a maximum limit of 625 ppm.  The POE oil has a max limit of 100 ppm.  Since there is a strong POE/water interaction, the refrigerant limit is too high.  The refrigerant limit was established to prevent free water freeze up.  As a result, the upper limit has been lowered to the upper limit of the POE moisture limit.

	Criteria
	Specification Requirement*
	Acceptable Limit

	Moisture
	10 ppm
	(100 ppm


Note:  * - The specification requirement refers to the acceptability criteria for new oil based on Carrier Material Specification PS10-34.

If higher moisture content is found, check the following:

· Check for a cooler or condenser leak

If a high moisture content condition is found, repair the leak, evacuate and dehydrate the system using standard refrigerant practices.

Refrigerant Charging

Beginning with production starting around 0802F for the 30GX and 0802Q for the 30HX, the liquid line charging port between the EXV/Economizer and the cooler was changed to a high flow shrader fitting.  

[image: image26.jpg]



Figure 16 - High Flow Shrader with Cap




[image: image27.jpg]



Figure 17 - High Flow Shrader with Cap Removed

The factory uses this device during the manufacturing process.  The fitting is only accessible with a special adapter.  RCD has the adapter set-up.  

	RCD Part Number
	Description

	A-62PF221
	¼” SAE Flare Coupler Assembly

	A-62PF321
	3/8” SAE Flare Coupler Assembly


Charging can be accomplished by installing a tee between the suction pressure transducer fitting and cooler suction shrader.  Refrigerant charging must be slow.  Failure to slowly charge the circuit will result in Economizer Pressure Transducer Alerts.

Beginning with units with serial number 0503F for the 30GX machines, and 0903Q for 30HX machines, the factory added a charging shrader valve on the liquid line in addition to the high flow shrader valve.  This is not an exact break in serial numbers due to stocking conditions.

Service Bulletins pertaining to this component:

· SMB030009 – 30GX, 30HX, 30RA Refrigerant Access


This bulletin described the use of the high flow shrader factory access ports and the adapters required to use them.

30HXA Refrigerant Charging

30HXA/09AZ Initial Refrigerant Charging Chart

The following table depicts the approximate amount of charge for the 30HXA and 09AZ combinations with 25 feet of line separation.  Additional refrigerant is required for longer line lengths.

	30HXA

Model
	Circuit
	Cooler

Charge
	09AZV

Model
	Condenser

Charge
	Liquid Line

Size
	25 ft. Line

Charge
	TOTAL

Charge (lbs.)

	106
	A
	88
	102FE
	24
	1-3/8
	16
	128

	
	B
	56
	
	18
	1-3/8
	16
	90

	116
	A
	84
	112FE
	42
	1-3/8
	16
	142

	
	B
	61
	
	42
	1-3/8
	16
	119

	126
	A
	90
	122FE
	24
	1-3/8
	16
	130

	
	B
	71
	
	24
	1-3/8
	16
	111

	136
	A
	99
	132FE
	57
	1-3/8
	16
	172

	
	B
	71
	
	42
	1-3/8
	16
	129

	146
	A
	95
	142FE
	57
	1-3/8
	16
	168

	
	B
	80
	
	57
	1-3/8
	16
	152

	161
	A
	120
	162FE
	68
	1-3/8
	16
	204

	
	B
	88
	
	68
	1-3/8
	16
	172

	171
	A
	95
	172FE
	68
	1-3/8
	16
	179

	
	B
	112
	
	68
	1-3/8
	16
	196

	186
	A
	108
	182FE
	68
	1-3/8
	16
	192

	
	B
	108
	
	68
	1-3/8
	16
	192

	206
	A
	160
	101FA
	49
	1-5/8
	22
	231

	
	B
	108
	091FA
	37
	1-3/8
	16
	160

	246
	A
	176
	151FA
	113
	2-1/8
	38
	327

	
	B
	108
	091FA
	37
	1-3/8
	16
	160

	261
	A
	176
	171FA
	136
	2-1/8
	38
	350

	
	B
	108
	091FA
	37
	1-3/8
	16
	160

	271
	A
	176
	181FA
	136
	2-1/8
	38
	350

	
	B
	108
	091FA
	37
	1-3/8
	16
	160


Service Valves

Several styles of service valves are used on the 30GX/HX machines.

Discharge Service Valves

Discharge Service Valves are ball valves installed between the oil separator and the outdoor coil on the 30GX machines.  On the 30HXA, it is installed between the compressor and the oil separator.  On the 30HXC, it is installed between the compressor and the condenser.

Liquid Line Service Valves

Liquid Line Service Valves for earlier machines were angle valves.  This style of valve requires additional steps to maintain the refrigerant seal. 

For 30GX machines beginning with Serial Numbers 4901F, the angle valve was replaced by a ball valve.

Oil Line Service Valves

There is a single oil line service valve used on the 30HX machines located at the inlet to the external oil filter.  This service valve is an angle valve with a Roto-Loc connection.  The 30GX machines use this same style at the inlet to the external oil filter.  Additionally on the 30GX machines there is an angle valve at each compressor.

Suction Service Valves

Suction Service Valves are factory installed options for both the 30GX and 30HX machines.  This device is installed within the suction pipe between the cooler and compressor.  An actuator stem protruding from the suction pipe operates the valve.  An o-ring seal achieves refrigerant isolation.  The actuator opens the valve with a counter-clockwise rotation.  A clock-wise rotation will close the valve.  The actuator stem has a left-hand thread, locking nut.  The locking nut secures the actuator in the position desired.  

Beginning approximately 4801F, the suction service actuator and handle design changed.  

Transducers

The ComfortLink Control system uses 2 unique pressure transducers.  A low side pressure transducer, HK05YZ001 is used for the Economizer and Suction Pressure Transducers.  A high range transducer, HK05YZ002 or HK05YZ007 is used for the Discharge and Oil Pressure Transducers.   The HK05YZ007 transducers have a brass body for corrosion protection.

With the two different styles of the transducer, calibration is no longer required.  

Thermistors

The ComfortLink Control system uses a 5 k( @ 77 (F (25 (C) thermistor for the Entering Chilled Water Thermistor, Leaving Chilled Water Thermistor, Discharge Gas Thermistor, Outdoor Air Thermistor, and in Master/Slave parallel flow applications, the Lead/Lag Leaving Fluid Thermistor.

For Space Temperature reset, a 10 k( @ 77 (F (25 (C) thermistor is required.

For the above sensors, either voltage drop or resistance can be used to verify accuracy of the thermistors.

The compressor motor thermistors are also 5 k( @ 77 (F (25 (C) thermistors, but have a slightly different curve than the thermistors previously discussed.   A different temperature vs. resistance chart is required to verify the accuracy of the thermistor.  Voltage drop cannot be used to check accuracy for the compressor motor thermistors.

The thermistors are connected to the Main Base Board (MBB) with IDC (Insulation Displacement Connector) connections.  The tools required to make these connections are as follows:

	Manufacturer
	Part Number
	Description

	Tyco Electronics (Amp)
	58580-1
	Hand Tool with Terminating Head

	
	58074-1
	Hand Tool (included in 58580-1)

	
	58247-1
	Terminating Head (included in 58580-1)

	Ideal Industries
	45-165
	UTP/Coax Stripper


The cable stripper is easier to strip the gray jacket of the thermistor cable.  It is not required.

Water Analysis

To aid in the determination of a root cause for a cooler failure, it is recommended that a water sample be analyzed.  If the work is to be performed by an independent laboratory, the following items should be checked:

A water analysis consists of the following tests:

pH

Calcium, ppm as CaCO3
Magnesium, ppm as CaCO3
Iron, ppm

Chloride, ppm

Sulfate, ppm as SO3
M alkalinity, ppm as CaCO3
P alkalinity, ppm as CaCO3
Silica, ppm as SiO2
Nitrate, ppm as NO3
Suspended Solids, ppm

Appearance/Comments

Additional tests could include: 

Phosphate, ppm as PO4
Fluoride, ppm 

Boron, ppm

Sodium, ppm

Potassium, ppm 

Ammonia, ppm as NH4
Aluminum, ppm

Hydrogen Sulfide, ppm as H2S

Maintenance

Recommended Maintenance Schedule

The following are only recommended guidelines.  Job site conditions may dictate that maintenance schedules be performed more often than recommended.

Routine:

For 30GX machines with E-coat Condenser Coils:

· Check condenser coils for debris, clean as necessary

· Periodic clean water rinse, especially in coastal and industrial applications.

Every month:

· Check Sightglass Dry Eye for moisture.  If moisture is indicated, obtain and test an oil sample, change as necessary.  Check the chilled water loop for signs of refrigerant, which may indicate a cooler leak.

For 30GX machines with E-coat Condenser Coils:

· Check condenser coils for debris, clean as necessary

· Coil cleaning with Environmentally Sound Coil Cleaner.

Every 3 months:

For all machines:

· Check all refrigerant joints and valves for refrigerant leaks, repair as necessary

· Check oil filter pressure drops, replace as necessary

· Check chilled water flow switch operation
For 30GX machines:

· Check condenser coils for debris, clean as necessary

· Check condenser fan operation

Every 12 months:

For all machines:

· Check all electrical connections for tightness, tighten as necessary.

· Check calibration of all transducers for each circuit, recalibrate/replace as necessary

· Check accuracy of thermistors, replace if greater than ( 2 (F (1 (C)

· Obtain and test an oil sample, change as necessary

· Check cooler approach (Cooler Leaving Water Temperature – Saturated Suction Temperature), clean tubes if appropriate

· Check to be sure that the proper concentration of antifreeze is present in the chilled water loop

· Check to be sure that the proper amount of inhibitor is present in the chilled water loop.

· Check all refrigerant strainers and filter driers for pressure drops, replace/clean as necessary

· Check chilled water strainers, clean as necessary

For 30GX machines:

· Check cooler heater operation

For 30HXC machines:

· Check Condenser Water Regulating Valve operation, if equipped

· Check condenser approach (Saturated Condensing Temperature – Condenser Leaving Water Temperature), clean tubes if appropriate

· Check to be sure that the proper amount of inhibitor is present in the condenser water loop.

· Check condenser water strainers, clean as necessary

Recommended Spare Parts List

The following recommended spare parts list is divided into critical and recommended replacement parts.  Critical parts are components that, if they fail, will cause the equipment to stop functioning, or otherwise fail to deliver the required cooling capacity.  Without these parts, the machine cannot be made operational.  Recommended parts are components that, if they fail, could cause deterioration of the system performance.  If a recommended part fails, the system can be usually made somewhat functional, even if only partial operation, until the correct part can be obtained.  If the deterioration of the system performance is not acceptable by the customer, then the recommended, should be treated as critical parts.

Refer to RCD’s EPIC 2000 for the appropriate part number and quantity of parts for each machine.

In the Comments Section the following abbreviations are used:


PSN – Prior Serial Number


SSN – Starting Serial Number

30GXN,GXR Spare Parts List  

	30GXN,GXR Critical Parts:

	Part Number
	Description
	Comments

	HH79NZ029
	Thermistor
	

	HH83ZB001
	Circuit Breaker
	

	HN67LM103
	ComfortLink Compressor Protection (Full Current)
	See EPIC 2000 for appropriate part number.

	HN67LM104
	ComfortLink Compressor Protection (1/2-Current)
	See EPIC 2000 for appropriate part number.

	HR53VK120
	Switch
	

	HR81LG005
	Flow Switch, Paddle
	

	HR81LG015
	Flow Switch, Thermal Dispersion
	SSN: 1201F

	HT01BD121
	Transformer
	

	SC15
	Fuse
	

	30GT515217
	EXV Board
	w/o Software HK50AA026

	30HX501314
	Main Base Board
	w/o Software HK50AA029

	30HX501316
	Screw Compressor Board
	w/o Software HK50AA032

	853002-640
	Cooler Tube Plug Ring
	Do not plug any more than 10% of the total number of tubes.

	853103-1
	Cooler Tube Plug Pin
	Do not plug any more than 10% of the total number of tubes.


	30GXN,GXR Recommended Parts:

	Part Number
	Description
	Comments

	ADK305S
	Filter Drier
	

	EB51LZ221
	Pressure Relief Valve
	

	EB51LZ320
	Pressure Relief Valve
	

	EF19ZE024
	Solenoid Coil
	

	HK02ZA441
	High Pressure Switch
	

	HK05YZ001
	Transducer
	

	HK05YZ007
	Transducer
	

	HK50AA028
	Energy Management Module
	No software loaded

	HK50AA033
	Navigator
	

	HN52KC015
	Oil Pump Contactor
	230-3-50, 380/415-3-50 Machines Only

	HN52KC016
	Oil Pump Contactor
	208/230-3-60, 230-3-60, 

380-3-60, 460-3-60, 575-3-60 Machines Only

	HR46GN001
	MotorMaster III Controller
	If equipped (PSN 0802F)

	
	MotorMaster V Controller
	If equipped (SSN 0802F)

See EPIC 2000 for appropriate part numbers

	KC21AH005
	Tube Brush
	

	P903-1205
	Compressor Oil 
	5 gallons

	06NA660001
	Compressor Oil Solenoid Kit
	

	06NA660011
	Compressor Unloader Solenoid
	

	06NA660016
	Compressor Internal Oil Filter
	

	30GT660010
	EXV Motor Kit
	30GXN/R080-115, 220B, 240B,  Only

	30GX503303
	Oil Pump
	

	30GX504025
	Oil Level Switch
	

	30GX660002
	Liquid Level Sensor
	

	32GB401454
	Economizer Stepper Motor Assembly
	30GXN/R125-204, 220A, 225, 240A, 249-450 Only

	32GB401484
	Economizer O-ring Kit
	30GXN/R125-204, 220A, 225, 240A, 249-450 Only

	32GB660013
	EXV O-ring Kit
	30GXN/R080-115, 220B, 240B,  Only

	3-010-311
	Liquid Line Strainer Screen and Gasket
	

	S-4004UA
	External Oil Filter
	

	
	Compressors
	See EPIC 2000 for appropriate part numbers

	
	Compressor Contactor/Starter
	See EPIC 2000 for appropriate part numbers

	
	Fan Blades
	See EPIC 2000 for appropriate part numbers

	
	Fan Circuit Breaker
	See EPIC 2000 for appropriate part numbers

	
	Fan Contactor
	See EPIC 2000 for appropriate part numbers

	
	Fan Motor
	See EPIC 2000 for appropriate part numbers

	
	Fan Overload Contactor
	See EPIC 2000 for appropriate part numbers.  Used only on High Static Fan Options

	
	Fan Overload Heater
	See EPIC 2000 for appropriate part numbers. Used only on High Static Fan Options

	
	CCP Current Transformer
	See EPIC 2000 for appropriate part numbers


	30GXN,GXR Recommended Tools:

	Part Number
	Description
	Comments

	06NA660015
	Compressor Service Tool Kit
	


30HXA Spare Parts List  

	30HXA Critical Parts:

	Part Number
	Description
	Comments

	HH79NZ029
	Thermistor
	

	HH83ZB001
	Circuit Breaker
	

	HN67LM103
	ComfortLink Compressor Protection (Full Current)
	See EPIC 2000 for appropriate part number.

	HN67LM104
	ComfortLink Compressor Protection (1/2-Current)
	See EPIC 2000 for appropriate part number.

	HR53VK120
	Switch
	

	HR81LG005
	Flow Switch, Paddle
	

	HT01BD121
	Transformer
	

	SC15
	Fuse
	

	30GT515217
	EXV Board
	w/o Software HK50AA026

	30HX501314
	Main Base Board
	w/o Software HK50AA029

	30HX501316
	Screw Compressor Board
	w/o Software HK50AA032

	853002-640
	Cooler Tube Plug Ring
	Do not plug any more than  10% of the total number of tubes.

	853103-1
	Cooler Tube Plug Pin
	Do not plug any more than  10% of the total number of tubes.


	30HXA Recommended Parts:

	Part Number
	Description
	Comments

	ADK305S
	Filter Drier
	

	EB51LZ221
	Pressure Relief Valve
	

	EB51LZ320
	Pressure Relief Valve
	

	EF19ZE024
	Solenoid Coil
	

	HK02YB097
	Pressure Switch
	Fan Cycling Pressure Switch

	HK02ZA275
	High Pressure Switch
	

	HK05YZ001
	Transducer
	

	HK05YZ007
	Transducer
	

	HK50AA028
	Energy Management Module
	No software loaded

	HK50AA033
	Navigator
	

	HN52KC015
	Oil Pump Contactor
	230-3-50, 380/415-3-50 Machines Only

	HN52KC016
	Oil Pump Contactor
	208/230-3-60, 230-3-60, 

380-3-60, 460-3-60, 575-3-60 Machines Only

	KC21AH005
	Tube Brush
	

	P903-1205
	Compressor Oil 
	5 gallons

	06NA660001
	Compressor Oil Solenoid Kit
	

	06NA660011
	Compressor Unloader Solenoid
	

	06NA660016
	Compressor Internal Oil Filter
	

	30GT660010
	EXV Motor Kit
	30HXA076-146 Only

	30GX503303
	Oil Pump
	

	30GX504025
	Oil Level Switch
	

	30GX660002
	Liquid Level Sensor
	

	32GB401454
	Economizer Stepper Motor Assembly
	30HXA161-271 Only

	32GB401484
	Economizer O-ring Kit
	30HXA161-271 Only

	32GB660013
	EXV O-ring Kit
	30HXA076-146 Only

	3-010-310
	Liquid Line Strainer Screen and Gasket
	30HXA076-146 Only

S/N:  3400F-5100F

	3-010-311
	Liquid Line Strainer Screen and Gasket
	30HXA161-271 Only

	3-010-312
	Liquid Line Strainer Screen and Gasket
	30HXA076-146 Only

SSN: 5200F

	4004TA
	External Oil Filter
	

	
	Compressors
	See EPIC 2000 for appropriate part numbers

	
	Compressor Contactor/Starter
	See EPIC 2000 for appropriate part numbers

	
	CCP Current Transformer
	See EPIC 2000 for appropriate part numbers


	30HXA Recommended Tools:

	Part Number
	Description
	Comments

	06NA660015
	Compressor Service Tool Kit
	


30HXC Spare Parts List  

	30HXC Critical Parts:

	Part Number
	Description
	Comments

	HH79NZ029
	Thermistor
	

	HH83ZB001
	Circuit Breaker
	

	HN67LM103
	ComfortLink Compressor Protection (Full Current)
	See EPIC 2000 for appropriate part number.

	HN67LM104
	ComfortLink Compressor Protection (1/2-Current)
	See EPIC 2000 for appropriate part number.

	HR53VK120
	Switch
	

	HR81LG005
	Flow Switch, Paddle
	

	HT01BD121
	Transformer
	

	SC15
	Fuse
	

	30GT515217
	EXV Board
	w/o Software HK50AA026

	30HX501314
	Main Base Board
	w/o Software HK50AA029

	30HX501316
	Screw Compressor Board
	w/o Software HK50AA032

	853002-640
	Cooler and Condenser Tube Plug Ring
	Do not plug any more than  10% of the total number of tubes.

	853103-1
	Cooler and Condenser Tube Plug Pin
	Do not plug any more than  10% of the total number of tubes.


	30HXC Recommended Parts:

	Part Number
	Description
	Comments

	ADK305S
	Filter Drier
	

	EB51LZ221
	Pressure Relief Valve
	

	EF19ZE024
	Solenoid Coil
	

	HK02ZA440
	High Pressure Switch
	

	HK05YZ001
	Transducer
	

	HK05YZ007
	Transducer
	

	HK50AA028
	Energy Management Module
	No software loaded

	HK50AA033
	Navigator
	

	HN52KC015
	Oil Pump Contactor
	230-3-50, 380/415-3-50 Machines Only

	HN52KC016
	Oil Pump Contactor
	208/230-3-60, 230-3-60, 

380-3-60, 460-3-60, 575-3-60 Machines Only

	KC21AH005
	Tube Brush
	

	P903-1205
	Compressor Oil 
	5 gallons

	06NA660001
	Compressor Oil Solenoid Kit
	

	06NA660011
	Compressor Unloader Solenoid
	

	06NA660016
	Compressor Internal Oil Filter
	

	30GT660010
	EXV Motor Kit
	30HXC076-146 Only

	30GX503303
	Oil Pump
	

	30GX660002
	Liquid Level Sensor
	

	30HX502414
	Oil Level Switch
	

	32GB401454
	Economizer Stepper Motor Assembly
	30HXC161-271 Only

	32GB401484
	Economizer O-ring Kit
	30HXC161-271 Only

	32GB660013
	EXV O-ring Kit
	30HXC076-146 Only

	3-010-310
	Liquid Line Strainer Screen and Gasket
	30HXC076-146 Only

S/N:  3400F-5100F

	3-010-311
	Liquid Line Strainer Screen and Gasket
	30HXC161-271 Only

	3-010-312
	Liquid Line Strainer Screen and Gasket
	30HXC076-146 Only

SSN: 5200F

	4004TA
	External Oil Filter
	

	
	Compressors
	See EPIC 2000 for appropriate part numbers

	
	Compressor Contactor/Starter
	See EPIC 2000 for appropriate part numbers

	
	CCP Current Transformer
	See EPIC 2000 for appropriate part numbers


	30HXC Recommended Tools:

	Part Number
	Description
	Comments

	06NA660015
	Compressor Service Tool Kit
	

	AW24
	¾” Allen Wrench
	Snap-On Part Number


� EMBED PBrush  ���





























Confidential

04/18/02

Confidential

02/26/03


_1055531769.unknown

_1060595641.xls
Chart1

		0

		4

		20



4-20 mA Signal

4-20 mA Signal

Reset Amount deg. F

0

0

10



Sheet1

		4-20 mA Signal		Reset Amount, deg. F

		0		0

		4		0

		20		10






_1060600179.xls
Chart1

		4		4		4

		20		10.4		4.5

				17.71		17.71

				20		20



Control Equation

Fresh Water Control

Brine Control

4-20 mA Signal

Temperature Set Point (F)

10

38

12

80

38

12

70

70

70

70



Sheet1

		4-20 mA Remote Temperature Signal		Temperature Set Point		4-20 mA Remote Temperature Signal		Temperature Set Point		4-20 mA Remote Temperature Signal		Temperature Set Point

		4		10		4		38		4		12

		20		80		10.4		38		4.5		12

						17.71		70		17.71		70

						20		70		20		70

		4		-12.2222222222		4		3.3333333333		4		-11.1111111111

		20		26.6666666667		10.4		3.3333333333		4.5		-11.1111111111

						17.71		21.1111111111		17.71		21.1111111111

						20		21.1111111111		20		21.1111111111






_1072077903.unknown

_1060596675.xls
Chart1

		0		0

		2		2

		10		10



Building Load

Reset Amount

Temperature Difference (EWT-LWT) deg. F

Reset Amount deg. F

Temperature Difference (EWT-LWT) deg. F

Reset Amount deg. F

% Building Load

10

0

10

20

0

100



Sheet1

		Temperature Difference (EWT-LWT) deg. F		Reset Amount deg. F		Building Load

		0		10		0

		2		10		20

		10		0		100






_1058877567.unknown

_1058877848.unknown

_1052836854.unknown

_1055531728.unknown

_1052836963.unknown

_1052835425.unknown

_1044872574

