

BULLETIN

Carrier Corporation


North American Operations



	Number:
	SMB000075    
	Date:
	11/06/00
	Supersedes:
	New
	Date:
	

	Title:
	30/38/09 High Pressure Trips  

	Category:
	Policy
	Termination Date:
	12/31/01

	Author:
	Douglas Bates
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC: 30GTN/GTR/GUN/GUR 040-210, 230A, 230B, 245A, 245B, 255A, 255B, 270A, 270B,                                  290A, 290B, 315A, 315B, 330A, 330B, 360A, 360B, 390A, 390B, 420A, 420B 

          09DK 054-094

          38AH 044-134

BDP:  None

	
	


Situation: 

Several occurrences of high-pressure switch trips have been reported as a result of the baffles not being installed between the condenser fans in production of all 30GTN/GTR/GUN/GUR040-210 Chillers, 09DK054-094 Condensers and 38AH 044-134 Condensing Units.  With these baffles removed, air is being re-circulated and short-cycled through the fans that are not running resulting in insufficient air being drawn through the condenser coils.  Units with serial numbers between 1600F94483 and 3200F22578 are affected.

Solution:

The units will be modified in the fan staging control circuit to overcome the lack of airflow through the coil.

On the affected units, the fan staging control circuit will be changed. Instructions with a list of kits for the various models are attached. The kits will include parts, instructions and replacement label diagrams to overlay the originals.

On units with MotorMaster III, there will be additional relays and rewiring of the MMIII.

Factory Action:

On units with serial numbers beginning 3300F, the baffles have been installed during production.  There have been a number of units reworked at the factory prior to shipment.  Attached is a list of units that have already been modified at the factory, and are not covered by this SMB.  Also attached are copies of the instructions for use by service managers.

Units already modified at the factory
	Model #
	Serial #
	
	Model #
	Serial #
	
	Model #
	Serial #
	


	09DK-054---501
	3000F19242
	

	09DK-054---501
	3100F20493
	

	09DK-054---501
	3200F22510
	

	09DK-054---501
	3200F22558
	

	09DK-054---601
	1600F94564
	

	09DK-054---601
	2300F07647
	

	09DK-054---601
	2300F07669
	

	09DK-054---601
	2400F09320
	

	09DK-054---601
	2600F12903
	

	09DK-054---601
	3000F19142
	

	09DK-054---601
	3000F19161
	

	09DK-064---501
	3200F22562
	

	09DK-064---601
	2900F16648
	

	09DK-064---601
	3000F19180
	

	09DK-074---501
	3000F19163
	

	09DK-074---501
	3200F22471
	

	09DK-074---601
	3100F20509
	

	09DK-084---501
	3200F22473
	

	09DK-084---601
	3100F20453
	

	09DK-084---601
	3200F22514
	

	09DK-084---601
	3200F22516
	

	09DK-094---601
	2300F07628
	

	09DK-094---601
	3100F20469
	

	09DK-094---601
	3100F20486
	

	30GTN045---5--KA
	3200F22552
	

	30GTN060--E621KA
	3000F19234
	

	30GTN070---5
	2400F09402
	

	30GTN090---620KA
	2900F16705
	

	30GTN090---6--KA
	2700F14744
	

	30GTN090--K6--KA
	3100F20477
	

	30GTN090--K6--KA
	3100F20516
	

	30GTN100---5--KA
	3200F22518
	

	30GTN100---5--KA
	3200F22564
	

	30GTN100--K6--KA
	3000F19249
	

	30GTN100-S-6--KA
	3200F22541
	

	30GTN110---5--KA
	1800F97652
	

	30GTN110---5--KA
	1800F97677
	

	30GTN110---5--KA
	1900F01399
	

	30GTN110---5--KA
	2000F02777
	

	30GTN110---5--KA
	2400F09324
	

	30GTN110---5--KA
	2400F09347
	

	30GTN110---5--KA
	2900F16651
	

	30GTN110---5--KA
	2900F16669
	

	30GTN110---5--KA
	2900F16704
	

	30GTN110---5--KA
	3000F19171
	

	30GTN110---5--KA
	3000F19246
	

	30GTN110---6
	2200F05975
	

	30GTN110---6--KA
	3200F22563
	

	30GTN110--K6--KA
	3100F20495
	

	30GTN130---5--KA
	3100F20474
	

	30GTN130---5--KA
	3100F20514
	

	30GTN130---6--KA
	3000F19152
	

	30GTN130---6--KA
	3000F19185
	

	30GTN130---6--KA
	3000F19243
	

	30GTN130---6--KA
	3100F20451
	

	30GTN130---6--KA
	3100F20492
	

	30GTN130---923
	1700F95998
	

	30GTN130---923
	1700F96015
	

	30GTN130---923
	1700F96055
	

	30GTN130--K6--KA
	3100F20479
	

	30GTN130--K6--KA
	3100F20536
	

	30GTN150---6--KA
	2900F16700
	

	30GTN150---6--KA
	3000F19148
	

	30GTN150---6--KA
	3000F19205
	

	30GTN150---6--KA
	3000F19207
	

	30GTN150---6--KA
	3100F20454
	

	30GTN150--K6--KA
	3200F22535
	

	30GTN170---6--KA
	2000F02758
	

	30GTN170---6--KA
	2000F02813
	

	30GTN170---6--KA
	2000F02836
	

	30GTN170---6--KA
	2100F04249
	

	30GTN170---6--KA
	2100F04288
	

	30GTN170---6--KA
	2100F04294
	

	30GTN170---6--KA
	2100F04314
	

	30GTN170---6--KA
	2200F05963
	

	30GTN170---6--KA
	2200F05999
	

	30GTN170-E-6--KA
	2000F02761
	

	30GTN190---5--KA
	2200F06024
	

	30GTN190---6
	3100F20508
	

	30GTN190---6--KA
	1600F94542
	

	30GTN190---6--KA
	1700F96012
	

	30GTN190---6--KA
	1900F01297
	

	30GTN190---6--KA
	2000F02791
	

	30GTN190---6--KA
	2000F02801
	

	30GTN190---6--KA
	2000F02826
	

	30GTN190---6--KA
	2100F04284
	

	30GTN190---6--KA
	2100F04303
	

	30GTN190--K6--KA
	2900F16707
	

	30GTN210---521KA
	3000F19203
	

	30GTN210---5--KA
	1700F96035
	

	30GTN210---5--KA
	2000F02772
	

	30GTN210---5--KA
	2000F02810
	

	30GTN210---5--KA
	3000F19182
	

	30GTN210---6--KA
	2000F02770
	

	30GTN210---6--KA
	2900F16678
	

	30GTN210---6--KA
	3100F20448
	

	30GTN210---6--KA
	3100F20466
	

	30GTN210---6--KA
	3200F22489
	

	30GTN210--K6--KA
	2700F14772
	

	30GTN210--K6--KA
	2900F16643
	

	30GTN210--K6--KA
	3100F20446
	

	30GTR070---5--KJ
	1900F01314
	

	30GTR130---1--CZ
	2000F02775
	

	30GTR190--K5--KB
	2300F07699
	

	30GUR050--E523AL
	2900F16618
	

	38AH-044---501
	2600F12862
	

	38AH-044---501
	3200F22530
	

	38AH-044---501
	3200F22548
	

	38AH-044---603
	3200F22499
	

	38AH-044---603
	3200F22520
	

	38AH-044---603
	3200F22546
	

	38AH-054---61090
	2900F16716
	

	38AH-054--C16623
	2700F14736
	*

	38AH-054--C16623
	2700F14776
	*

	38AH-054--C16623
	2700F14793
	*

	38AH-054--C16623
	2700F14795
	*

	38AH-064---501
	3200F22465
	

	38AH-064---501
	3200F22512
	

	38AH-064---501
	3200F22559
	

	38AH-064---601
	3000F19206
	

	38AH-064---601
	3200F22467
	

	38AH-064---601
	3200F22533
	

	38AH-064---601
	3200F22560
	

	38AH-074---501
	2100F04329
	

	38AH-074---501
	2400F09339
	

	38AH-074---501
	2400F09387
	

	38AH-074---601
	2900F16642
	

	38AH-074---601
	3000F19165
	

	38AH-074---601
	3000F19184
	

	38AH-074---601BA
	2000F02804
	

	38AH-074---601BA
	2000F02827
	

	38AH-084---501
	2000F02753
	

	38AH-084---501
	2100F04285
	

	38AH-084---603
	3200F22466
	

	38AH-084---603
	3200F22492
	

	38AH-084--C16623
	2700F14740
	*

	38AH-084--C16623
	2700F14763
	*

	38AH-084--C16623
	2700F14782
	*

	38AH-084--C16623
	2700F14800
	*

	38AH-094---601
	1900F01296
	

	38AH-104---601BA
	2500F11173
	


* Units were reworked with baffles installed.

Field Action:

The following list of kits have been created to modify the affected units.  The kits contain the appropriate wires, relays, pressure switches, revised label diagrams and instructions required to rework one unit.  The kits are available from RCD.

	Model #
	Parts Kit #

	38AH 044-064, 124A, 124B (all voltages),
	38AH400283

	38AH 074-104, 134B (-6,-9,-1)
	38AH400283

	38AH 074-104, 134B (-5)
	38AH400285

	09DK – ALL
	09DK400507

	30GTN/GTR/GUN/GUR 040-090, 230B, 245B (all voltages)
	30GT415709

	30GTN/GTR/GUN/GUR 100-110, 255B, 270B, 290B, 315B(all voltages)
	30GT415711

	30GTN/GTR/GUN/GUR130-420, 230A, 245A, 255A, 270A, 290A, 315A, (all voltages)
	30GT415713


For units equipped with MotorMaster III, the following relays will also need to be ordered:

	MotorMaster III 60 Hz
	HN61KX011

	MotorMaster III 50 Hz
	HN61KX010


Policy:

30GTN/GTR/GUN/GUR 040-090 w/out MotorMaster-

30GTN/GTR/GUN/GUR 100-210 with MotorMaster-

09DK054-094 and 38AH-044-134 All voltages with MotorMaster-

For the first machine on a site, we will allow parts and one and one-half (1.5) hours of labor only.  For additional units on the same site, parts and one (1) hour of labor only will be allowed.

30GTN/GTR/GUN/GUR 040-090 with MotorMaster-


For the first machine on a site, we will allow parts and two (2) hours of labor only.  For additional units on the same site, parts and one and one-half (1.5) hours of labor only will be allowed.

30GTN/GTR/GUN/GUR 100-210 w/out MotorMaster-

09DK054-094 and 38AH-044-134 All voltages w/out MotorMaster-

For the first machine on a site, we will allow parts and one (1) hour of labor only.  For additional units on the same site, parts and one-half (1/2) hour of labor only will be allowed.

This policy expires 12/31/01

Mail Keys:  2.14, 2.19, 2.27A, 2.30, 2.32, 2.32I, 2.40A, 2.40I, 2.40M, 5.25A, 5.25G


_988694773.doc
�



�
















