30RA IFM Flow Switch – Field Replacement

This kit applies to flow switch replacement on units prior to date code 2907.  This kit includes an electronic flow dispersion switch to replace the mechanical paddle switch used previously.

Kit Contents

Flow Switch – 00PPN500001800A
Adapter – 30RA501461
1” NPT Plug

Cable, Flow Switch – 30RA401551
[image: image1.jpg]


[image: image2.jpg]



IFM Switch



M & M Paddle Switch

Installation Procedure

Remove water from unit.

Remove M & M paddle switch from return water line in unit.  Plug hole with 1” NPT plug.

Determine location for new flow switch.


On non-pump units, locate new sensor 6 to 12” upstream of old switch location.

On pump units, locate new sensor in any upstream location on return pipe.

Drill 39/64” (.614/.604”) hole in pipe at the 2:00 to 3:00 o’clock position.  Remove pipe to flush drill debris.

Braze adapter into pipe.

Install sensor using pipe sealant that is resistant to glycol.  Orient sensor so LEDs are visible from access panel.

Connect cable to switch.  Hand tighten only.  Route cable to main control box.  Connect wires as shown on diagram shown in the supplement and marked on cable.

Fill system with water and verify operation per manual supplement attached.

