	Device
	Circuit Board Part Number
	(LEN) Resistance between Pins / Connector

	
	With Software
	Vendor
	Pins 1(+) to 3(-)
	Pins 1(+) to 2(G)
	Pins 2(G) to 3(-)

	MBB

Main Base Board
	00PSN500038100
	CEPL1303403-02
	8.6K Ω
J9A,B,C
	7.8K Ω

J9A,B,C
	1.1K Ω

J9A,B,C

	SPM

Scroll

Compressor Board
	32GB500362E
	CEPL130537-02
	70K Ω
JP1 
	40K Ω
JP1
	40K Ω
JP1

	AUX 1

Fan Board
	32GB500442E
	CEPL130567-02
	29K Ω 

J9
	16K Ω
J9
	13.5K Ω
J9

	AUX 2 

Fan Board
	32GB500432E
	CEPL130568-02
	29K Ω 

J9
	16K Ω
J9
	13.5K Ω
J9

	EMM

Energy Management Module
	00PSN500038300
	CEPL130355-02

32GB500372E
	5.0K Ω
J9A
	4.0K Ω
J9A
	1.0K Ω
J9A

	EXV

EXV Board
	00PSN500038200
	CEPL130415-02

32GB500422E
	40K Ω
J4
	20K Ω
J4
	20K Ω
J4

	
	
	
	270K Ω *
J4
	11M Ω *
J4
	11M Ω *
J4

	STDU

Scrolling Marquee Display
	HK50AA031
	CEPL130347-01
	40K Ω
J1
	20K Ω

J1
	20K Ω

J1


	Device
	Circuit Board Part Number
	(CNN) Resistance between Pins / Connector

	
	With Software
	Vendor
	Pins (+) to (-)
	Pins (+) to (G)
	Pins (G) to (-)

	MBB

Main Base Board
	00PSN500038100
	CEPL130403-02
	44K Ω
J12
	22K Ω

J12
	22K Ω

J12


* Starting serial number 0607N

If resistance is less than half of indicated values the board should be considered bad.

30RB LEN Resistance Table 

