Recommended Spare Parts List XE "Recommended Spare Parts List" 
The following recommended spare parts list is divided into critical and recommended replacement parts.  Critical parts are components that, if they fail, will cause the equipment to stop functioning, or otherwise fail to deliver the required cooling capacity.  Without these parts, the machine cannot be made operational.  Recommended parts are components that, if they fail, could cause deterioration of the system performance.  If a recommended part fails, the system can be usually made somewhat functional, even if only partial operation, until the correct part can be obtained.  If the deterioration of the system performance is not acceptable by the customer, then the recommended, should be treated as critical parts.

Refer to RCD’s EPIC 2000 for the appropriate part number and quantity of parts for each machine.

In the Comments Section the following abbreviations are used:


PSN – Prior Serial Number


SSN – Starting Serial Number

30XA Series A Spare Parts List 

Serial Number Range:  0205Q-

	30XA Series A - Critical Parts

	Part Number
	Description
	Comments

	00PPN500001800A
	Chilled Water Flow Switch
	

	MT0350D
	Control Transformer
	TRAN1 and TRAN2.  

	00PSN500038200
	EXV Board w/Software
	32GB500422-E w/o Software

	32GB500442-E
	Fan Board
	This board replaces the AUX2 board, 32GB500432-E (Critical 080)

	ATQR5
	Fuse, Control Transformer
	FU1, FU2, FU4, FU5, FU11, and FU12.  

	FNM20
	Fuse, Control Transformer
	FU3 and FU6

	B500J13RKF
	Isolation Transformer
	TRAN3.  See EPIC 2000 for appropriate Part Numbers.

	00PSN500160701A
	Main Base Board w/Software
	

	00PPG000008105A
	Thermistors
	Entering Water Temperature,

Leaving Water Temperature, Outdoor Ambient Temperature, and Suction Gas Temperature

	HH83XB001
	Transformer, Circuit Breaker (3.2 Amps)
	CB1 to CB12

	853002-640
	Cooler and Condenser Tube Plug Ring
	Do not plug any more than 10% of the total number of tubes.

	853103-1
	Cooler and Condenser Tube Plug Pin
	Do not plug any more than 10% of the total number of tubes.


	30XA Series A - Recommended Parts

	Part Number
	Description
	Comments

	
	
	

	00PPN500001300A
	Capacity Control Solenoid Coil
	Load/Unload Solenoid

	P903-2301
	Compressor Oil
	1 gallon

	
	Compressors
	See EPIC 2000 for appropriate Part Numbers.

	
	Compressor Circuit Breaker
	See EPIC 2000 for appropriate Part Numbers.

	
	Compressor Contactor
	See EPIC 2000 for appropriate Part Numbers.

	
	Compressor Auxiliary Contacts – Normally Open
	Normally Open Contact – Used on Wye-Delta Starters only.  See EPIC 2000 for appropriate Part Numbers.

	
	Compressor Auxiliary Contacts – Normally Closed
	Normally Closed Contact – Used on Wye-Delta Starters only.  See EPIC 2000 for appropriate Part Numbers.

	
	Compressor Starter Mechanical Interlock
	Used on Wye-Delta Starters only.  See EPIC 2000 for appropriate Part Numbers

	
	Compressor Contactor Adapter
	Used on Wye-Delta Starters only.  See EPIC 2000 for appropriate Part Numbers

	00PSG000114700A
	Compressor Protection Module (CPM)
	PSN:

Without Software:  CEPL130602-01

	
	Compressor Current Transformer
	See EPIC 2000 for appropriate Part Numbers

	00PPG000030900A
	Discharge Isolation Valve
	

	3RH11221AB00
	Discharge Isolation Valve Relay
	

	HK30ZZ001
	EXV Stepper Motor
	

	32GB500442-E
	Fan Board
	This board replaces the AUX2 board, 32GB500432-E (Recommended 160-390)

	00PSG000000101A
	Fan Prop
	

	
	Fan Circuit Breaker
	See EPIC 2000 for appropriate Part Numbers.

	
	Fan Motor
	See EPIC 2000 for appropriate Part Numbers.

	
	Fan Motor Contactor
	See EPIC 2000 for appropriate Part Numbers.

	KH29MD060
	Filter Drier Core
	See EPIC 2000 for quantities.

	EK41JK101
	Fusible Plug
	(1) per circuit, Liquid Line

	EK41JK202
	Fusible Plug
	Economizer Assembly (090-500)

	00PPG000011300A
	High Pressure Switch
	(1) per circuit

	
	Low Ambient Head Pressure Controller
	See EPIC 2000 for appropriate Part Numbers.

	00PPG000012800A
	Oil Filter
	(1) per circuit

	00PPG000011400A
	Oil Level Switch
	(1) per circuit

	00PPG000011600A
	Oil Solenoid Coil
	(1) per circuit

	00PPG000012000A
	Pressure Transducer, High
	(2) per circuit, (Discharge and Oil Pressure)

	00PPG000012100A
	Pressure Transducer, Low
	(2) per circuit, (Suction and Economizer Pressure)

	EB51LZ221
	Relief Valve
	(1) per circuit. Cooler


The following Recommended Tools List is for Service Offices only.  This is not intended for all sites.

	30XA Recommended Tools:

	Part Number
	Description
	Comments

	06TT660041
	Compressor Service Tool Kit
	

	30GX680016
	Direct Download Cable
	Cable Connection for bench top software downloads using SmartLoader.

	30GX680005
	ComfortLink Power Cube
	Power Cube with Connection for bench top software downloads using SmartLoader.



- 2 -
2/25/05


