
30XA080-500

Controls, Start-Up, Operation, Service and Troubleshooting

 XE "Safety considerations" SAFETY CONSIDERATIONS

Installing, starting up, and servicing this equipment can be hazardous due to system pressures, electrical components, and equipment location (roof, elevated structures, etc.).  Only trained, qualified installers and service mechanics should install, start up, and service this equipment.   When working on this equipment, observe precautions in the literature, and on tags, stickers, and labels attached to the equipment, and any other safety precautions that apply.  Follow all safety codes.  Wear safety glasses and work gloves.  Use care in handling, rigging, and setting this equipment, and in handling all electrical components.

	WARNING

	Electrical shock can cause personal injury and death.  Shut off all power to this equipment during installation and service.  There may be more than one disconnect switch. Tag all disconnect locations to alert others not to restore power until work is completed.


	WARNING

	DO NOT VENT refrigerant relief valves within a building.  Outlet from relief valves must be vented in accordance with the latest edition of ANSI/ASHRAE (American National Standards Institute/American Society of Heating, Refrigeration and Air Conditioning Engineers) 15 (Safety Code for Mechanical Refrigeration). The accumulation of refrigerant in an enclosed space can displace oxygen and cause asphyxiation. Provide adequate ventilation in enclosed or low overhead areas. Inhalation of high concentrations of vapor is harmful and may cause heart irregularities, unconsciousness or death.  Misuse can be fatal.  Vapor is heavier than air and reduces the amount of oxygen available for breathing.  Product causes eye and skin irritation.  Decomposition products are hazardous.


	WARNING

	DO NOT attempt to unbraze factory joints when servicing this equipment.  Compressor oil is flammable and there is no way to detect how much oil may be in any of the refrigerant lines.  Cut lines with a tubing cutter as required when performing service.  Use a pan to catch any oil that may come out of the lines and as a gage for how much oil to add to system.  DO NOT re-use compressor oil.


	CAUTION

	This unit uses a microprocessor-based electronic control system.  Do not use jumpers or other tools to short out components, or to bypass or otherwise depart from recommended procedures.  Any short-to-ground of the control board or accompanying wiring may destroy the electronic modules or electrical components.


	CAUTION

	To prevent potential damage to heat exchanger tubes, always run fluid through heat exchanger when adding or removing refrigerant charge. Use appropriate anti-freeze solutions in cooler fluid loop to prevent the freezing of heat exchanger, and/or interconnecting piping when the equipment is exposed to temperatures below 32 F (0 °C). Proof of flow switch are factory installed on all models. Do NOT remove power from this chiller during winter shutdown periods without taking precaution to remove all water from heat exchanger . Failure to properly protect the system from freezing may constitute abuse and may void warranty.


	CAUTION

	Compressors require specific rotation. Test condenser fan(s) first to ensure proper phasing. Swap any two incoming power leads to correct condenser fan rotation before starting any other motors. Operating the unit without testing the condenser fan(s) for proper phasing could result in equipment damage.


	CAUTION

	Refrigerant charge must be removed slowly to prevent loss of compressor oil that could result in compressor failure.


	

	


GENERAL

This publication contains Controls, Operation, Start-Up, Service and Troubleshooting information for the 30XA080-500 air-cooled liquid chillers with electronic controls.  These chillers are equipped with ComfortLink™ controls and electronic expansion valves.






	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	



 XE "Manual:Conventions used" Conventions Used in This Manual - The following conventions for discussing configuration points for the local display Navigator will be used in this manual.
Point names will be written with the Mode name first, then any submodes, then the point name, each separated by an arrow symbol ((. Names will also be shown in bold and italics. As an example, the IAQ Economizer Override Position which is located in the Configuration mode, Indoor Air Quality Configuration sub-mode, and the Air Quality Set Points sub-sub-mode, would be written as Configuration(IAQ(IAQ.SP(IQ.O.P.

This path name will show the user how to navigate through the local display to reach the desired configuration. The user would scroll through the modes and submodes using the [↑] and [↓] keys. The arrow symbol in the path name represents pressing [enter] to move into the next level of the menu structure.

When a value is included as part of the path name, it will be shown at the end of the path name after an equals sign. If the value represents a configuration setting, an explanation will be shown in parenthesis after the value. As an example, Con​figuration(IAQ(AQ.CF(IQ.A.C = 1 (IAQ Analog Input).

Pressing the [escape] and [enter] keys simultaneously will scroll an expanded text description of the point name across the display. The expanded description is shown in the local display tables but will not be shown with the path names in text.

The CCN point names are also referenced in the local display tables for users configuring the unit with CCN software instead of the local display. The CCN tables are located in Appendix B of the manual.

 XE "Controls" cONTROLS

 XE "Controls:General" General — The 30XA air-cooled liquid chillers contain the ComfortLink™ electronic control system that controls and monitors all operations of the chiller.  The control system is composed of several components as listed in the sections below.  All machines have at the very least a Main Base Board (MBB), Navigator, EXV Board, Fan Board, one Compressor protection (CPM) per compressor, Emergency Off Switch, a Remote Contact-Off-Enable Switch .
 XE "Controls:Main Base Board" Main Base Board (MBB) - The MBB is the heart of the ComfortLink control system. See Fig. 1. It contains the major portion of operating software and controls the operation of the machine.  The MBB continuously monitors input/output channel information received from its inputs and from all other modules.  The MBB receives inputs from status and feedback switches, pressure transducers and thermistors.  The MBB also controls several outputs. Some inputs and outputs to control the machine are located on other boards, but are transmitted to or from the MBB via the internal communications bus.  Information is transmitted between modules via a 3-wire communication bus or LEN (Local Equipment Network).  The CCN (Carrier Comfort Network) bus is also supported. Connections to both LEN and CCN buses are made at TB3.  For a complete description of board inputs and outputs and their channel identifications, see the Table 2. 

[image: image1.png]LOGATION OF
SERIAL NUMBER

Fig. 1 — Main Base Board





Table 2 –  XE "Controls:Main Base Board inputs and outputs" Main Base Board Inputs and Outputs

	Main Base Board

	Used on:  30XA080-500

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	MBB-J1, MBB-J1A, MBB-J1B

	
	
	11
	

	
	
	12
	

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	MBB-J9A, MBB-J9B, MBB-J9C

	
	
	+
	

	
	
	G
	

	
	
	-
	

	Carrier Communication

Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	MBB-J12

	
	
	+
	

	
	
	G
	

	
	
	-
	

	Input
	Description
	I/O Type
	Scrolling Marquee

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	CWFS
	Chilled Water Flow Switch
	Switch
	INPUTS(GEN.I(LOCK
	MBB-J5B-CH17

	
	
	
	
	17
	

	Demand Limit SW1
	Demand Limit Switch #1
	Switch
	INPUTS→GEN.I→DLS1
	MBB-J4-CH13

	
	
	
	
	
	

	
	
	
	
	
	

	DPTA
	Circuit A Discharge Pressure Transducer
	Pressure Transducer
	PRESSURES→PRC.A→DP.A
	MBB-J7A-CH6

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S
	Signal

	
	
	
	
	R
	-, Return

	DPTB
	Circuit B Discharge Pressure Transducer
	Pressure Transducer
	PRESSURES→PRC.B→DP.B
	MBB-J7C-CH8

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S
	Signal

	
	
	
	
	R
	-, Return

	DUAL
	Dual Chiller LWT Thermistor
	5k Thermistor
	TEMPERATURES→UNIT→CHWS
	MBB-J6-CH3

	
	
	
	
	R
	

	
	
	
	
	
	

	Dual Set Point
	Dual Set Point Input
	Switch
	INPUTS→GEN.I→DUAL
	MBB-J4-CH12

	
	
	
	
	
	

	
	
	
	
	
	

	EWT
	Entering Water Thermistor
	5k Thermistor
	TEMPERATURES→UNIT→EWT
	MBB-J6-CH2

	
	
	
	
	R
	

	
	
	
	
	
	

	LWT
	Leaving Water Thermistor
	5k Thermistor
	TEMPERATURES→UNIT→LWT
	MBB-J6-CH1

	
	
	
	
	R
	

	
	
	
	
	
	

	OAT
	Outdoor Air Thermistor
	5k Thermistor
	TEMPERATURES→UNIT→OAT
	MBB-J6-CH4

	
	
	
	
	R
	

	
	
	
	
	
	

	PMP1

PMP2
	Pump #1 Interlock

Pump #2 Interlock
	Switch
	INPUTS→GEN.I→PUMP
	MBB-J5C-CH18

	
	
	
	
	18
	

	
	
	
	
	C
	

	PMPI
	External Chilled Water Pump Interlock
	Switch
	INPUTS→GEN.I→LOCK
	MBB-J4-CH15A

	
	
	
	
	
	

	
	
	
	
	
	

	SPTA
	Circuit A Suction Pressure Transducer
	Pressure Transducer
	PRESSURES→PRC.A→SP.A
	MBB-J7B-CH7

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S
	Signal

	
	
	
	
	R
	-, Return

	SPTB
	Circuit B Suction Pressure Transducer
	Pressure Transducer
	PRESSURES→PR.B→SP.B
	MBB-J7D-CH9

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S
	Signal

	
	
	
	
	R
	-, Return

	Remote Contact-Off-Enable
	Unit Status
	Switch
	INPUTS→GEN.I→ONOF
	MBB-J4-CH11

	
	
	
	
	
	

	
	
	
	
	
	

	Output
	Description
	I/O Type
	Scrolling Marquee

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	ALM R
	Alarm Relay
	Relay
	OUTPUTS→GEN.O→ALRM
	MBB-J3-CH24

	
	
	
	
	
	

	
	
	
	
	
	

	ALT R
	Alert Relay
	Relay
	OUTPUTS→GEN.O→ALRT
	MBB-J3-CH25

	
	
	
	
	
	

	
	
	
	
	
	

	CL-HT
	Cooler Heater
	Contactor
	OUTPUTS→GEN.O→CO.HT
	MBB-J2B-CH21

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	MBB-J2C-CH22

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	MBB-J2C-CH23

	
	
	
	
	
	

	
	
	
	
	
	

	ISV A
	Isolation Valve A
	Contactor
	OUTPUTS→GEN.O→BLV.A
	MBB-J2A-CH19

	
	
	
	
	
	

	
	
	
	
	
	

	        ISV B
	Isolation Valve B
	Contactor
	OUTPUTS→GEN.O→BLV.B
	MBB-J2A-CH20

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


 XE "Controls:Scroll Protection Module (SPM)" Compressor Protection Module (CPM) —There is one CPM per compressor and it is responsible for controlling its compressor.  The device controls the compressor contactors, oil solenoid, load/unload solenoid, motor cooling solenoid(080 only) and the oil separator  heater.  It also monitors the compressor motor temperature, high pressure switch, oil level switch, discharge gas temperature, Oil pressure transducer, motor current, MTA setting and economizer pressure transducer.  The CPM responds to commands from the MBB and sends the MBB (Main Base Board) the results of the channels it monitors via the LEN (Local Equipment Network). See Table 3. Figure below
[image: image2.png]mmmmmmmmmm
OOOOOOOOOO

o

Bl

OlFag

]





Table 3 –  XE "Controls:Scroll Protection Module Inputs and Outputs" Compressor Protection Module Inputs and Outputs*

	Scroll Protection Module

	Address
	          1            2                3                   4    

A     OFF       OFF        OFF             OFF        

B     OFF       OFF        ON               OFF         

C     OFF       OFF        OFF             ON        



	Used on: 
	A All Units

B All Units

C (400-500)

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	CPM-x-J1

	
	
	11
	24 VAC

	
	
	12
	GROUND

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	CPM-x-J12

	
	
	1
	+

	
	
	2
	G

	
	
	3
	-

	
	
	CPM-x-J12

	
	
	1
	+

	
	
	2
	G

	
	
	3
	-

	Input
	Description
	I/O Type
	Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	HPS-x
	Circuit x High Pressure Switch
	Switch
	Not Available
	CPM-x-J7-CH05

	
	
	
	
	1
	

	
	
	
	
	2
	

	Oil  LS x
	Oil Level  Switch
	Switch
	INPUTS→GEN.I →OIL.x
	CPM-x-J6 –CH06

	
	
	
	
	1
	

	
	
	
	
	2
	

	MTA
	Must Trip Amps
	8 Pin Dip Switch
	Configuration→Unit       →MTA x
	
	

	SW1
	Configuration Switch
	4 Pin Dip Switch
	NA
	
	

	MTR-x
	Compressor xn Motor Temperature
	NTC Thermistor
	TEMPERATURES→CIRx →CTPx
	CPM-x-J9-CH01

	
	
	
	
	1
	

	
	
	
	
	2
	

	DGT x
	Compressor xn Discharge Gas Temperature
	NTC Thermistor
	TEMPERATURES→CIRx →DGT. X
	CPM-x-J9-CH02

	
	
	
	
	1
	

	
	
	
	
	2
	

	OPT x
	Oil Pressure Transducer
	Pressure Transducer
	PRESSURES→PRC.x→OP. X
	CPM-x J10B-CH04

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S

R
	Signal

Return

	EPT x
	Economizer  Pressure Transducer
	Pressure Transducer
	PRESSURES→PRC.X→ECP. x
	CPM-x J10A-CH03

	
	
	
	
	5V
	+, 5 vdc Ref.

	
	
	
	
	S

R
	Signal

Return

	
	Compressor Current X Phase A 
	Current Sensor
	
	CPM J8 CT1
	

	
	Compressor Current X Phase B
	Current Sensor
	
	CPM J8 CT2
	

	
	Compressor Current X Phase C
	Current Sensor
	
	CPM J8 CT3
	

	Output
	Description
	I/O Type
	NAVIGATOR

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	C x 1M
	Compressor x 1M Contactor
	Contactor
	
	CPM-x-J2 Channel 7

	
	
	
	
	
	

	
	
	
	
	
	

	C x 2M
	Compressor x 2M Contactor
	Contactor
	
	CPM-x-J2 Channel 8

	
	
	
	
	
	

	
	
	
	
	
	

	C x S
	Compressor x S Contactor
	Contactor
	
	CPM-x-J2 Channel 9

	Oil HTR x
	Oil Heater Relay x
	Contactor
	OUTPUTS→CIR.X→HT.x
	CPM-x-J2 Channel 10

	
	
	
	
	
	

	
	
	
	
	
	

	OS-x
	Oil Solenoid x
	Solenoid
	OUTPUTS→CIR.X→OLS.x
	CPM-x-J2 Channel 12 

	
	
	
	
	
	

	SL1-x
	Load Solenoid x
	Solenoid
	OUTPUTS→CIR.X→SL1.x
	CPM-x-J2 Channel 13

	SL2-x
	Unload Solenoid x
	Solenoid
	OUTPUTS→CIR.X→SL2.x
	CPM-x-J2 Channel 14




* “X” denotes the circuit, A, B or C.  

The CPM module also has 3 Dip switch inputs S1,S2 and S3.

DIP Switch #1 S1 Input  8 position Dip switch
  Position 1 – Starter configuration 



0 – Direct Start



1 – Y-Delta Start

Position 2&3  - Current Transfromer (CT) position



00 – CT are located in the main line 

01 - CT are located in the Delta of motor 

10– Soft Starter  (Not available at this time)
11 – Invalid will cause MTA configuration Fault Alarm

Position 4,5&6 – CT Selection



000 – 100A/1V CT1


001 – 100A/0.503 V CT2


010 – 100A/0.16V CT3



011 – Invalid will cause MTA Configuration Alarm



100 – Invalid will cause MTA Configuration Alarm


101 – Invalid will cause MTA Configuration Alarm


110 – Invalid will cause MTA Configuration Alarm


111 – Invalid will cause MTA Configuration Alarm
Position 7 - Contactor Failure Action

0- All units should be configured on

1- Used when Shunt Trip available in unit

Position 8 – Not used

DIP Switch #2 S2 MTA setting

MTA Must trip setting is computed from Dipswitch 2 setting, in combination with the CT position and CT selection. Refer to Appendix for DIP switch settings for all units. The MTA setting which is calculated using the settings of S1 and S2 must match MTA setting in software or MTA alarm will be generated.
Dip Switch # 3 S3 LEN Bus address Number

 XE "Controls:Electronic Expansion Valve (EXV) Board" Electronic Expansion Valve (EXV) Board —80 Ton Unit has one EXV Board. The 90-500 each circuit has an EXV board See Fig. 2.  The board is responsible for monitoring the suction gas temperature and economizer gas thermistors.  The board also signals the Main EXV and ECEXV motors to open or close.  The electronic expansion valve board responds to commands from the MBB and sends the MBB the results of the channels it monitors via the LEN (local equipment network). See Tables 4 and 5.

Fig. 2 – EXV Board
[image: image3.png]RO

s =

imi
ERdiGyS

5 8

TF
HEL

Beadbed)

M ivEvivgagn Lo

.0
:

(@O
T
%
o

=
=
=
=
=B
0

q

.
U= T
[

e @i

LOGATION OF
|~ SERIAL NUMBER

Fig. 3 — EXV Board




Table 4 – 30XA080  XE "Controls:EXV1 Board Inputs and Outputs" EXVA Board Inputs and Outputs

	EXV1 Board

	                  1            2                3                   4                    5               6              7              8

	Address:  ON       ON             ON             ON                 ON            ON          OFF       ON

	Used on:  30XA080

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	EXVA-J1

	
	
	11
	24 vac

	
	
	12
	Ground

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	EXVA-J4

	
	
	1
	+

	
	
	2
	G

	
	
	3
	-

	Input
	Description
	I/O Type
	Navigator

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	SGTA
	Circuit A Suction Gas Thermistor
	5k Thermistor
	TEMPERATURE→CIR.A→SGT.A
	EXVA-J3

	
	
	
	
	TH
	

	
	
	
	
	A
	

	SGTB
	Circuit B Suction Gas Thermistor
	5k Thermistor
	TEMPERATURE→CIR.B→SGT.B
	EXVA-J3

	
	
	
	
	TH
	

	
	
	
	
	B
	

	Output
	Description
	I/O Type
	Navigator

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	EXV-A
	Circuit A EXV
	Stepper Motor
	OUTPUTS→CIR.A→EXV.A
	EXVA-J2A

	
	
	
	
	1
	

	
	
	
	
	2
	

	
	
	
	
	3
	

	
	
	
	
	4
	

	EXV-B
	Circuit B EXV
	Stepper Motor
	OUTPUTS→CIR.B→EXV.B
	EXVA-J2B

	
	
	
	
	1
	

	
	
	
	
	2
	

	
	
	
	
	3
	

	
	
	
	
	4
	


Table 5 – 30XA090-500   XE "Controls:EXV1 Board Inputs and Outputs" EXV n Board Inputs and Outputs

	EXVn Board

	                                     1            2                3                   4                    5               6              7              8

	Circuit A Address:  ON       ON             ON             ON                 ON            ON          OFF       ON

Circuit B Address:  OFF     ON             ON             ON                 ON            ON          OFF       ON

Circuit C Address:  ON       OFF           ON             ON                 ON            ON          OFF       ON



	Used on:  30XA090-500

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	EXVn-J1

	
	
	11
	24 vac

	
	
	12
	Ground

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	EXVn-J4

	
	
	1
	+

	
	
	2
	G

	
	
	3
	-

	Input
	Description
	I/O Type
	Navigator

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	SGT n
	Circuit n Suction Gas Thermistor
	5k Thermistor
	TEMPERATURE→CIR.A→SGT.n
	EXV n-J3

	
	
	
	
	TH
	

	
	
	
	
	A
	

	ECT n
	Circuit n Economizer Gas Thermistor
	5k Thermistor
	TEMPERATURE→CIR.B→EGT.n
	EXV n-J3

	
	
	
	
	TH
	

	
	
	
	
	B
	

	Output
	Description
	I/O Type
	Scrolling Marquee

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	EXV-n
	Circuit n EXV
	Stepper Motor
	OUTPUTS→CIR.n→EXV.n
	EXVn-J2A

	
	
	
	
	1
	

	
	
	
	
	2
	

	
	
	
	
	3
	

	
	
	
	
	4
	

	ECEXV-n
	Circuit n ECEXV
	Stepper Motor
	OUTPUTS→CIR.n→ECEXV.n
	EXVn-J2B

	
	
	
	
	1
	

	
	
	
	
	2
	

	
	
	
	
	3
	

	
	
	
	
	4
	


 XE "Controls:Fan boards" Fan Boards –At least one Fan board is installed in each unit.  See Fig. 3 and 4. There are two types of Fan Boards, with and without an analog signal for the low ambient head pressure control fan speed controllers.   If a unit does not have low ambient head pressure control installed, it will not have the analog connection terminals.  The Fan Board responds to commands from the MBB and sends the MBB the results of the channels it monitors via the LEN. See Tables 6 - 8. 

Fig. 3 – Fan Board (AUX 1) without low ambient head pressure control
[image: image4.png]omve

SRS SO TE
L fr=sia=a 5@
B B
2[R 3 3
oL & =
v wal @ |-
= B oo
A
. 8 [io
m a |-
TR ERERER ® loo
388 BRFHID LIS
[0 '5s% www w%% -
L [ 2
81 B2 TB3 1B * °
I 11
wssszoma
T I R R A Il I | i | e i T

Fig. 4A — Fan Board (AUX 1) without Low Ambient Temperature Head Pressure Control




Fig. 4 – Fan Board (AUX 2) with low ambient head pressure control
[image: image5.png]LOGATION OF
SRR ABER

sTTus si0 e

B

oo

o

1O

Fig. 4B — Fan Board (AUX 2) with Low Ambient Temperature Head Pressure Control




Table 6 –  XE "Controls:Fan board 1 outputs" Fan Board A Outputs

	Fan Board 1

	                     1              2                   3                     4                        5                   6                7              8

	Address     OFF         ON             OFF               OFF                  ON               OFF           ON         OFF 

	Used on: 30XA080-120

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	FB A-J1

	
	
	11
	

	
	
	12
	

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	FB A-J9

	
	
	+
	

	
	
	G
	

	
	
	-
	

	
	
	+
	

	
	
	G
	

	
	
	-
	

	Output
	Description
	I/O Type
	Navigator 

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	MM-A*
	Circuit A Low Ambient Head Pressure Control Speed Signal
	0-10 VDC
	OUTPUTS→CIR.A→SPD.A
	FB A-CH9

	
	
	
	
	+
	

	
	
	
	
	-
	

	MM-B*
	Circuit B Low Ambient Head Pressure Control Speed Signal 
	0-10 VDC
	OUTPUTS→CIR.B→SPD.B
	FB A-CH10

	
	
	
	
	+
	

	
	
	
	
	-
	

	FCA1
	Fan Contactor A1
	Contactor
	
	FB A-J2-CH1

	FCA2
	 Fan Contactor A2
	Contactor
	
	FB A-J2-CH2 



	FCA 3
	Fan Contactor A3
	Contactor
	
	FB A-J2-CH3

	FCA 4
	Fan Contactor A4
	Contactor
	
	FB A-J2-CH4

(90-120 Only)

	FCB1
	Fan Contactor B1
	Contactor
	
	FB A-J3-CH5

	FCB2
	 Fan Contactor B2
	Contactor
	
	FB A-J3-CH6 



	FCB 3
	Fan Contactor B3
	Contactor
	
	FB A-J3-CH7

	FCB 4
	Fan Contactor B4
	Contactor
	
	FB A-J3-CH8

(90-120 Only)


* Output only on low ambient head pressure control (AUX2)

Table 7 –  XE "Controls:Fan board 1 outputs" Fan Board n Outputs

	Fan Board n

	                                       1              2                   3                     4                        5                   6                7              8

	Circuit A Address     OFF         ON             OFF               OFF                  ON               OFF           ON         OFF

Circuit B Address      ON          ON             OFF               OFF                  ON               OFF           ON         OFF



	Used on: 30XA140-350

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	FB A-J1

	
	
	11
	

	
	
	12
	

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	FB A-J9

	
	
	+
	

	
	
	G
	

	
	
	-
	

	
	
	+
	

	
	
	G
	

	
	
	-
	

	Output
	Description
	I/O Type
	Navigator 

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	MM-n*
	Circuit n Low Ambient Head Pressure Control Speed Signal
	0-10 VDC
	OUTPUTS→CIR.n→SPD.n
	FB n-CH9

	
	
	
	
	+
	

	
	
	
	
	-
	

	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	FCn1
	Fan Contactor n1
	Contactor
	
	FB n-J2-CH1

	FCn2
	 Fan Contactor n2
	Contactor
	
	FB n-J2-CH2 



	FCn 3
	Fan Contactor n3
	Contactor
	
	FB n-J2-CH3

	FCn 4
	Fan Contactor n4
	Contactor
	
	FB n-J2-CH4



	FCn5
	Fan Contactor n5
	Contactor
	
	FB n-J3-CH5

	FCn6
	 Fan Contactor n6
	Contactor
	
	FB n-J3-CH6 



	FCn7
	Fan Contactor n7
	Contactor
	
	FB n-J3-CH7

	FCn8
	Fan Contactor n8
	Contactor
	
	FB n-J3-CH8




· Output only on low ambient head pressure control (AUX2)

· n Indicates Circuit A or B

Table 8 –  XE "Controls:Fan board 3 inputs and outputs" Fan Board C Inputs and Outputs

	Fan Board 3

	DIP SWITCH:                    1               2                3                4                   5            6            7             8

	Address:                            OFF          OFF          ON            OFF           ON           OFF     ON          OFF 

	Used on:  30XA400-500

	Power
	24 vac supply
	Connection Point

	
	
	Pin
	Notation

	
	
	FBC-J1

	
	
	11
	

	
	
	12
	

	Local Equipment Network
	
	Connection Point

	
	
	Pin
	Notation

	
	
	FBC-J9

	
	
	+
	

	
	
	G
	

	
	
	-
	

	
	
	+
	

	
	
	G
	

	
	
	-
	

	Input
	Description
	I/O Type
	Scrolling Marquee

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	DPTC
	Circuit C Discharge Pressure Transducer
	Pressure Transducer
	PRESSURE→PRC.C→DP.C
	FBC-J7-CH13

	SPTC
	Circuit C Suction Pressure Transducer
	Pressure Transducer
	PRESSURE→PRC.C→SP.C
	FBC-J8-CH14

	Output
	Description
	I/O Type
	Scrolling Marquee

Point Name
	Connection Point

	
	
	
	
	Pin
	Notation

	
	
	
	
	

	MM-C
	Circuit C Low Ambient Head Pressure Control Speed Signal (210-300)
	0-10 VDC
	OUPTUTS→CIR.C→SPD.C
	FBC-CH9

	
	
	
	
	+
	

	
	
	
	
	-
	

	FCC1
	Fan Contactor C1
	Contactor
	
	FBC-J2-CH1



	FCC2
	Fan Contactor C2
	Contactor
	
	FBC-J2-CH2

	FCC 3
	Fan Contactor C3
	Contactor
	
	FBC-J2-CH3



	FCC 4
	Fan Contactor C4
	Contactor
	
	FBC-J2-CH4



	FCC5
	Fan Contactor C5
	Contactor
	
	FBC-J3-CH5

	FCC6
	Fan Contactor C6
	Contactor
	
	FBC-J3-CH6

	FCC7
	Fan Contactor C7
	Contactor
	
	FBC-J3-CH7

	FCC8
	Fan Contactor C8
	Contactor
	
	FBC-J3-CH8

	
	
	
	
	

	
	
	
	
	


*  Output only on low ambient head pressure control (AUX2)

 XE "Controls:Enable-off-remote contact switch" Enable-Off-Remote Contact Switch – This switch is installed in all units and provides the owner/servicer with a local means of enabling or disabling the machine.  It is a 3-position switch used to control the chiller.  When switched to the Enable position the chiller is under its own control.  Move the switch to the Off position to shut the chiller down.  Move the switch to the Remote Contact position and a field-installed dry contact can be used to start the chiller.  The contacts must be capable of handling a 24-vac, 20-mA load.  In the Enable and Remote Contact (dry contacts closed) positions, the chiller is allowed to operate and respond to the scheduling configuration, CCN configuration and set point data.

 XE "Controls:Emergency on/off switch" Emergency On/Off Switch — This switch is installed in all units.  The Emergency On/Off switch should only be used when it is required to shut the chiller off immediately. Power to all modules is interrupted when this switch is off and all outputs from these modules will be turned off.
 XE "Controls:Energy management module (EMM)" Energy Management Module (EMM) — The EMM is available as a factory-installed option or as a field-installed accessory.  The EMM receives 4 to 20 mA inputs for the temperature reset, cooling set point reset and demand limit functions.  The EMM also receives the switch inputs for the field-installed second stage 2-step demand limit and ice done functions.  The EMM communicates the status of all inputs with the MBB, and the MBB adjusts the control point, capacity limit, and other functions according to the inputs received. See Table 9. 

	CAUTION

	Care should be taken when interfacing with other manufacturer’s control systems due to possible power supply differences, full wave bridge versus half wave rectification, which could result in equipment damage.  The two different power supplies cannot be mixed.  ComfortLink™ controls use half wave rectification.  A signal isolation device should be utilized if a full wave bridge signal generating device is used.


Table 9 –  XE "Controls:Energy management module (EMM) inputs and outputs" Energy Management Module (EMM) Inputs and Outputs

	Energy Management Module

	Address  Default = 1, address 9

	Used on:  30XA080-500

	Input
	Description
	I/O Type
	I/O Point Name
	Connection Point

	4-20 mA or 2-10 vac Demand Limit
	4-20 mA Demand Limit
	4-20 ma or 

2-10 vdc
	INPUTS→GEN.I→DMND
	EMM-J7B-CH6

	4-20 mA or 2-10 vac Temperature Reset/Setpoint
	4-20 mA Temperature Reset/ Set point
	4-20 ma or 

2-10 vdc
	INPUTS→GEN.I→RSET
	EMM-J7A-CH5

	Demand Limit SW2
	Demand Limit Step 2
	Switch Input
	INPUTS→GEN.I→DLS2
	EMM-J4-CH9

	Ice Done
	Ice Done Switch
	Switch Input
	INPUTS→GEN.I→ICE.D
	EMM-J4-CH11A

	Occupancy Override 
	Occupied Schedule Override
	Switch Input
	INPUTS→GEN.I→OCCS
	EMM-J4-CH8

	Remote Lockout Switch
	Chiller Lockout
	Switch Input
	INPUTS→GEN.I→RLOC
	EMM-J4-CH10

	SPT
	Space Temperature Thermistor
	10k Thermistor
	TEMPERATURE→UNIT→SPT
	EMM-J6-CH2

	Output
	Description
	I/O Type
	I/O Point Name
	Connection Point

	% Total Capacity
	
	0-10 vdc
	OUTPUTS→GEN.O→CATO
	EMM-J8-CH7

	RUN R
	Run Relay
	Relay
	OUTPUTS→GEN.O→RUN
	EMM-J3-CH24

	SHD R
	Shutdown Relay
	Relay
	OUTPUTS→GEN.O→SHUT
	EMM-J3-CH25


Basic Control Usage

 XE "Controls:Navigator module" 

 XE "Navigator module" Navigator Module— The Navigator module provides a mobile user interface to the ComfortLink control system. The display has up and down arrow keys, an [ENTER] key, and an [ESCAPE] key.  These keys are used to navigate through the different levels of the display structure.  Press the [ESCAPE] key until ‘Select a Menu Item’ is displayed to move through the top 11 mode levels indicated by LEDs on the left side of the display. See Fig. 6.

[image: image6.png]



(Source: 30RB-2pd, page 3)

Fig. 6  –  Navigator Display Module
Once within a Mode or sub-mode, a “>” indicates the currently selected item on the display screen.  Pressing the [ENTER] and [ESCAPE] keys simultaneously will put the Navigator into expanded text mode where the full meaning of all sub-modes, items and their values can be displayed.  Pressing the [ENTER] and [ESCAPE] keys when the display says ‘Select Menu Item’ (Mode LED level) will return the Navigator to its default menu of rotating display items (those items in the Run Status(VIEW). In addition, the password will be disabled requiring that it be entered again before changes can be made to password protected items.  The Service Test function should be used to verify component operation.  Press the [ESCAPE] key to exit out of the expanded text mode.

NOTE: When the Language Selection Configuration Mode(DISP(LANG, variable is changed, all appropriate display expansions will immediately change to the new language.  No power-off or control reset is required when reconfiguring languages.

When a specific item is located, the item name appears on the left of the display, the value will appear near the middle of the display and the units (if any) will appear on the far right of the display.  Press the [ENTER] key at a changeable item and the value will begin to flash.  Use the up and down arrow keys to change the value, and confirm the value by pressing the [ENTER] key.

	IMPORTANT:  All configuration changes (except for set points and time schedules) require a power cycle to permanently set the configuration.


Changing item values or testing outputs is accomplished in the same manner. Locate and display the desired item. Press [ENTER] so that the item value flashes.  Use the arrow keys to change the value or state and press the [ENTER] key to accept it.  Press the [ESCAPE] key to return to the next higher level of structure.  Repeat the process as required for other items.

Items in the Configuration and Service Test modes are password protected.  The words Enter Password will be displayed when required, with the default password also being displayed.  Use the arrow keys to change the number and press [ENTER] to enter the digit.  Continue with the remaining digits of the password.  The default password is 0113.  The password can only be changed through CCN operator interface software such as ComfortWORKS®, ComfortView™ and Service Tool.

 XE "Navigator module:Adjusting the contrast" Adjusting the Contrast — The contrast of the display can be adjusted to suit ambient conditions.  To adjust the contrast of the Navigator, press the [ESCAPE] key until the display reads, “Select a menu item.”  Using the arrow keys move to the Configuration mode.  Press [ENTER] to obtain access to this mode.  The display will read:

> 
TEST OFF


METR OFF


LANG ENGLISH

Pressing [ENTER] will cause the “OFF” to flash.  Use the up or down arrow to change “OFF” to “ON”.  Pressing

[ENTER] will illuminate all LEDs and display all pixels in the view screen.  Pressing [ENTER] and [ESCAPE] simultaneously allows the user to adjust the display contrast.  The display will read:


Adjust Contrast


- - - -+ - - - - - - - - - - - - - - -

Use the up or down arrows to adjust the contrast.  The screen’s contrast will change with the adjustment.  Press [ENTER] to accept the change.  The Navigator will keep this setting as along as it is plugged in to the LEN bus.

 XE "Navigator module:Adjusting the backlight brightness" Adjusting the Backlight Brightness — The backlight of the display can be adjusted to suit ambient conditions.  The factory default is set to the highest level.  To adjust the backlight of the Navigator, press the [ESCAPE] key until the display reads, “Select a menu item.”  Using the arrow keys move to the Configuration mode.  Press [ENTER] to obtain access to this mode.  The display will read:

> 
TEST OFF


METR OFF


LANG ENGLISH

Pressing [ENTER] will cause the “OFF” to flash.  Use the up or down arrow keys to change “OFF” to “ON”. Pressing [ENTER] will illuminate all LEDs and display all pixels in the view screen.  Pressing the up and down arrow keys simultaneously allows the user to adjust the display brightness.  The display will read:


Adjust Brightness


- - - - - - - - - - - - - - - - - +

Use the up or down arrow keys to adjust the brightness.  The screen’s brightness will change with the adjustment. Press [ENTER] to accept the change.  The Navigator will keep this setting as long as it is plugged in to the LEN bus.
Table 10 –  XE "Controls:ComfortLink display menu Structure" 

 XE "Navigator module:ComfortLink display menu structure" 

 XE "Scrolling marquee display:ComfortLink display menu structure" ComfortLink Display Menu Structure

	ComfortLink Display Menu Structure

	Mode

	Run Status
	Service Test
	Temperatures
	Pressures
	Set Points
	Inputs
	Outputs
	Configuration
	Time Clock
	Operating Modes
	Alarms

	Auto Display

(VIEW)
	Manual Test Mode

(TEST)
	Unit Temperatures (UNIT)
	Circuit A Pressures (PRC.A)
	Cooling Setpoints (COOL)
	General Inputs (GEN.I)
	Circuit A Outputs (CIR.A)
	Display Configuration (DISP)
	Time of Day (TIME)
	Operating Control Type (SLCT)
	Reset Current Alarms (R.ALM)

	Remote User Interface

(R.CCN)
	Quick Test Mode (QUIC)
	Circuit A Temperatures (CIR.A)
	Circuit B Pressures (PRC.B)
	Heating Setpoints (HEAT)
	
	Circuit B Outputs (CIR.B)
	Unit Configuration (UNIT)
	Day, Date (DATE)
	Operating Modes (MODE)
	Current Alarms (ALRM)

	Machine Starts/

Hours

(RUN)
	
	Circuit B Temperatures (CIR.B)
	Circuit C Pressures (PRC.C)
	Misc.  Setpoints (MISC)
	
	Circuit C Outputs (CIR.C)
	Service Configurations (SERV)
	Schedule 1 (SCH1)
	
	Alarm History (H.ALM)

	Compressor Run Hours

(HOUR)
	
	Circuit C Temperatures (CIR.C)
	
	
	
	General Outputs (GEN.O)
	Options Configuration (OPTN)
	Schedule 2 (SCH2)
	
	

	Compressor Starts (STRT)
	
	
	
	
	
	
	Reset, Demand Limit, Master/Slave (RSET)
	Holidays (HOLI)
	
	

	Fan Run Hours (FAN)
	
	
	
	
	
	
	
	Service Maintenance Configuration (MCFG)
	
	

	Compressor Disable (CP.UN)
	
	
	
	
	
	
	
	
	
	

	Predictive Maintenance (MAIN)
	
	
	
	
	
	
	
	
	
	

	Software Versions (VERS)
	
	
	
	
	
	
	
	
	
	


 XE "Controls:Local equipment network" Local Equipment Network – Information is transmitted between modules via a 3-wire communication bus or LEN (Local Equipment Network).  External connection to the LEN bus is made at TB3. 

 XE "Controls:Board addresses" 

 XE "Boards:Board addresses" Board Addresses — All boards (except the Main Base Board and the Energy Management Module Board) have 8-position DIP switches.  Addresses for all boards are listed with the Input/Output Tables for each board.

 XE "Controls:Control Module communication" Control Module Communication

RED LED — Proper operation of the control boards can be visually checked by looking at the red status LEDs light-emitting diodes).  When operating correctly, the red status LEDs should be blinking in unison at a rate of once every 2 seconds.  If the red LEDs are not blinking in unison, verify that correct power is being supplied to all modules.  Be sure that the Main Base Board (MBB) is supplied with the current software.  If necessary, reload current software. If the problem still persists, replace the MBB.  A red LED that is lit continuously or blinking at a rate of once per second or faster indicates that the board should be replaced.

GREEN LED — The MBB has one green LED.  The Local Equipment Network (LEN) LED should always be blinking whenever power is on.  All other boards have a LEN LED which should be blinking whenever power is on.  Check LEN connections for potential communication errors at the board connectors.  See Input/Output Tables for LEN Connector designations.  A 3-wire sensor bus accomplishes communication between modules. These 3 wires run in parallel from module to module. The J9A connector on the MBB provides communication directly to the marquee display and Navigator.

YELLOW LED — The MBB has one yellow LED.  The Carrier Comfort Network (CCN) LED will blink during times of network communication.

 XE "Controls:Carrier comfort network interace" 

 XE "CCN:Interface" Carrier Comfort Network (CCN) Interface — The 30XA units can be connected to the CCN, if desired.  The communication bus wiring is a shielded, 3-conductor cable with drain wire and is supplied and installed in the field.  The system elements are connected to the communication bus in a daisy chain arrangement.  The positive pin of each system element communication connector must be wired to the positive pins of the system elements on either side of it.  This is also required for the negative and signal ground pins of each system element.  Wiring connections for CCN should be made at TB3.  Consult the CCN Contractor’s Manual for further information. See Fig. 7.

[image: image7.png]@ com ¢ sHED

) GoM) © SHEWD

) CoM) © SHEWD

v cen

f
S0
D]

@
=0

O

]

]

Ty
Fl
EAD)
Dl

O
O

]

]

Ty
Fl
EAD)
Dl

O

v cen

—
L reo

L reo

=0 g EoHEq Jex

Comfortlink CCN Communication Wiring




Fig. 7 –  XE "CCN:ComfortLink CCN communication wiring" ComfortLink CCN Communication Wiring 

NOTE: Conductors and drain wire must be 20 AWG (American Wire Gage) minimum stranded, tinned copper. Individual conductors must be insulated with PVC, PVC/nylon, vinyl, Teflon, or polyethylene.  An aluminum/polyester 100% foil shield and an outer jacket of PVC, PVC/nylon, chrome vinyl, or Teflon with a minimum operating temperature range of –20 C to 60 C is required.  See Table 22 for recommended wire manufacturers and part numbers.

	Table 22 - CCN Communication Bus Wiring

	Manufacturer
	Part Number

	
	Regular Wiring
	Plenum Wiring

	Alpha
	1895
	-

	American
	A21451
	A48301

	Belden
	8205
	884421

	Columbia
	D6451
	-

	Manhattan
	M13402
	M64430

	Quabik
	6130
	-


It is important when connecting to a CCN communication bus that a color-coding scheme be used for the entire network to simplify the installation.  It is recommended that red be used for the signal positive, black for the signal negative, and white for the signal ground. Use a similar scheme for cables containing different colored wires.
At each system element, the shields of its communication bus cables must be tied together. If the communication bus is entirely within one building, the resulting continuous shield must be connected to a ground at one point only.  If the communication bus cable exits from one building and enters another, the shields must be connected to grounds at the lightning suppressor in each building where the cable enters or exits the building (one point per building only). To connect the unit to the network:

1. Turn off power to the control box.

2. Cut the CCN wire and strip the ends of the red (+), white (ground), and black (–) conductors. (Substitute appropriate colors for different colored cables.)

3. Connect the red wire to (+) terminal on TB3 of the plug, the white wire to COM terminal, and the black wire to the (–) terminal.

4. The RJ14 CCN connector on TB3 can also be used, but is only intended for temporary connection (for example, a laptop computer running Service Tool).

	IMPORTANT: A shorted CCN bus cable will prevent some routines from running and may prevent the unit from starting.   If abnormal conditions occur, unplug the connector. If conditions return to normal, check the CCN connector and cable.  Run new cable if necessary. A short in one section of the bus can cause problems with all system elements on the bus.


Configuration Options




 XE "Controls:Ramp loading" Ramp Loading

Ramp Loading Configuration(OPTN(RL.S, limits the rate of change of leaving fluid temperature.  If the unit is in a Cooling mode and configured for Ramp Loading, the control makes 2 comparisons before deciding to change stages of capacity.  The control calculates a temperature difference between the control point and leaving fluid temperature. If the difference is greater than 4° F (2.2° C) and the rate of change (°F or °C per minute) is more than the configured Cool Ramp Loading Setpoints(COOL(CRMP, the control does not allow any changes to the current stage of capacity.

 XE "Controls:Minutes off time" Minutes Off Time

Minutes Off Time Configuration(OPTN(DELY is a field configurable item that is a time delay added to the start when the machine is commanded ON.  This is a field 
configurable  item from 1 to 15 minutes.  The factory default is 1 minute.  This feature is useful when multiple units are installed.  Staggering the start will reduce the inrush potential.

 XE "Controls:Dual chiller control" Dual Chiller Control

The dual chiller routine is available for the control of two parallel units supplying chilled fluid on a common loop.  This control is designed for a parallel fluid flow arrangement only.  One chiller must be configured as the master chiller, the other as the slave chiller.  An additional leaving fluid temperature thermistor (Dual Chiller LWT) must be installed in the common chilled water piping as described in the Installation Instructions for both the master and slave chiller.  See the Field Wiring section in the Base Unit Installation Instructions for Dual Chiller LWT sensor control wiring.  A chilled water flow switch is factory-installed for each chiller.  

Parallel chiller control with dedicated pumps is recommended.  Chiller must start and stop its own water pump located on its own piping.  If pumps are not dedicated for each chiller, chiller isolation valves are required: each chiller must open and close its own isolation valve through the control (valve shall be connected to the pump outputs).   Pump Control is enabled as described in the Cooler Pump Control Section.  One additional parameter is set for the dual chiller control.  Lag Unit Pump Select, Configuration(RSET(LAGP allows the user to configure the control to energize the pump for the lag chiller once the unit enters an occupied time period or hold it off until the lag unit is started.  It is recommended that this parameter be set to 0, OFF IF U STOP. 

The control of the slave chiller shall be done through commands emitted by the master chiller.  The slave chiller has no action in the master/slave operations: it shall only verify that CCN communication with its master is present.

The dual chiller control provides the ability to select a lead chiller between the master and slave chiller.  By configuring Lead/Lag Balance Select Configuration(OPTN(LLBL to ENBL, the lead chiller selection is based on the Lead/Lag Balance Delta Configuration(OPTN(LLBD between the master and slave run hours.  As long as the run hour difference between the master and the slave remain less than the LLBD the chiller in the lead position will remain as the lead chiller. Lead/lag changeover between the master and the slave due to hour balance shall occur during chiller operating odd days, such as day 1, day 3, day 5 of the month at 12:00 a.m.  If this function is unused then, the master chiller will always be the lead chiller.  

The dual chiller control algorithm has the ability to delay the start of the lag chiller in two manners.  The Lead Pulldown Time, Configuration(RSET(LPUL provides a field configurable time delay of 0 to 60 minutes.  This time delay gives the lead chiller a chance to remove the heat that the chilled water loop picked up while being inactive during an unoccupied period.  The Lead Pulldown Time parameter is a one-time time delay initiated after starting the lead chiller, manually or by a schedule, before checking 

whether to start an additional chiller.  This routine provides the lead chiller an opportunity to pull down the loop temperature before starting another chiller.  The second time delay, Lead/Lag Delay Configuration(RSET(LLDY is a time delay imposed between the last stage of the lead chiller and the start of the lag chiller.  This prevents enabling the lag chiller until the lead/lag delay timer has expired. See Tables 23 and 24. 

Table 23 –  XE "Controls: Configuring the master chiller" Configuring the Master Chiller

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[Enter]
	CCNA
	CCN Address
	Confirm address of chiller.  The master and slave chiller must have different addresses.

	
	[Enter]
	1
	
	Factory default address is 1.  With the master chiller the address is not as important.

	
	[Escape]
	CCNA
	
	

	
	[↓]
	CCNB
	CCN Bus Number
	Confirm the bus number of the chiller.  The master and slave chiller must be on the same bus.

	
	[Enter]
	0
	
	Factory default address is 0.  

	
	[Escape]
	CCNB
	
	

	
	[Escape]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	
	
	
	

	
	[↓]
	MSSL
	Master/Slave Select
	

	
	[Enter]
	0
	Disable
	

	
	[Enter]
	0
	Disable
	Flashing to indicate Edit mode.  May require Password

	
	[↑]
	1
	Master
	Use up arrows to change value to 1.

	
	[Enter]
	1
	
	Accepts the change.

	
	[Escape]
	MSSL
	
	

	
	[↓]
	SLVA
	Slave Address
	

	
	[Enter]
	1
	
	

	
	[Enter]
	1
	
	Flashing to indicate Edit mode.  

	
	[↑]
	2
	
	Use up arrows to change value to 2.  This address must match the address of the slave chiller.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	SLVA
	
	

	
	[↓]
	LLBL
	Lead/Lag Balance Select
	

	
	[Enter]
	ENBL
	
	Factory Default is ENBL

	
	[Escape]
	LLBL
	
	

	
	[↓]
	LLBD
	Lead/Lag Balance Delta
	

	
	[Enter]
	168
	
	Factory Default is 168.

	
	[Escape]
	LLBD
	
	

	
	[↓]
	LLDY
	Lead/Lag Delay
	

	
	[Enter]
	10
	
	Factory Default is 10.

	
	[Escape]
	LLDY
	
	

	
	[↓]
	LAGP
	Lag Unit Pump Select
	

	
	[Enter]
	0
	Off if U Stp
	Factory Default is 0, Off if unit is off.

	
	[Escape]
	LAGP
	
	

	
	[↓]
	LPUL
	Lead Pulldown Time
	

	
	[Enter]
	0
	
	Factory Default is 0

	
	[Escape]
	
	
	

	
	[Escape]
	
	
	At mode level

	Operating Modes
	[Enter]
	OPER
	Operating Control Type
	

	
	[Enter]
	0
	Switch Control
	Master chiller should be configured for job requirements, Switch Control, Time Schedule, or CCN. 

	
	[Escape]
	
	
	At mode level


Bold values indicate sub mode level.

Table 24 –  XE "Controls:Configuring the slave chiller" Configuring the Slave Chiller

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[Enter]
	CCNA
	CCN Address
	Confirm address of chiller.  The master and slave chiller must have different addresses.

	
	[Enter]
	1
	
	Factory default address is 1.  The slave chiller address must match what was programmed in the Master Chiller SLVA item.

	
	[Enter]
	1
	
	Flashing to indicate Edit Mode.

	
	[↑]
	2
	
	This item must match Master Chiller SLVA item.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	CCNA
	
	

	
	[↓]
	CCNB
	CCN Bus Number
	Confirm the bus number of the chiller.  The master and slave chiller must be on the same bus.

	
	[Enter]
	0
	
	Factory default address is 0.  

	
	[Escape]
	CCNB
	
	

	
	[Escape]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	
	
	
	

	
	[↓]
	MSSL
	Master/Slave Select
	

	
	[Enter]
	0
	Disable
	

	
	[Enter]
	0
	Disable
	Flashing to indicate Edit mode.  May require Password

	
	[↑]
	2
	Slave
	Use up arrows to change value to 2.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	MSSL
	
	

	
	[↓]
	SLVA
	Slave Address
	Not required.

	
	[↓]
	LLBL
	Lead/Lag Balance Select
	Not required.

	
	[↓]
	LLBD
	Lead/Lag Balance Delta
	Not required.

	
	[↓]
	LLDY
	Lead/Lag Delay
	Not required.

	
	[↓]
	LAGP
	Lag Unit Pump Select
	Not required.

	
	[↓]
	LPUL
	Lead Pulldown Time
	Not required.

	
	[Escape]
	
	
	

	
	[Escape]
	
	
	At mode level

	Operating Modes
	[Enter]
	OPER
	Operating Control Type
	

	
	[Enter]
	0
	Switch Control
	

	
	[Enter]
	0
	
	Flashing to indicate Edit Mode.

	
	[↑]
	2
	CCN Control
	Use up arrows to change value to 2.  

NOTE: Must be configured for CCN.

	
	[Enter]
	2
	
	Accepts the value.

	
	[Escape]
	OPER
	
	

	
	[Escape]
	
	
	At mode level


Bold values indicate sub mode level.

 XE "Controls:Capacity control" 

 XE "Capacity control" Capacity Control

The control system cycles compressors, and positions the slide valve of each compressor   to maintain the user-configured leaving chilled fluid temperature set point.  Entering fluid temperature is used by the Main Base Board (MBB) to determine the temperature drop across the cooler and is used in determining the optimum time to add or subtract capacity stages.  Return fluid temperature, space temperature (requires additional sensor), or outdoor-air temperature reset features can automatically reset the chilled fluid temperature set point.  It can also be reset from an external 4 to 20-mA signal (requires Energy Management Module).  Temperature reset requires a temperature sensor and the Energy Management Module. 

The control has an automatic lead-lag feature built in for circuit and compressor starts.  If enabled, the control will determine which circuit Configuration(OPTN(LLCS=0 and compressor to start to even the wear.  The compressor wear factor (combination of starts and run hours) is used to determine which compressor starts.  


[image: image8.wmf])

(

1

.

0

)

(

Hours

Run

Compressor

Starts

Compressor

Factor

Wear

Compressor

+

=


In this case, the circuit with the lowest  compressor wear factor is the circuit that starts first.     If the automatic lead-lag function for the circuit is not enabled Configuration(OPTN(LLCS=1 (Circuit A leads), 2 (Circuit B leads), 3 (Circuit C leads), the selected circuit will be the first to start.  Again, the compressor with the lowest wear factor within the circuit will be the first to start.  Minimum Load Control is enabled Configuration(UNIT(HGBP=1, the valve will be operational only during the first stage of cooling.


EQUAL LOADING – (Configuration  OPTN  LOAD=0)   the circuit which has started will maintain minimum stage of capacity and slide valve fully unloaded, when additional capacity is required the next circuit with the lowest compressor wearfactor is started with the the slide valve in the minimum position. As additional capacity is required the slide valve for a circuit will be adjusted in approximately 5% increments to match capacity requirements. The control will alternate between circuits to maintain the same percentage of capacity on each circuit.
STAGE LOADING - (Configuration  OPTN  LOAD=1)  the circuit which has started will gradually load the slide valve to match  required load until fully loaded . Once the compressor is fully loaded the next circuit with the lowest compressor wearfactor is started with the slide valve in the minimum position. The circuit which is operating at 100 % will gradually unload to meet capacity requirements.   


	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	









	
	

	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	









	
	

	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	









	
	

	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	









	
	

	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	




The capacity control algorithm runs every 30 seconds.  The algorithm attempts to maintain the Control Point at the desired set point.  Each time it runs, the control reads the entering and leaving fluid temperatures.  The control determines the rate at which conditions are changing and calculates 2 variables based on these conditions.  Next, a capacity ratio is calculated using the 2 variables to determine whether or not to make any changes to the current stages of capacity.  This ratio value ranges from –100 to +100%.  If the next change of capacity is a compressor, the control starts (stops) a compressor when the ratio reaches +100% (–100%).  If the next stage of capacity is to reposition the slide valve to increase capacity the change will occur when the ratio is +60%  or decrease in capacity when the ratio is 60 %.If installed, the minimum load valve solenoid will be energized with the first stage of capacity.  Minimum load valve value is a fixed 10 tons in the total capacity calculation.  The control will also use the minimum load valve solenoid as the last stage of capacity before turning off the last compressorA delay of 3 minutes occurs after each compressor capacity step change. 

 XE "Capacity control:Capacity control overrides" Capacity Control Overrides – The following overrides will modify the normal operation routine.  If any of the following override conditions listed below are satisfied, it shall determine the capacity change instead of the normal control.  Overrides are listed by priority order.  

Override #1:  Cooler Freeze Protection 

This override attempts to avoid the freeze protection alarm.  If the Leaving Water Temperature is less than Brine Freeze Set Point Configuration(SERV(LOSP + 2.0 °F (1.1 ºC) then remove a stage of capacity.

Override #2:  Circuit A Low Saturated Suction Temperature in Cooling

Override #3:  Circuit B Low Saturated Suction Temperature in Cooling

Override #4:  Circuit C Low Saturated Suction Temperature in Cooling

These overrides attempt to avoid the low suction temperature alarms.  This override is active only when more than one compressor in a circuit is ON.  If the Saturated Suction Temperature is less than Brine Freeze Set Point Configuration(SERV(LOSP – 6.0 °F  for 90 seconds, or The Saturated Suction Temperature is less than –4 ºF (-20 ºC), a the slide valve in the affected circuit will be repositioned .  

Override #5:  Low Temperature Cooling and High Temperature Heating

This override removes one stage of capacity when the difference between the Control Point Run Status(VIEW(CTPT and the Leaving Water Temperature Run Status(VIEW(LWT reaches a predetermined limit and the rate of change of the water is 0 or still decreasing.

Override #6:  Low Temperature Cooling and High Temperature Heating

This override removes two stages of capacity when the Entering Water Temperature Run Status(VIEW(EWT is less than the Control Point Run Status(VIEW(CTPT.

Override #7:  Ramp Loading

If the unit is configured for ramp loading Configuration(OPTN(RL.S=ENBL and if the difference between the Leaving Water Temperature and the Control Point is greater than 4 ºF (2.2 ºC) and the rate of change of the leaving water is greater than Cool Ramp Loading Rate Setpoints(COOL(CRMP then no capacity stage increase will be made. MD05 Mode 5 will be in effect.

Override #8:  Service Manual Test Override

The manual test consists in adding a stage of capacity every 30 seconds, until the control enables all of the requested compressors and Minimum Load Control selected in the Comfortlink Display service test menu.  All safeties and higher priority overrides are monitored and acted upon. 
Override # 9:  Demand Limit
This override mode is active when a command to limit the capacity is received.  If the current unit capacity is greater than the active capacity limit value, a stage is removed.   If the current capacity is lower than the capacity limit value, the control will not add a stage that will result in the new capacity being greater then the capacity limit value. MD04 will be in effect.

Override #10:  Cooler Interlock Override
This override prohibits compressor operation until the cooler interlock Inputs(GEN.I(LOCK is closed.  

Override #11:  High Temperature Cooling and Low Temperature Heating

This override algorithm runs once when the unit is switched to ON.  If the difference between the Leaving Water Temperature Run Status(VIEW(LWT and the Control Point Run Status(VIEW(CTPT exceeds a calculated value and the rate of change of the water temperature is greater than -0.1ºF/min, a stage will be added.

Override #12:  High Temperature Cooling and Low Temperature Heating

This override runs only when Minimum Load Control is Enabled, Configuration(UNIT(HGBP is 1, 2 or 3.  This override will add a stage of capacity if the next stage is Minimum Load Control, when the difference between the Leaving Water Temperature Run Status(VIEW(LWT and the Control Point Run Status(VIEW(CTPT exceeds a calculated value and the rate of change of the water temperature is greater than a fixed value.

Override #13: Minimum On/Off and Off/On Time Delay

Whenever a capacity  change has been made, slide valve or a compressor, the control will remain at this capacity stage for the next 90 seconds.  During this time, no capacity control algorithm calculations will be made.  If the capacity step is a compressor, an additional 90-second delay is added to the previous hold time  (See Override #22). This override allows for the system to stabilize before another capacity stage is added or removed.  If the unit encounters a condition of a higher priority override, the higher priority override will take precedence. MD10 Mode 10 will be in effect.

Override #14: Slow change override

This override prevents compressor stage changes when the leaving temperature is close to the control point and slowly moving towards the control point.

Override #15: System Manager Capacity Control
If a Chillervisor is controlling the unit and the Chillervisor is controlling multiple chillers, the unit will add a stage to attempt to load to the demand limited value. Mode 10
Override #37:  Circuit A Low Superheat

Override #38:  Circuit B Low Superheat

Override #39:  Circuit C Low Superheat  

This override attempts to avoid liquid slugging for the running compressors.  No capacity steps will be added to the affected circuit until a superheat greater than 18 ºF (10 ºC) is established.  If the capacity of the machine must be increased, the control will look to another circuit for additional capacity. Mode 30,31,32
Override #16:  Circuit A High Pressure Override

Override #17:  Circuit B High Pressure Override

Override #18:  Circuit C High Pressure Override  

This override attempts to avoid a high pressure failure. The algorithm is run every 4 seconds. If the Saturated Condensing Temperature for the circuit is above the High Pressure Threshold Configuration(SERV(HP.TH then the slide valve is repositioned on the circuit to reduce head pressure.  
Mode –27,28,29
Override #19: standby mode
This override algorithm will not allow a compressor to run if the unit is in Stand-by Mode, Run Status(VIEW(HC.ST=2.

Override #22:  Minimum On Time Delay

In addition to Override #13 Minimum On/Off and Off/On Time Delay, for compressor capacity changes, an additional 90-second delay will be added to the delay.  No compressor will be de-energized until 3 minutes have elapsed since the last compressor has been turned ON.  When this override is active, the capacity control algorithm calculations will be performed, but no capacity reduction will be made until the timer has expired.  However, control shall not take care of this 3 minutes minimum On/Off time in case of overrides with highest precedence.

Override #23:  Circuit A Low Saturated Suction Temperature in Cooling

Override #24:  Circuit B Low Saturated Suction Temperature in Cooling

Override #25:  Circuit C Low Saturated Suction Temperature in Cooling
If the circuit is operating in an area close to the operational limit of the compressor, the circuit capacity will remain at the same point or unload to raise the saturated suction temperature.  This algorithm will be active  following conditions is true:

1. Saturated Suction Temperature is less than Brine Freeze Configuration(SERV(LOSP – 6 ºF (3.3 ºC) 

2. Saturated Suction Temperature is less than Brine Freeze Configuration(SERV(LOSP with the circuit approach (Leaving Water Temperature – Saturated Suction Temperature) is greater than 15 ºF (8.3 ºC) and the Circuit Superheat (Discharge  Gas Temperature – Saturated Discharge Temperature) is greater than 25 ºF (8.3 ºC).

If any of these conditions are met, the appropriate Operating Mode, 21 (Circuit A), 22 (Circuit B) or 23 (Circuit C) will be enabled.

Override #34:  Circuit A Low Refrigerant Charge

Override #35:  Circuit B Low Refrigerant Charge

Override #36:  Circuit C Low Refrigerant Charge
The capacity override attempts to protect the compressor from starting with no refrigerant in the circuit.  This algorithm runs only when the circuit is not operational, no compressors ON.  There are several criteria that will enable this mode.

1. The Saturated Suction Temperature or Saturated Discharge Temperature is less than –13 ºF (-25 ºC)

2. All of these conditions must be true:

a. The Saturated Suction Temperature or Saturated Discharge Temperature is less than Leaving Water Temperature by more than 5.4 ºF (3.0 ºC)

b. Saturated Suction Temperature or Saturated Discharge Temperature is less than 41 ºF (5 ºC)

c. Outdoor Air Temperature is less than 32 ºF (0 ºC)

d. Saturated Suction Temperature or Saturated Discharge Temperature is less than the Outdoor Air Temperature by more than 5.4 ºF (3.0 ºC)

3. All of these conditions must be true:

a. The Saturated Suction Temperature or Saturated Discharge Temperature is less than Leaving Water Temperature by more than 5.4 ºF (3.0 ºC)

b. Saturated Suction Temperature or Saturated Discharge Temperature is less than 41 ºF (5 ºC)

c. Saturated Suction Temperature or Saturated Discharge Temperature is less than the Brine Freeze Point Configuration(SERV(LOSP by more than 6 ºF (3.3 ºC)

4. All of these conditions must be true:

a. The Saturated Suction Temperature or Saturated Discharge Temperature is less than Leaving Water Temperature by more than 5.4 ºF (3.0 ºC)

b. Saturated Suction Temperature or Saturated Discharge Temperature is less than 41 ºF (5 ºC)

c. Saturated Suction Temperature or Saturated Discharge Temperature is less than the Outdoor Air Temperature by more than 9 ºF (5 ºC)

If any of these conditions 1, 2, 3 or 4 are met, the appropriate Operating Mode, 21 (Circuit A), 22 (Circuit B) or 23 (Circuit C) will be enabled.
Override #41:  Circuit A High Current Override

Override #42:  Circuit B High Current Override

Override #43:  Circuit C High Current Override  

This override attempts to avoid a overcurrent failure. The algorithm is run every 4 seconds. If the compressor current is greater is greater than 79% of Must Trip Amps (MTA) but less than 85 % MTA then the capacity will be held at current capacity. If compressor current is greater than 85% then capacity will be reduced until current is less than 85 % MTA. Configuration(UNIT(MTA.x then the slide valve is repositioned on the circuit to reduce head pressure.  

Mode –27,28,29

 XE "Head pressure control" \t "See low ambient head pressure control" 

 XE "Controls:Low ambient head pressure control" 

 XE "Low ambient head pressure control" Low Ambient Head Pressure Control

The Main Base Board (MBB) controls the condenser fans to maintain the lowest condensing temperature possible, and thus the highest unit efficiency.  The MBB uses the saturated condensing temperature input from the discharge pressure transducer to control the fans.  Head pressure control is maintained through a calculated set point which is automatically adjusted based on actual saturated condensing and saturated suction temperatures so that the compressor(s) is (are) always operating within the manufacturer's specified envelope (see Fig. 13).  Each time a fan is added the calculated head pressure set point will be raised 25 F (13.9 C) for 35 seconds, to allow for the system to stabilize.  The control will automatically reduce the unit capacity as the saturated condensing temperature approaches an upper limit.  The control will indicate through an operating mode that high ambient unloading is in effect.  If the saturated condensing temperature in a circuit exceeds the calculated maximum, the circuit will be stopped.  For these reasons, there are no head pressure control methods or set points to enter.  The control will turn off a fan stage when the condensing temperature is below the minimum head pressure requirement for the compressor.  Fan sequences are shown in Fig. 14.

LOW AMBIENT HEAD PRESSURE CONTROL OPTION — For low-ambient operation, the lead fan on a circuit can be equipped with low ambient head pressure control option or accessory.  The controller is energized with the first fan stage and adjusts fan speed to maintain the calculated head pressure set point. See Table   .

Table    -  XE "Low ambient head pressure control: Fan Staging" Fan Staging

[image: image50.png]



[image: image51.wmf]Solenoid 2

Solenoid 1

HPS, Discharge 

Gas Temperature 

Sensor Location

Motor 

Temperature 

Sensors

Oil Pressure 

Transducer 

Location

Solenoid 2

Solenoid 1

HPS, Discharge 

Gas Temperature 

Sensor Location

Motor 

Temperature 

Sensors

Oil Pressure 

Transducer 

Location



 XE "Low ambient head pressure control: Operating instructions" LOW AMBIENT HEAD PRESSURE CONTROL OPERATING INSTRUCTIONS – The 30XA low ambient control is a variable speed drive (VFD) that varies the speed of the lead condenser fan in each circuit to maintain the calculated head pressure control setpoint. The speed varies in proportion to the 0-10vdc analog signal produced by the Fan Board. The display indicates motor speed in Hz by default.

Configuration – The low ambient head pressure control option is equipped from the factory with a Basic Operator Panel  (BOP). Default parameters are configured to operate based on a 0-10 vdc analog input signal present on terminals 3(AIN+) and 4(AIN-). Jumpers between terminals 2(0V) & 4(AIN-) and terminals 5(DIN1) and 8(24V+) are required for proper operation. The drive is enabled based on an increase in the analog input signal above 0 vdc. When the signal is at 0 vdc the drive holds the fan at 0 rpm. The low ambient head pressure control setpoint is not adjustable. Refer to the Head Pressure Control section for details. If the drive is replaced the following parameters must be configured:

Table    - Head Pressure Control Parameters

	Parameter
	Value
	Description

	P0010
	1
	Enter Quick Commissioning

	P0311
	1140
	Rated Motor Speed

	P3900
	1
	End of quick commissioning

	P0003*
	3
	User access level

	P0757*
	0.5
	Selection of frequency set point

	P1210 *
	6
	Automatic Restart


*Remove jumper from terminals 5 & 8 before configuring parameter. Reinstall jumper after configuration is complete.

Dip switch settings:

Dip switch 1 is not used.

Dip switch 2 is the motor frequency. (OFF = 50Hz, ON = 60Hz)

Drive Programming – Parameter values can be altered via the BOP. The BOP features a five-digit, seven –segment display for displaying parameter numbers and values, alarm and fault messages, set points, and actual values. Parameter information cannot be saved via the BOP. See Fig.    . See Table     for a list of buttons on the BOP.

NOTE: The BOP motor control functions are disabled by default. To control the motor via the BOP, parameter P0700 should be set to 1 and P1000 set to 1. The BOP can be fitted to and removed from the inverter while power is applied.  If the BOP has been set as the I/O control (P0700 = 1), the drive will stop if the BOP is removed.
[image: image9.png]L3

LINE
VOLTAGE L2
L1

13| |
N D, D
2 c* c
; \
I L U v W
T1 72 T3
U TO CONDENSER

FAN MOTOR

Fig. 10 — Low Ambient Temperature Control Power Wiring

ENABLE

JUMPER

o1

DIP Swich2
— 50/60Hz

I /o,

+

0-10VDC FROM FAN BOARD

Fig. 11 — Low Ambient Temperature Control Signal Wiring






[image: image10.png]Fig. 12 — Low Ambient Temperature Controller

Chansing Parameters with the Operator Panel — See Fig. 13
Tor the procedure for changing the value of parameter PO0O4.
Modifying the value of an indexed parameter is illustrated in
Fig. 13 using the example of P0719. Follow the same proce-
dure 10 alter other parameters using the operator panel.

NOTE: In some cases when changing parameter values the
display on the operator panel displays [BSEEB. This means the
drive is busy with tasks of higher priority

Changing Single Digits in Parameter Values — For chang-
ing the parameters value rapidly. the single digits of the display
can be changed by performing the following actions:

Ensure the operator panel is in the parameter value chang-
ing level as described in the Changing Parameters with the
Operator Panel section.

1. Press @) (function button). which causes the farthest

right digit to blink.

Change the value of this digit by pressing ° or °

3. Pressing @)
digit o blink.

4. Perform steps 2 to 4 unil the required value is displayed.

(function button) again fo cause the next

5. Press (@) (parameter button) to exit the parameter value
changing level.

NOTE: The function button may also be used to acknowledge
a fault condition.

d =13 — It is important that
parameter POO10 is used for commissioning and PO0O3 is used
to select the number of parameters to be accessed. The PO0I0
parameter allows a group of parameters to be selected that will
enable quick commissioning. Parameters such as molor sci-
tings and ramp settings are included. At the end of the quick
commissioning sequences. P3900 should be selected. which.
when set to 1. will carry out the necessary motor calculations
and clear all other parameters (not included in PO010=1 to the
default settings. This will only occur in Quick Commissioning
mode. Sce Fig. 14.

Reset to Factory Default —To reset all parameters to the fa
tory default settings: the following parameters should be sct as
follows:

1. Set PO010=30.

2. SetPOOTO=I.
NOTE: The reset process can take up to 3 minuies to complete.

CHANGING P0004 — PARAMETER FILTER FUNCTION

RESULT ON
STEP. DISPLAY

T e () 10 avoess paramaers
~0000

2 Press ° until PO004 Is display

POOCHY
o press (@ 1o sucess the parametr m

value level

4 P\ﬂaﬁf ° or ° tothe required 1

5 Press ° to confirm and
value

the

Ty the command parameters are
visible to the user

GHANGING P0719 AN INDEXED PARAMETER
SELECTION OF COMMAND/SETPOINT SOURCE

RESULT ON
STEP. DISPLAY
1 Press @) oo
° ~0000

2 Press ° until FO719 15 displa

ss parameters

P0718

3 Press @ to access the parameter

valus level 000

4 Press ° to display current set value

0

PRy yn——
0@

e

6 P\essom conform and st
value

P0T18

7 Fress () unii 10000 s disp

~00300

8 Press @ to retum the display to the
standard drive display (as define

by
the customen)

Fig. 13 — Changing Parameters
with the Operator Panel





[image: image11.png]Table 20 — Low Ambient Temperature Controller Operator Panel
PANEL/BUTTON

~0000

FUNCTION

Indicates Status.

DESCRIPTION

The LCD displays the settings currently used

Start Converter | The Star

nverter bution is disabled by defaull. To enable this button set PO

Stop Converter Press the Stop Corwerter but a standstill at the selcte
famp down rate. Disabled b
Press the Stop Converter butt stio a standstil
“This funcion is always enable

Change Direction | Press the Change Direct
Reverse s indicated ¢

enable set PO700

o butt Je the directi
aminus () sign or a flashing dec

f the m
int. Disabled &

defaul, to

r Press the Jog e
fun at the preset
buiton s n

1 button while the inverter has no oLtput to cause the motar to start and
requency. The motor stops when the button s released. The
nabled when the motar is running,

Fun

hs buton can be used to view additional infc
he folowing information starting from

v d - units V)

e but-
on

ameter during opera

units v
(P

jaling t
ons buttan repeated

The
s wil
Press the Func
Jump Function

Fress of the Fn butten from ar
RO000, when anofher parameter
the Functions again o return.

5 set to show any of the above 3, 4,
the menu).

toggle thre

5] then
wn when

ah clisplay

parameter (PXXXX ar PXOOOK) ta immediats
nbe changed, i required. Returm to RO

jump to
0 and press

ss Parameters | Allows acesss to the parameters.

Increase Valug, Fress the Increase

Setpaint using th

isplayed value. To change the Frequency

ease Value | Press the Decrease Value but

Frequency Setpoint using the

nto decrease the disy
serating panel st P10

Alue. To change the,

Troubleshooting with the Operating Panel — Warnings and

Fault Messages (Tables 21 and 22) — In the event of a fail-

Taults arc displayed on the operating panel with Axxx and

Fxxx, The individual messages are shown in Table 21.
11 the motor fails to start, check the following:

« Power is present on T1 T2 and T3.

+ Configuration jumpers ar in place.

+ Control signal between | vde and 10 vde is pres
terminals 3 and 4.

« PODIO=0.

« POT00=2

ent on

ure. the drive switches off and a fault code appears on the
displa

NOTE: To reset the fault code. one of the following methods
can be used:

1. Cyele the power to the drive.

2. Press m;@ button on the operator panel.





[image: image12.png]PO010_Start Quick Commissioning
0 Ready to Run
1 Quick Commissianing
20 Factory Setting
NOTE: FO010 must alviays be setback to 0 before operating
the motor. However If P3800 = 1 Is set after commissioring this
Is done automatically

POT00 Operation.
0 Power In KW, { default 50 Hz.
1 Powierin hp: Tdefault 60 Hz
2_Power in KiV;f default 60 Hz.

0700 _Selection of Command Source
(onioffiraverse)

0 Factory Setting

1 Basic Operator Panel
2_Terminal/Digital Inputs

P1000_Selection of Frequency Setpoint
0 No frequency setpoint

1 Operator panel frequiency control 1 1
2_Analog Setpoint

NOTE: Settngs 0and 1 should be changed using the DIP
switches to allow permanent setting.

P0304_Rated Motor Voltag
10V — 2000V
Nominal motor valtage (V) from rating plate

P0305_Rated Motor Current”
0— 2 xinverter rated current (&)

Nominal motor current (&) from ating plate

P0307 _Rated Motor Power"
0 kW — 2000 kW

Nominal motor power (kW) from rating plate.
If PO100 = 1, values wil be in hp

—_—

PO310_Rated Motor Frequency™
12 Hz — 650 He
Nominal motor frequency (Hz) from rating plate

P0311_Rated Motor Speed”
— 4000 1/min
Nominal motor speed (rpm) r

m ratin

plate

-specific parameters — see motor rating plate,
NOTE: Shaded

33 are for referancs

—

F1080_Tin. Motor Frequency
‘Sets minimum motor frequency (0-650H2) at which the motor
wil un indzpendent of the fr=cuisncy sipoint. The value set
hers is valid for both clockwise and counterelockvise rotation.

h 4
P1082_Tax. Wotor Frequency
‘Sets maximum motor frequency (0-650Hz) at which the motar
Wil 1N at ndependent of the freguency setpeint. The value set
here is valid for both clockwise and counterelockwise rotation

P1120_Ramp-Up Time.
05-6505
Time taken for the motor to accslerate from standstil up to

maximum molor frequency.

P1121_Ramp-Down Time
056505

Time taken for motor to decelerate fram maximum motor
frequency down to a standstil

0° Bl Gulck CommiSoning wiheut malar caeuaton or
factory reset

1 End Quick Commissioning with motor caleulation and
factory reset (Recommended)

2 End Quick Commissioning with motor calculation and with
IO reset

3 End Quick Commissioning with motor ealeulation but
without /0 reset

Fig. 14 — Low Ambient Temperature Controller Flow Chart Quick Commissioning




[image: image13.png]Table 21 — Low Ambient Temperature Controller Fault Messages

FAULT

Fo001
Overcurrent

POSSIBLE CAUSES

[ Hotor povier does not correspond fo he
inverler power

Hctor fead short ireit

Ground faui

TROUBLESHOOTING

Check e olowing
1. Hotor pover (RO307) must carespond to nverter porwer (P0206)

2. Hotor Sable and metor must have no Sharl-crcs or raund faus

3. otor paramelers must maich the motor n uss

3 Motor must not e obsirucied or overicaded

[Afer Stepe 1-4 have been checked, increase the ramp time (P1120) and reduce the
oot ieve (P1310. 1311, P1312)

70002
Overvoliage

DC-Tk voltage (10026) exceads I Tevel

(P2172)

- Overvoliage can be causea either by too high
main supply voltage of f molor s in regenera-
i mode.

- Regenerative mode can be caused by fast
ramp downs or il the molor i driven ffom an

acive load

Check the following
"Supply voltage (P0210) must fe within limits indicated on rating plate

2 DC-link voliage controllr must be enabled (P1240) and have parameters set
corecly

Ramp-down time (P1121) must malch inertia of foad

70003 [ Hain suppiy aied Check e ollowing
Undervoltage - Shockload culside specified lmits 1. Supply voltage (P0210) mustfie within limits indicated on rating plate
2 Suppiy must not be susoeplible o temporary filires or voitage feductons
Fo001 [~ Ambient Emperature ouside of imits Check the following
Drive - Fanaiure. 1. Fan must turn when inverter s running
Overtemperature 2. Puise frequency must be set 1o default valus.
3. Al et and outlet points are not obsiructed
3 Amblent temperatuire covid bo higher than specified for he drive
70005 "D overioaded Check he lowing
Drive Bt - Duty eyl too demanding 1. Load duty cycle must i within specifid imits
- Hotor povier (P0307) exceads diive power |2 Molor power (POS07) must match ciive pover (P0208)
capabilty (P0206)
Fo0T1 [ Hotor overicaded 1 Check motor data
Hotor - Hotor daia incorrect 2 Check loading on motor
Overtemperature Pt |- Long time period operating atlow speeds  [3. Boostsetings oo high (P1310,P1311, P1312)
4 Check parameter for molor thermal e constant
5. Chek paramer or mor 4 viarning fovel
Fo031 [Stator resistance measurement e T Chesk  the motor s conneciad to the dive,
Stator Resistance 2. Check ihat the moor data has been entered correctly
Measuremen Failure.
Fo051 [Reading orwriing of he non-volate parameter |1 Factory reset and new parameters set
Parameter EEPROM Fautt storage has fied 2_Replace diie.
F0052 [Reading of the powersiack iarmation s [Replace drve
Powerstack Fault _Jfailed or the data s invald
F0060 internal cormmunicatians fature T Acknowledge Gl
Asic Tmeout 2 Replace dive ifrepeated
70070 [No Setpoit received from communicatons |1 Check connections (o (he communications board

Communications
Board Setpoint Error

[board during telegram of tme.

Chek the master

Fo071 [No responss during telegram of e via US| 1 Check conneciions (o e communications board
No Data for USS (Rs232 [(BOP k) 2 Check the master
Link) During
Telegram Off Time
F0072 [No responss during telegram of e via US| 1 Check conneciions (o ihe communications board
No Data from USS (Rs485 [(COM ink) 2 Check the master
Link) During
Telegram Off Time
F0050 Eroken wie Check connechon o analog mput
Anlognput - |- Signalut of tmits
Lost Input Signal
70055 [External faul i tiggered via torminal iputs_|Disable terminal input for Gl vigger
External Fault
Fo01 [Softvare error or processor falre T Run salf st routines
Stack Overflow 2 Replace e
Fo221 [FID Feedtack below minimum valie P2265 |1 Change value of P2265
Pl Fecdback 2 Adust fecdback gain
Below Winimum Value
F0222 [PID Feedtack above maimum vals P2267 |1 Change value of P2267
Pl Feedback Above 2 Adust fecdback gain

Maximim Value

F0450
(Service Mods Only)
BIST Tests Failure

LEGEND
Ft— Cument Squared Time

Faut vaie
‘Some o the power secion tests have failed

2 Some of the control board tests have faled

4 Some of the funclional tests have faied

5 Some of the 10 modle tesis have faled

16 The Infernal RAVI has faied 1 check on

Trverter may rum bt cariain acions Wil ot funclion comectly
2 Replace e,




[image: image14.png]Table 22 — Alarm Messages

FAULT POSSIBLE GAUSES TROUBLESHOOTING
e T pwer does noTcorreSpon 1o e | T CIeck WHeIar e olor povier corresponds 1 The drTve power
Gurrent Limit drive povier 2. Check that the cable length imits have not been exceeded
- Motor eads are oo short 3. Check mtor cable and motar for shorLcrcuit and ground faults
- Ground fauit 3 Chck whether the molor parameters correspand wilh the motor being used
5. Chck the staor resistance
& Increase e ramp-Up-ime
7. Redlce the boost
8. Check whether the motor i obsiructed or overloaded
G502 "~ Wains supply Too figh T Check Thal mans supply voltage s vl alowatle rangs
Overvoltage Limit |+ Load reqenerative 2 Increase ramp down times
- Ramp-down time (oo short NOTE: If the vdc-max cortroller is active, ramp-down fimes wil be automatcally
increased
G503 [~ Wains supply oo Tow ‘Check main supply vltags (POZT0]
Undervoltage Limit__] - Short mains iierruption
ey Tarming levelof erler Nt S mperaiire | 1 CHeck ¥ ambent Erperatre s Wi Speced s
Drive (POS1A) s exceeded, resbiling I pulse ro- | 2. Check oad condiions and duty cycle
Overtemperature | quency reduction andior output requency [ 3. Check i fan s turning when drve s running
reduclion (depending on parameters set
0810}
G0 Waring Tevel & xceeded, SUmenTvThe | CReck Tauly oyde & Wi spectied e
Drive ft reduced f parameters set (PO10 = 1)
AGE0 ealsk temperature and Iermal Jonction | Check 14ty cyae 1 wibin speciied 1.
Drive Duty Cycle | model re vl of aicwable range
R Tiotor overfoaded T Tlwm
Wotor 1.'P0611 (motor 14 fme consiant) should be st to appropriate value

Overtemperature 2t

2
3
i

0314 (Molor 2 overload warning level) should be set o sultabie evel
Are long periods of operalion at low speed ecuring
Check ihal boos! selings ars not oo high

AT
Hotor Data
Wentification Active

TIotor daia Taen iAo (PTaT0) Selecied or
nnning

VA Uil motor ericalon T Tvshed

"A0600
RTOS Overrun Warning
LEGEND
Pt — Cument Squared Time

Softwars ermor









· 
· 
· 


 XE "Controls:Machine control" 

 XE "Machine control" Machine Control

Three variables control how the machine operates.  One variable controls the machine On-Off function.  Another controls the set point operation.  The third variable controls the Heat-Cool operation.   REF _Ref88551831 \h 
 \* MERGEFORMAT 23 illustrates how the control method and cooling set point select variables direct the operation of the chiller and the set point to which it controls.  The illustration also shows the On/Off state of the machine for the given combinations.

 XE "Controls:Control methods" 

 XE "Control methods" Control Methods

Machine On/Off control is determined by the configuration of the Operating Type Control Operating Modes(SLCT(OPER.  Options to control the machine locally via a switch, on a local Time Schedule, or via a Carrier Comfort Network command are offered.  

 XE "Control methods:Switch control" 

 XE "Switch control" SWITCH CONTROL – In this Operating Type Control, the Enable/Off/Remote Contact switch controls the machine locally.  All models are factory configured with OPER=0 (Switch Control).  With the OPER set to 0, simply switching the Enable/Off/Remote Contact switch to the Enable or Remote Contact position (external contacts closed) will put the chiller in an occupied state.  The unit Occupied status Run Status(VIEW(OCC will change from NO to YES.  The Status Unit Control Type Run Status(VIEW(CTRL will change from 0 (Local Off) when the switch is Off to 1 (Local On) when in the Enable position or Remote Contact position with external contacts closed.

[image: image15.png]Table 23 — Control Methods and Cooling Set Points

PRERIETER ACTE
Control Method Setpoint Select Enable Dual Setpoint Setpoint
(OPER) h (sPSE) e | Switch (DUAL) | Occupied (SP.OC)

1
(Setpoint1) Enable

Enable

o
(Switch Ctrl)

Enable

Enabled

Unoccupizd

1
(Time Sched)

Enable

Unoceupied

2
(cCN)

Enable C

Effect





 XE "Control methods:Time schedule" 

 XE "Time schedule" TIME SCHEDULE — In this Operating Type Control, the machine operates under a local schedule programmed by the user as long as the Enable/Off/Remote Contact switch is in the Enable or Remote Contact with external contacts closed.  To operated under this Operating Type Control, Operating Modes(SLCT(OPER = 1 (Time Sched).  Two Internal Time Schedules are available.  Time Schedule 1 Time Clock(SCH1 is used for single set point On-Off control.  Time Schedule 2 Time Clock(SCH2 is used for dual set point On-Off and Occupied-Unoccupied set point control.   The control will use the operating schedules as defined under the Time Clock mode in the Scrolling Marquee Display.

If the clock_number remains at 0, an internal schedule will be used.

 XE "Control methods:CCN global schedule" 

 XE "CCN global schedule" CCN GLOBAL SCHEDULE — A CCN Global Schedule can be set.  The schedule number can be set anywhere from 65 to 99 for operation under a CCN global schedule.  30RB units can be configured to follow a CCN Global Time Schedule broadcast by another system element. The ComfortView Network Manager’s Configure and Modify commands or the Service Tool’s Modify/Names function must be used to change the number of the Occupancy Equipment Part Table Name (OCC1P01E) to the Global Schedule Number.  The Schedule Number can be set from 65 to 99 (OCC1P65E). 

The Occupancy Supervisory Part table name (OCC1PO1S) number must be changed to configure the unit to broadcast a Global Time Schedule. The Schedule Number can be set from 65 to 99 (OCC1P65S). When OCC1PxxS is set to a value greater than 64, an occupancy flag is broadcast over the CCN every time it transitions from occupied to unoccupied or vice-versa. By configuring their appropriate Time Schedule decisions to the same number, other devices on the network can follow this same schedule. The Enable/Off/Remote Contact must be in the Enable position or Remote Contact position with the contacts closed for the unit to operate.  The Status Unit Control Type Run Status(VIEW(STAT will be 0 (Local Off) when the switch is Off.  The Status Unit Control Type will be 2 (CCN) when the Enable/Off/Remote Contact switch input is On.  

CCN CONTROL — An external CCN device such as Chillervisor controls the On/Off state of the machine.  This CCN device forces the variable CHIL_S_S between Start/Stop to control the chiller. The Status Unit Control Type Run Status(VIEW(STAT will be 0 (Local Off) when the Enable/Off/Remote Contact switch is Off.  The Status Unit Control Type will be 2 (CCN) when the Enable/Off/Remote Contact switch input is Closed and the CHIL_S_S variable is Stop or Start.  

 XE "Control methods: Unit run status" UNIT RUN STATUS

As the unit transitions from off to on and back to off, the Unit Run Status Run Status(VIEW(STAT will change based on the unit’s operational status.  The variables are: 0 (Off), 1 (Running), 2 (Stopping), and 3 (Delay).

· 0 indicates the unit is Off due to the Enable/Off/Remote Contact Switch, a time schedule or CCN command.

· 1 indicates the unit is operational.

· 2 indicates the unit is shutting down due to the command to shutdown from the Enable/Off/Remote Contact Switch, a time schedule or CCN command.

3 indicates the unit has received a command to start from Enable/Off/Remote Contact Switch, a time schedule or CCN command, and is waiting for the start-up timer Configuration(OPTN(DELY to expire.

 XE "Control methods: CCN control" 

 XE "CCN control" CCN CONTROL — An external CCN device such as Chillervisor controls the On/Off state of the machine.  This CCN device forces the variable CHIL_S_S between Start/Stop to control the chiller. The control mode [Operating Modes, MODE] will be 1 when the switch is Off.  The control mode will be 2 when the Enable/Off/Remote Contact switch input is On and the CHIL_S_S variable is Stop. Similarly, the control mode will be 6 when the CHIL_S_S variable is Start.

 XE "Cooling set point selection" Cooling Set Point Selection

Several options for controlling the Leaving Chilled Water Set Point are offered and are configured by the Cooling Set Point Select Operating Modes(SLCT(SP.SE variables.  In addition to the Cooling Set Point Select, Ice Mode Enable Configuration(OPTN(ICE.M, and Heat Cool Select Operating Modes(SLCT(HC.SE variables also have a role in determining the set point of the machine.  All units are shipped from the factory with the Heat Cool Select variable set to HC.SE=0 (Cooling).  All set points are based on Leaving Water Control, Configuration(SERV(EWTO=NO.

In all cases, there are limits on what values are allowed for each set point.  These values depend on the Cooler Fluid Type Configuration(SERV(FLUD and the Brine Freeze Set point Configuration(SERV(LOSP.  See Table 30.

Table 30 –  XE "Cooling set point selection: Configuration set point limits" 

 XE "Configuration set point limits" Configuration Set Point Limits

	Set Point Limit
	Cooler Fluid Type, FLUD

	
	1 = Water
	2 = Medium Brine

	Minimum *
	38 ºF (3.3 ºC)
	14 ºF (-10.0 ºC)

	Maximum
	60 ºF (15.5 ºC)


The minimum set point for Medium Temperature Brine applications is related to the Brine Freeze Point.  The set point is limited to be no less than the Brine Freeze Point + 5 ºF (2.8 ºC). See Table 31.

 XE "Cooling set point selection: Set point occupancy" SET POINT OCCUPANCY - When Set point Select Operating Modes(SLCT(SP.SE=0 (Set point Occ) is configured, the unit’s active set point is based on Cooling Set Point 1, Set Point(COOL(CSP.1 during the occupied period while operating under Time Clock(SCH1.  If the Time Clock(SCH2 is in use, the unit’s active set point is based on Cooling Set Point 1, Set Point(COOL(CSP.1 during the occupied period and Cooling Set Point 2, Set Point(COOL(CSP.2 during the unoccupied period.

 XE "Cooling set point selection: Set point 1" SET POINT 1 - When Set point Select Operating Modes(SLCT(SP.SE=1 (Setpoint1) is configured, the unit’s active set point is based on Cooling Set Point 1, Set Point(COOL(CSP.1.  

 XE "Cooling set point selection: Set point 2" SET POINT 2 - When Set point Select Operating Modes(SLCT(SP.SE=2 (Setpoint2) is configured, the unit’s active set point is based on Cooling Set Point 2, Set Point(COOL(CSP.2.  

 XE "Cooling set point selection: 4 to 20 mA input" 4 TO 20 mA INPUT — When Setpoint Select Operating Modes(SLCT(SP.SE=3 (4-20mA Setp) is configured, the unit’s active set point is based on an external 4 to 20 mA signal input to the Energy Management Module (EMM).

The following equation is used to control the set point. See Fig. 8.


Set Point = 10 + 70(mA – 4)/16     (deg F)


Set Point = -12.2 + 38.9(mA – 4)/16   (deg C)


[image: image16.wmf]4-20 mA Set Point Control

0

10

20

30

40

50

60

70

80

90

0

5

10

15

20

mA Signal

Equation

Medium Tempertaure Brine

Fresh Water

Fig. 8 – Set Point Control

 XE "Cooling set point selection: Dual switch" DUAL SWITCH — When Setpoint Select Operating Modes(SLCT(SP.SE=4 (Dual Setp Sw) is configured, the unit’s active set point is based on Cooling Set Point 1 (CSP1) Set Point(COOL(CSP.1 when the Dual Set Point switch contacts are open and Cooling Set Point 2 Set Point(COOL(CSP.2 when they are closed.

 XE "Cooling set point selection: Ice mode" ICE MODE – Operation of the machine to make and store ice can be accomplished many ways.  The Energy Management Module and an Ice Done Switch is required for operation in the Ice Mode.  In this configuration, the machine can operate with up to three cooling set points: Cooling Set Point 1 (Occupied) Set Point(COOL(CSP.1, Cooling Set Point 2 (Unoccupied) Set Point(COOL(CSP.2, and Ice Set Point Set Point(COOL(CSP.3.


	
	

	
	
	
	

	

	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	
	
	
	
	
	

	

	

	
	
	
	
	
	

	

	

	
	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	

	
	
	
	
	

	

	

	
	
	
	
	
	

	

	

	
	
	
	
	
	

	

	

	
	
	
	
	
	


 XE "Controls:Temperature reset" 

 XE "Temperature reset" Temperature Reset

The control system is capable of handling leaving-fluid temperature reset based on return cooler fluid temperature. Because the change in temperature through the cooler is a measure of the building load, the return temperature reset is in effect an average building load reset method. The control system is also capable of temperature reset based on outdoor-air temperature (OAT), space temperature (SPT), or from an externally powered 4 to 20 mA signal. An accessory sensor must be used for SPT reset (33ZCT55SPT).  The Energy Management Module (EMM) is required for temperature reset using space temperature or a 4 to 20 mA signal. 

Under normal operation, the chiller will maintain a constant leaving fluid temperature approximately equal to the chilled fluid set point. As the cooler load varies, the entering cooler fluid will change in proportion to the load as shown in the Return Water Reset figure. Usually the chiller size and leaving-fluid temperature set point are selected based on a full-load condition. At part load, the fluid temperature set point may be colder than required.  If the leaving fluid temperature were allowed to increase at part load, the efficiency of the machine would increase.

Return temperature reset allows for the leaving temperature set point to be reset upward as a function of the return fluid temperature or, in effect, the building load.

To use Return Water Reset, four variables must be configured.  They are: Cooling Reset Type Configuration(RSET(CRST, Delta T No Reset Temp Setpoints(COOL(CRT1, Delta T Full Reset Temp Setpoints(COOL(CRT2 and Degrees Cool Reset Setpoints(COOL(DGRC.  In the following example, 5.0 F (2.8 C) chilled water set point reset at 2.0 F (1.1 C) cooler (T (Entering Water Temperature – Leaving Water Temperature) and 0° F (0° C) reset at 10.0 F (5.6 C) cooler (T. The variable CRT.1 should be set to the cooler temperature difference ((T) where no chilled water temperature reset should occur. The variable CRT.2 should be set to the cooler temperature difference where the maximum chilled water temperature reset should occur. The variable DGRC should be set to the maximum amount of reset desired. To verify that reset is functioning correctly proceed to Run Status mode, sub-mode VIEW, and subtract the active set point (SETP) from the control point (CTPT) to determine the degrees reset. See Fig. 9 and Table 32.


[image: image17.wmf]Return Water Reset

0

1

2

3

4

5

6

0

1

2

3

4

5

6

7

8

9

10

Entering - Leaving Water Temperature (deg F)

Degrees Reset (deg F)


Fig. 9 –  XE "Temperature reset: Return water reset" Return Water Reset

Table 32  -  XE "Temperature reset: Return water reset configuration" Return Water Reset Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	[Enter]
	0
	No Reset
	

	
	[Enter]
	0
	No Reset
	Flashing to indicate Edit mode.  May require Password

	
	[↓]/[↑]
	2
	DeltaT Temp
	Use up or down arrows to change value to 2.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	CRST
	
	

	
	[Escape]
	
	
	At mode level

	Setpoints
	[↓]/[↑]
	
	
	Change to Setpoints Mode

	
	[Enter]
	COOL
	Cooling Setpoints
	

	
	[Enter]
	CSP.1
	Cooling Setpoint 1
	

	
	[↓]
	CSP.2
	Cooling Setpoint 2
	

	
	
	
	
	

	
	[↓]
	CRT1
	Delta T No Reset Temp
	Cooler Temperature difference where no temperature reset is required.

	
	[Enter]
	0
	
	Value of CRT1

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	10
	
	Value of No Temperature Reset, 10 from the example.

	
	[Enter]
	10
	
	Accepts the change.

	
	[Escape]
	CRT1
	
	

	
	[↓]
	CRT2
	Delta T Full Reset Temp
	Cooler Temperature difference where full temperature reset, DGRC is required.

	
	[Enter]
	0
	
	Value of CRT2.

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	2
	
	Value of full Temperature Reset, 2 from the example.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	CRT2
	
	

	
	[↓]
	CRO1
	
	

	
	
	
	
	

	
	[↓]
	DGRC
	Degrees Cool Reset
	Amount of temperature reset required.

	
	[Enter]
	0
	
	Value of DGRC

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	6
	
	Amount of Temperature Reset required, 6 from the example.

	
	[Enter]
	6
	
	Accepts the change.

	
	[Escape]
	DGRC
	
	


Bold values indicate sub mode level.

Other, indirect means of estimating building load and controlling temperature reset are also available and are discussed below. See Fig. 10. 


[image: image18.wmf]Chilled Water Temperature Control

40

42

44

46

48

50

52

54

56

0

10

20

30

40

50

60

70

80

90

100

% Loading

Fluid Temperature (deg F)

EWT

LWT

Design

Rise

Fig. 10 –  XE "Temperature reset:Chilled water temperature control" Chilled Water Temperature Control 

To use Outdoor Air Temperature Reset four variables must be configured.  They are: Cooling Reset Type Configuration(RSET(CRST, OAT No Reset Temp Setpoints(COOL(CRO1, OAT Full Reset Temp Setpoints(COOL(CRO2 and Degrees Cool Reset Setpoints(COOL(DGRC.  In the following example, the outdoor air temperature reset example provides 0° F (0° C) chilled water set point reset at 85.0 F (29.4 C) outdoor-air temperature and 15.0 F (8.3 C) reset at 55.0 F (12.8 C) outdoor-air temperature. See Fig. 11 and Table 33.


[image: image19.wmf]OAT Temperature Reset

0

2

4

6

8

10

12

14

16

0

20

40

60

80

100

120

Outdoor Temperature (deg F)

Reset Amount (deg F)

Fig. 11 –  XE "Temperature reset: Outdoor air temperature reset" OAT Temperature Reset

Table 33 –  XE "Temperature reset: Outdoor air temperature reset configuration table" OAT Temperature Reset Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	[Enter]
	0
	No Reset
	

	
	[Enter]
	0
	No Reset
	Flashing to indicate Edit mode.  May require Password

	
	[↓]/[↑]
	1
	Out Air Temp
	Use up or down arrows to change value to 1.

	
	[Enter]
	1
	
	Accepts the change.

	
	[Escape]
	CRST
	
	

	
	[Escape]
	
	
	At mode level

	Setpoints
	[↓]/[↑]
	
	
	Change to Setpoints Mode

	
	[Enter]
	COOL
	Cooling Setpoints
	

	
	[Enter]
	CSP.1
	Cooling Setpoint 1
	

	
	[↓]
	CSP.2
	Cooling Setpoint 2
	

	
	
	
	
	

	
	[↓]
	CRO1
	OAT No Reset Temp
	Outdoor Temperature where no temperature reset is required.

	
	[Enter]
	0
	
	Value of CRO1

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	85
	
	Value of No Temperature Reset, 85 from the example.

	
	[Enter]
	85
	
	Accepts the change.

	
	[Escape]
	CRO1
	
	

	
	[↓]
	CRO2
	OAT Full Reset Temp
	Outdoor Temperature where full temperature reset, DGRC is required.

	
	[Enter]
	0
	
	Value of CRO2.

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	55
	
	Value of full Temperature Reset, 55 from the example.

	
	[Enter]
	55
	
	Accepts the change.

	
	[Escape]
	CRO2
	
	

	
	[↓]
	CRS1
	
	

	
	[↓]
	CRS2
	
	

	
	[↓]
	DGRC
	Degrees Cool Reset
	Amount of temperature reset required.

	
	[Enter]
	0
	
	Value of DGRC

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	15
	
	Amount of Temperature Reset required, 15 from the example.

	
	[Enter]
	15
	
	Accepts the change.

	
	[Escape]
	DGRC
	
	


Bold values indicate sub mode level.

To use Space Temperature Reset in addition to the Energy Management Module, four variables must be configured.  They are: Cooling Reset Type Configuration(RSET(CRST, Space T No Reset Temp Setpoints(COOL(CRS1, Space T Full Reset Temp Setpoints(COOL(CRS2 and Degrees Cool Reset Setpoints(COOL(DGRC.  In the following example, The space temperature reset example provides 0° F (0° C) chilled water set point reset at 72.0 F (22.2 C) space temperature and 6.0 F (3.3 C) reset at 68.0 F (20.0 C) space temperature. See Fig. 12 and Table 34.


[image: image20.wmf]Space Temperature Reset

0

1

2

3

4

5

6

7

60

62

64

66

68

70

72

74

76

78

80

Space Temperature (deg F)

Degrees Reset (deg F)

Fig. 12 –  XE "Temperature reset: Space temperature reset" Space Temperature Reset

Table 34 –  XE "Temperature reset: Space temperature reset configuration" Space Temperature Reset Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	[Enter]
	0
	No Reset
	

	
	[Enter]
	0
	No Reset
	Flashing to indicate Edit mode.  May require Password

	
	[↓]/[↑]
	4
	Space Temp
	Use up or down arrows to change value to 4.

	
	[Enter]
	4
	
	Accepts the change.

	
	[Escape]
	CRST
	
	

	
	[Escape]
	
	
	At mode level

	Setpoints
	[↓]/[↑]
	
	
	Change to Setpoints Mode

	
	[Enter]
	COOL
	Cooling Setpoints
	

	
	[Enter]
	CSP.1
	Cooling Setpoint 1
	

	
	[↓]
	CSP.2
	Cooling Setpoint 2
	

	
	
	
	
	

	
	[↓]
	CRS1
	Space T No Reset Temp
	Space Temperature where no temperature reset is required.

	
	[Enter]
	0
	
	Value of CRS1

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	72
	
	Value of No Temperature Reset, 72 from the example.

	
	[Enter]
	72
	
	Accepts the change.

	
	[Escape]
	CRS1
	
	

	
	[↓]
	CRS2
	Space T Full Reset Temp
	Space Temperature where full temperature reset, DGRC is required.

	
	[Enter]
	0
	
	Value of CRO2.

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	68
	
	Value of full Temperature Reset, 68 from the example.

	
	[Enter]
	68
	
	Accepts the change.

	
	[Escape]
	CRS2
	
	

	
	[↓]
	DGRC
	Degrees Cool Reset
	Amount of temperature reset required.

	
	[Enter]
	0
	
	Value of DGRC

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	6
	
	Amount of Temperature Reset required, 6 from the example.

	
	[Enter]
	6
	
	Accepts the change.

	
	[Escape]
	DGRC
	
	


Bold values indicate sub mode level.
To use 4-20 mA Temperature Reset in addition to the Energy Management Module, four variables must be configured.  They are: Cooling Reset Type Configuration(RSET(CRST, Current No Reset Val Setpoints(COOL(CRV1, Current Full Reset Val Setpoints(COOL(CRV2 and Degrees Cool Reset Setpoints(COOL(DGRC.  In the following example, at 4 mA no reset takes place.  At 20 mA, 5° F (2.8° C) chilled water set point reset is required. See Fig. 13 and Table 35. 

	IMPORTANT: Care should be taken when interfacing with other control systems due to possible power supply differences: full wave bridge versus half wave rectification.  Connection of control devices with different power supplies may result in permanent damage.  ComfortLink™ controls incorporate power supplies with half wave rectification.  A signal isolation device should be utilized if the signal generator incorporates a full wave bridge rectifier.



[image: image21.wmf]4-20 mA Temperature Reset

0

1

2

3

4

5

6

0

2

4

6

8

10

12

14

16

18

20

mA Signal

Degrees Reset (deg F)

Fig. 13 –  XE "Temperature reset: 4 to 20mA temperature reset" 4-20mA Temperature Reset

Table 35 –  XE "Temperature reset: 4 to 20mA temperature reset configuration table" 4-20mA Temperature Reset Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	Cooling Reset Type
	

	
	[Enter]
	0
	No Reset
	

	
	[Enter]
	0
	No Reset
	Flashing to indicate Edit mode.  May require Password

	
	[↓]/[↑]
	3
	4-20 mA Input
	Use up or down arrows to change value to 3.

	
	[Enter]
	3
	
	Accepts the change.

	
	[Escape]
	CRST
	
	

	
	[Escape]
	
	
	At mode level

	Setpoints
	[↓]/[↑]
	
	
	Change to Setpoints Mode

	
	[Enter]
	COOL
	Cooling Setpoints
	

	
	[Enter]
	CSP.1
	Cooling Setpoint 1
	

	
	[↓]
	CSP.2
	Cooling Setpoint 2
	

	
	
	
	
	

	
	[↓]
	CRV1
	Current No Reset Val
	Current value where no temperature reset is required.

	
	[Enter]
	0
	
	Value of CRV1

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	4
	
	Current value for No Temperature Reset, 4 from the example.

	
	[Enter]
	4
	
	Accepts the change.

	
	[Escape]
	CRV1
	
	

	
	[↓]
	CRV2
	Current Full Reset Val
	Current value where full temperature reset, DGRC is required.

	
	[Enter]
	0
	
	Value of CRV2.

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	20
	
	Current value of full Temperature Reset, 20 from the example.


	
	[Enter]
	20
	
	Accepts the change.

	
	[Escape]
	CRV2
	
	

	
	[↓]
	CRT1
	
	

	
	
	
	
	

	
	[↓]
	DGRC
	Degrees Cool Reset
	Amount of temperature reset required.

	
	[Enter]
	0
	
	Value of DGRC

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	5
	
	Amount of Temperature Reset required, 5 from the example.

	
	[Enter]
	5
	
	Accepts the change.

	
	[Escape]
	DGRC
	
	


Bold values indicate sub mode level.
 XE "Controls: Demand limit" 

 XE "Demand limit" Demand Limit

Demand Limit is a feature that allows the unit capacity to be limited during periods of peak energy usage.  There are three types of demand limiting that can be configured.  The first type is through 2-step switch control, which will reduce the maximum capacity to 2 user-configurable percentages.  The second type is by 4 to 20 mA signal input which will reduce the maximum capacity linearly between 100% at a 4 mA input signal (no reduction) down to the user-configurable level at a 20 mA input signal.  The third type uses the CNN Loadshed module and has the ability to limit the current operating capacity to maximum and further reduce the capacity if required.

NOTE: 1-step Demand Limit is standard.  

The 2-step switch control and 4- to 20-mA input signal types of demand limiting require the Energy Management Module (EMM).

To use Demand Limit, select the type of demand limiting to use. Then configure the Demand Limit set points based on the type selected.  

 XE "Demand limit: 2-step switch controlled" DEMAND LIMIT (2-step Switch Controlled) — If using 2-step Demand Limit control, an Energy Management Module must be installed.  1-step Demand Limit control does not require the Energy Management Module.  To configure Demand Limit for 2-step switch control, three parameters must be configured; Demand Limit Select Configuration(RSET(DMDC, Switch Limit Setpoint 1 Setpoints(MISC(DLS1 and Switch Limit Setpoint 2 Setpoints(MISC(DLS2.  In the following example, Demand Limit Switch 1 is 60% and Demand Limit Switch 2 is 40%.  Demand Limit steps are controlled by two relay switch inputs field wired to TB5 for Switch 1 and TB6 for Switch 2. See Table 36.

Table 36 –  XE "Demand limit: 2-step switch controlled configuration table" 2-Step Demand Limit Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	
	

	
	[↓]
	HRST
	
	

	
	[↓]
	DMDC
	Demand Limit Select
	

	
	[Enter]
	0
	None
	

	
	[Enter]
	0
	None
	Flashing to indicate Edit mode.  May require Password

	
	[↓]/[↑]
	1
	Switch
	Use up or down arrows to change value to 1.

	
	[Enter]
	1
	
	Accepts the change.

	
	[Escape]
	DMDC
	
	

	
	[Escape]
	
	
	At mode level

	Setpoints
	[↓]/[↑]
	
	
	Change to Setpoints Mode

	
	[Enter]
	COOL
	Cooling Setpoints
	

	
	[↓]
	HEAT
	
	

	
	[↓]
	MISC
	Miscellaneous Setpoints
	

	
	[Enter]
	DLS1
	Switch Limit Setpoint 1
	

	
	[Enter]
	0
	None
	Current value for DLS1.

	
	[Enter]
	0
	None
	Flashing to indicate Edit mode.  May require Password

	
	[↑]
	60
	Switch
	Use arrows to change value to 60 from the example.

	
	[Enter]
	60
	
	Accepts the change.

	
	[Escape]
	DLS1
	
	

	
	[↓]
	DLS2
	Switch Limit Setpoint 2
	

	
	[Enter]
	0
	
	Current value of DLS2

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	40
	
	Use arrows to change the value for DLS2 to 40 from the example.

	
	[Enter]
	40
	
	Accepts the change.

	
	[Escape]
	DLS2
	
	

	
	
	
	
	

	
	[Enter]
	0
	
	Value of DGRC

	
	[Enter]
	0
	
	Flashing to indicate Edit mode

	
	[↑]
	5
	
	Amount of Temperature Reset required, 5 from the example.

	
	[Enter]
	5
	
	Accepts the change.

	
	[Escape]
	DGRC
	
	


Bold values indicate sub mode level.

For Demand Limit by 2-stage switch control, closing the first stage demand limit contact will put the unit on the first demand limit level.  The unit will not exceed the percentage of capacity entered as Demand Limit Switch 1 set point. Closing contacts on the second demand limit switch prevents the unit from exceeding the capacity entered as Demand Limit Switch 2 set point.  The demand limit stage that is set to the lowest demand takes priority if both demand limit inputs are closed.  If the demand limit percentage does not match unit staging, the unit will limit capacity to the closest capacity stage without exceeding the value.  To disable demand limit configure the DMDC to 0.

 XE "Demand limit: Externally powered demand limit" EXTERNALLY POWERED DEMAND LIMIT (4 to 20 mA Controlled) — 4-20 mA Demand Limit control requires the Energy Management Module.  To configure Demand Limit for 4 to 20 mA control three parameters must be configured.  They are: Demand Limit Select Configuration(RSET(DMDC, mA for 100% Demand Limit Configuration(RSET(DMMX and mA for 0% Demand Limit Configuration(RSET(DMZE.  In the following example, a 4 mA signal is Demand Limit 100% and a 20 mA Demand Limit signal is 0%.  The 4-20 mA signal is connected to TB6-1 and TB6-2, as shown in the 4 - 20mA Demand Relay figure. The demand limit is a linear interpolation between the two values entered. See Table 37 and Fig. 14.

	IMPORTANT: Care should be taken when interfacing with other control systems due to possible power supply differences: full wave bridge versus half wave rectification.  Connection of control devices with different power supplies may result in permanent damage.  ComfortLink™ controls incorporate power supplies with half wave rectification.  A signal isolation device should be utilized if the signal generator incorporates a full wave bridge rectifier.


Table 37 –  XE "Demand limit: Externally powered demand limit configuration table" Externally Powered Demand Limit Configuration

	Mode
	Keypad Entry
	Display
	Item Expansion
	Comment

	Configuration
	[Enter]
	DISP
	
	

	
	[↓]
	UNIT
	
	

	
	[↓]
	SERV
	
	

	
	[↓]
	OPTN
	
	

	
	[↓]
	RSET
	Reset Cool and Heat Tmp
	

	
	[Enter]
	CRST
	
	

	
	[↓]
	HRST
	
	

	
	[↓]
	DMDC
	Demand Limit Select
	

	
	[Enter]
	0
	None
	

	
	[Enter]
	0
	None
	Flashing to indicate Edit mode.  May require Password

	
	[↑]
	2
	4-20 mA Input
	Use up arrows to change value to 2.

	
	[Enter]
	2
	
	Accepts the change.

	
	[Escape]
	DMDC
	
	

	
	[↓]
	DMMX
	mA for 100% Demand Limit
	

	
	[Enter]
	0
	
	

	
	[Enter]
	0
	
	Flashing to indicate Edit mode. 

	
	[↑]
	4
	
	Use up arrows to change value to 4.

	
	[Escape]
	DMMX
	
	

	
	[↓]
	DMZE
	mA for 0% Demand Limit
	

	
	[Enter]
	0
	
	

	
	[Enter]
	0
	
	Flashing to indicate Edit mode. 

	
	[↑]
	20
	
	Use up arrows to change value to 20.

	
	[Escape]
	DMZE
	
	


Bold values indicate sub mode level.


[image: image22.wmf]4-20 mA Demand Limit

0

10

20

30

40

50

60

70

80

90

100

0

2

4

6

8

10

12

14

16

18

20

mA Demand Limit Signal 


Fig. 14 –  XE "Demand limit: Demand limit signal" Demand Limit

In Fig. 14, if the machine receives a 12 mA signal, the machine controls will limit the capacity to 50%.

 XE "Demand limit: CCN Loadshed controlled" CCN Loadshed Controlled — To configure Demand Limit for CCN Loadshed control the unit Operating Type Control must be in CCN control, Operating Modes(SLCT(SP.SE=2 and be controlled by a Chillervisor.  The Chillervisor can force the demand limit variable and directly control the capacity of the machine.  Additionally, the unit’s set point will be artificially lowered to force the chiller to load to the demand limit value.  

 XE "Controls:Remote alarm and alert relays" Remote Alarm and Alert Relays

The 30XA chiller can be equipped with a remote alert and remote alarm annunciator contacts.  Both relays connected to these contacts must be rated for a maximum power draw of 10 VA sealed, 25 VA Inrush at 24 Volts.  The alarm relay, indicating that the complete unit has been shutdown can be connected to TB5-12 and TB5-13.  See Wiring Details For an Alert Relay, indicating that at least 1 circuit was off due to the alert, a field supplied and installed relay, must be connected between MBB-J3-CH25-3 and TB5-13.

 XE "Start-up" START-Up

	CAUTION

	Do not manually operate contactors.  Serious damage to the machine may result.


The chilled water loop must be cleaned before the unit is connected.  To set the time for the parameter, go to Time Clock/MCFG/W.FIL.  Values for this item are counted as days.

 XE "Start-up:Pre-start-up" PRE-START-UP

	IMPORTANT: Before beginning Pre-Start-Up or Start-Up, complete Start-Up Checklist for ComfortLink™ Chiller

Systems at end of this publication.

The Checklist assures proper start-up of a unit, and provides a record of unit condition, application requirements, system information, and operation at initial start-up.


Do not attempt to start the chiller until following checks have been completed.

 XE "Start-up:System check" 

 XE "System check" System Check

1. Check all auxiliary components, such as the chilled fluid circulating pump, air-handling equipment, or other equipment to which the chiller supplies liquid.  Consult manufacturer’s instructions.  If the unit has field installed accessories, be sure all are properly installed and wired correctly. Refer to unit wiring diagrams.

2. Open compressor suction (if equipped) and discharge shutoff valves.

3. Open liquid line, oil line and economizer service valves.

4. Fill the chiller fluid circuit with clean water (with recommended inhibitor added) or other non-corrosive fluid to be cooled.  Bleed all air out of high points of system.  An air vent is included with the cooler.  If outdoor temperatures are expected to be below 32 F (0° C), sufficient inhibited propylene glycol or other suitable corrosion inhibited antifreeze should be added to the chiller water circuit to prevent possible freeze-up.

5. Check tightness of all electrical connections.




6. Oil separator heaters must be firmly seated under the oil separator, and must be energized for 24 hours prior to start-up.

7. Fan motors are 3 phase.  Check rotation of fans during the service test.  Fan rotation is counter clockwise as viewed from top of unit.  If fan is not turning counter clockwise, reverse 2 of the power wires at the main terminal block.  


8. Perform service test to verify proper operation.

 XE "Start-up and operation" \t "See Start-up Checklist" START-UP AND OPERATION

NOTE: Refer to Start-Up Checklist at the end of this publication.

 XE "Start-up:Actual start-up" 

 XE "Actual start-up" Actual Start-Up — Actual start-up should be done only under supervision of a qualified refrigeration mechanic.

1. Be sure all service valves are open. Units are shipped from factory with suction valves (if equipped) open. Discharge and liquid line service valves are closed.

2. Using the Navigator display, set leaving-fluid set point (CSP.1 is Set Point mode under sub-mode COOL).  No cooling range adjustment is necessary. 

3. If optional control functions or accessories are being used, the unit must be properly configured. Refer to Operating Data section for details.

4. Start chilled fluid pump, if unit is not configured for pump control, Configuration(OPTN(PUMP
5. Turn ENABLE/OFF/REMOTE CONTACT switch to ENABLE position.

6. Allow unit to operate and confirm that everything is functioning properly.  Check to see that leaving fluid temperature agrees with leaving set point Control Point Run Status/VIEW/CTPT.
 XE "Start-up:Operating limitations" 

 XE "Operating limitations" Operating Limitations

TEMPERATURES— Unit operating temperature limits are listed in Table 38.

Table 38 -  XE "Temperature limits:for standard units" Temperature Limits for Standard Units

	TEMPERATURE
	F
	C

	Maximum Ambient Temperature
	125
	52

	Minimum Ambient Temperature
	32
	0

	Maximum Cooler EWT*
	95
	35

	Maximum Cooler LWT
	60
	15

	Minimum Cooler LWT†
	40
	4.4


LEGEND

EWT — Entering Fluid (Water) Temperature

LWT — Leaving Fluid (Water) Temperature
*For sustained operation, EWT should not exceed 85 F (29.4 C).

†Unit requires modification below this temperature.

 XE "Temperature limits: Low ambient operation" Low Ambient Operation — If operating temperatures below 32° F (0 C) are expected, refer to separate installation instructions for low-ambient operation using accessory low ambient head pressure control, if not equipped.  Contact your Carrier representative for details.

NOTE: Wind baffles and brackets must be field-fabricated for all units using accessory low ambient head pressure control to ensure proper cooling cycle operation at low-ambient temperatures.  See Installation Instructions shipped with the low ambient head pressure control accessory or the 30XA unit for more information.

	CAUTION

	Brine duty application (below 40 F [4.4 C] LCWT) for chiller normally requires factory modification. Contact a Carrier Representative for details regarding your specific application. Brine operation without modification can result in compressor failure.


 XE "Operating limitations: Voltage" VOLTAGE

Main Power Supply — Minimum and maximum acceptable supply voltages are listed in the Installation Instructions.

Unbalanced 3-Phase Supply Voltage — Never operate a motor where a phase imbalance between phases is greater than 2%.

To determine percent voltage imbalance:

	% Voltage Imbalance = 100
	max voltage deviation from avg voltage

	x
	average voltage


The maximum voltage deviation is the largest difference between a voltage measurement across 2 legs and the average across all 3 legs. 

Example: Supply voltage is 240-3-60. 

AB = 243v

BC = 236v

AC = 238v

1. Determine average voltage: 

Average voltage = 243+236+238




     3



= 717



      3



= 239

2. Determine maximum deviation from average voltage: 

(AB) 243 – 239 = 4 v

(BC) 239 – 236 = 3 v

(AC) 239 – 238 = 1 v

Maximum deviation is 4 v. 

3. Determine percent voltage imbalance: 

	% Voltage Imbalance = 100 x
	               4

	
	             239




      = 1.7%

This voltage imbalance is satisfactory as it is below the maximum allowable of 2%.  

	IMPORTANT: If the supply voltage phase imbalance is more than 2%, contact your local electric utility company immediately. Do not operate unit until imbalance condition is corrected.


 XE "Operating limitations: Minimum fluid loop volume" 

 XE "Minimum fluid loop volume" MINIMUM FLUID LOOP VOLUME — To obtain proper temperature control, loop fluid volume must be at least 3 gallons per ton (3.25 L per kW) of chiller nominal capacity for air conditioning and at least 6 gallons per ton (6.5 L per kW) for process applications or systems that must operate at low ambient temperatures (below 32 F [0° C]).  Refer to application information in Product Data literature for details.

 XE "Operating limitations: Flow rate requirements" 

 XE "Minimum fluid loop volume" FLOW RATE REQUIREMENTS — Standard chillers should be applied with nominal flow rates approximating those listed in the Minimum and Maximum Cooler Flow Rates table. Higher or lower flow rates are permissible to obtain lower or higher temperature rises. Minimum flow rates must be exceeded to assure turbulent flow and proper heat transfer in the cooler. See Table 39.
[image: image23.png]COOLER PRESSURE DROP CURVES
20XA080-120

20XA140-240







	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	



	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	


[image: image24.wmf]
	

	


Consult application data section in the Product Data literature and job design requirements to determine flow rate requirements for a particular installation.
MD01 – Startup Delay in Effect

Criteria for Mode:
Tested when the unit is started.  This mode is active when the Minutes Off Time Configuration→OPTN→DELY timer is active.

Action taken:
The unit will not start until the timer has expired.

Termination:
The mode will terminate when the timer expires.
Possible Causes:
This mode is in effect only due to the Minutes Off Time timer.

MD02 – Second Setpoint in Use

Criteria for Mode:
Tested when the unit is ON.  This mode is active when Cooling Setpoint 2 Setpoints→COOL→CSP.2, or Ice Setpoint Setpoints→COOL→CSP.3, is in use.  While in this mode, the Active Setpoint Run Status→VIEW→SETP will show the CSP.2 or CSP.3 value.

Action taken:
The unit will operate to the Cooling Setpoint 2 CSP.2 or Ice Setpoint, CSP.3.

Termination:
This mode will terminate when the Cooling Setpoint 2 CSP.2 or Ice Setpoint CSP.3 is no longer in use.
Possible Causes:
This mode is in effect only due to programming options.

MD03 – Reset in Effect

Criteria for Mode:
Tested when the unit is ON.  This mode is active when Temperature Reset Configuration→RSET→CRST is enabled either by CRST=1 (Outside Air Temperature), CRST=2 (Return Water), CRST=3 (4-20 mA Input), or CRST=4 (Space Temperature) and is active.

Action taken:
The Active Setpoint Run Status→VIEW→SETP will be modified according to the programmed information and will be displayed as the Control Point Run Status→VIEW→CTPT.

Termination:
This mode will terminate when the Temperature Reset is not modifying the active leaving water set point, so SETP is the same as CTPT.
Possible Causes:
This mode is in effect only due to programming options.

MD04 – Demand Limit Active

Criteria for Mode:
Tested when the unit is ON.  This mode is active when Demand Limit Configuration→RSET→DMDC is enabled either by DMDC=1 (Switch), DMDC=2 (4-20 mA Input) or the Night Time Low Sound Capacity Limit Configuration→OPTN→LS.LT.

Action taken:
The Active Demand Limit Value Run Status→VIEW→LIM will be display the current demand limit according to the programmed information and the units capacity will be reduced to the amount shown or less, since it will not exceed the value.

Termination:
This mode will terminate when the Demand Limit command has been removed.

Possible Causes:
This mode is in effect only due to programming options.

MD05 – Ramp Loading Active

Criteria for Mode:
Tested when the unit is ON.  This mode is active when Ramp Loading Configuration→OPTN→RL.S is enabled and the following conditions are met:

1. The leaving water temperature is more than 4 F (2.2 C) from the Control Point Run Status→VIEW→CTPT, and

2. The rate of change of the leaving water temperature is greater than the Cool Ramp Loading Set Points→COOL→CRMP.

Action taken:
The control will limit the capacity step increase until one of the two conditions is no longer true.  

Termination:
This mode will terminate once both conditions above are no longer true. 
Possible Causes:
This mode is in effect only due to programming options.

MD06 – Cooler Heater Active

Criteria for Mode:
Tested when unit is ON or OFF.  This mode is active when the cooler heater is energized, if the Outdoor Air Temperature Temperature→UNIT→OAT is less than the calculated value, Freeze Setpoint + Cooler Heater Delta T Setpoint Configuration→SERV→HTR – 2 F (1.1 C) and either the Leaving Water Temperature Temperature→UNIT→LWT or the Entering Water Temperature Temperature→UNIT→EWT is less than or equal to Freeze Setpoint + Cooler Heater Delta T Setpoint HTR.


The Freeze Setpoint is 34 F (1.1 C), for fresh water systems, Configuration→SERV→FLUD=1.  The Freeze Setpoint is Brine Freeze Setpoint Configuration→SERV→LOSP, for Medium Temperature Brine systems, Configuration→SERV→FLUD=2.

Action taken:
The cooler heater will be energized.

Termination:
The cooler heater will be de-energized when both the Entering Water Temperature EWT and Leaving Water Temperature LWT are above the Freeze Setpoint + Cooler Heater Delta T Setpoint HTR.
Possible Causes:
This mode will be enabled for real conditions.  If the temperatures are not as described above, check the accuracy of the Outside Air, Entering and Leaving Water thermistors.

MD07 – Water Pump Rotation

Criteria for Mode:
Tested when the unit is ON or OFF.  This mode is active when the Cooler Pump Sequence Configuration→OPTN→PUMP=2 (2 Pumps Automatic Changeover) and the Pump Rotation Delta Timer Configuration→OPTN→ROT.P has been reached.

Action taken:
The control will switch the operation of the pumps.  The lead pump will be operating normally.  The other pump will be started, and then the old lead pump will be shutdown.

Termination:
This mode will terminate when the pump operation has been completed.
Possible Causes:
This mode is in effect only due to programming options.

MD08 – Pump Periodic Start

Criteria for Mode:
This mode is active when the cooler pump is started for the Periodic Pump Start configuration, Configuration Mode→OPTN→PM.PS=YES.

Action taken:
If the pump has not run that day, a pump will be started and run for 2 seconds at 2:00 PM.  If the machine is equipped with dual pumps, Pump #1 will run on even days.  Pump #2 will run on odd days.

Termination:
This mode will terminate when the pump shuts down.
Possible Causes:
This mode is in effect only due to programming options.

MD09 – Night Low Noise Active

Criteria for Mode:
This mode is active when the Night Time Low Noise Option has been configured and the time is within the configured time.  Programming a Night Low Noise Start Time, Configuration→OPTN→LS.ST and a Night Low Noise End Time, Configuration Mode→OPTN→LS.ND configures the option.

Action taken:
The control will raise the head pressure set point to reduce the number of condenser fans on, thereby reducing the sound of the machine.  Additionally, if the Night Time Low Sound Capacity Limit Configuration→OPTN→LS.LT has been configured, the units capacity will be limited to the programmed level.

Termination:
This mode will terminate once the Night Low Noise End Time LS.ND has been reached.
Possible Causes:
This mode is in effect only due to programming options.

MD10 – System Manager Active

Criteria for Mode:
Tested when the unit is ON or OFF.  This mode is active if a System Manager such as Building Supervisor, Chiller System Manager, or another CCN device is controlling the machine.

Action taken:
The machine will respond to the specific command received from the System Manager.

Termination:
The mode will be terminated if the System Manager control is released.
Possible Causes:
This mode is in effect only due to programming options.

MD11 – Mast Slave Ctrl Active

Criteria for Mode:
Tested if the machine is ON.  This mode is active if the Master Slave Control has been enabled.  Having 2 machines programmed, one as the master, Configuration→RSET→MSSL=1 (Master) and the other as a slave, Configuration→RSET→MSSL=2 (Slave).

Action taken:
Both the master and slave machine will respond to the capacity control commands issued by the master controller.  This may include, control point changes and demand limit commands.

Termination:
This mode will terminate when the Master Slave Control has been disabled.
Possible Causes:
This mode is in effect only due to programming options.

MD12 – Auto Changeover Active

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD13 – Free Cooling Active

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD14 – Reclaim Active

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD15 – Electric Heat Active

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD16 – Heating Low EWT Lockout

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD17 – Boiler Active

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD18 – Ice Mode in Effect

Criteria for Mode:
Tested when the unit is ON.  This mode is active when Ice Setpoint Setpoints→COOL→CSP.3, is in use.  While in this mode, the Active Setpoint Run Status→VIEW→SETP will show the CSP.3 value.

Action taken:
The unit will operate to the Ice Setpoint, CSP.3.

Termination:
This mode will terminate when the Ice Setpoint CSP.3 is no longer in use.
Possible Causes:
This mode is in effect only due to programming options.

MD19 – Defrost Active on Cir A

MD20 – Defrost Active on Cir B

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD21 – Low Suction Circuit A

MD22 – Low Suction Circuit B

MD23 – Low Suction Circuit C
Criteria for Mode: 
The criteria are tested when the circuit is ON.  The appropriate circuit mode will be active if one of the following conditions is true:

1. If the circuit’s Saturated Suction Temperature (SST) is more than 6 F (3.3 C) less than the freeze point and both the cooler approach (Leaving Water Temperature-SST) and discharge superheat (Discharge Gas Temperature-SDT) are greater than 25 F (8.3 C).  

2. If there is more than 1 compressor ON in the circuit and the circuit’s SST is more than 18 F (10.0 C) less than the freeze point for more than 90 seconds.

3. If there is more than 1 compressor ON in the circuit and the circuit’s SST is more than -4 F (-20.0 C) and the SST 30 seconds ago was 18 F (10.0 C) less than the freeze point.

4. If the circuit’s saturated suction temperature is more than 6 F (3.3 C) less than the freeze point for more than 3 minutes.  
For a fresh water system Configuration→SERV→FLUD=1, the freeze point is 34 F (1.1 C).  For medium temperature brine systems, Configuration→SERV→FLUD=2, the freeze point is Brine Freeze Set Point Configuration→SERV→LOSP.
Action taken: 
For criterion 1, no additional capacity will be added.  For criteria 2, 3 and 4, Capacity will be removed.

Termination: 
The mode will terminate when the circuit’s Saturated Suction Temperature is greater than the freeze point minus 6 F (3.3 C) or the circuit has alarmed.
Possible Causes:
If this condition is encountered, see Possible Causes for Alarms P.05, P.06, and P.07.

MD24 – High DGT Circuit A

MD25 – High DGT Circuit B

MD26 – High DGT Circuit C

Criteria for Mode:
This mode is not supported for Cooling Only units.

Action taken:
None.

Termination:
None.
Possible Causes:
This mode is in effect only due to programming options.

MD27 – High Pres Override Cir A

MD28 – High Pres Override Cir B

MD29 – High Pres Override Cir C

Criteria for Mode:
Tested when the circuit is ON.  The appropriate circuit mode will be active if the discharge pressure for the circuit, Discharge Pressure Circuit A, Pressure→PRC.A→DP.A, Discharge Pressure Circuit B, Pressure→PRC.B→DP.B, or Discharge Pressure Circuit C, Pressure→PRC.A→DP.C, is greater than the High Pressure Threshold Configuration→UNIT→HP.TH.

Action taken:
The capacity of the affected circuit will be reduced.  If the unit is equipped with Minimum Load Control and has been configured for High Ambient Configuration→UNIT→HGBP=3, the minimum load control valve will be energized.  Two minutes following the capacity reduction, the circuit’s saturated condensing temperature (SCTt+2) is calculated and stored.  The affect circuit will not be allowed to add capacity for at least 5 minutes following the capacity reduction.  If after the 5 minutes, the circuit’s saturated condensing temperature is less than SCTt+2 – 3 F (1.7 C) then if required, another stage of capacity will be added.


If additional steps of capacity are required, the control will look for other circuits to add capacity.

Termination:
This mode will terminate once the circuit’s saturated condensing temperature is less than SCTt+2 – 3 F (1.7 C).

Possible Causes:
If this condition is encountered, see Possible Causes for Alarm A1.03.

MD30 – Low Superheat Circuit A

MD31 – Low Superheat Circuit B

MD32 – Low Superheat Circuit C

Criteria for Mode:
Tested when the circuit is ON.  The appropriate circuit mode will be active is the circuit’s superheat is less than 18 F (10 C).

Action taken:
No additional stages of circuit capacity will be added until the circuit’s superheat is greater than 18 F (10.0 C).


If additional steps of capacity are required, the control will look for other circuits to add capacity.

Termination:
This mode will terminate once the affected circuit’s superheat is greater than 18 F (10.0  C).
Possible Causes:     
If this condition is encountered, see Possible Causes for Alarms P.11, P.12 and P.13.

MD33– High Compressor current Circuit A

MD34– High Compressor current Circuit B

MD35– High Compressor current Circuit C

Criteria for Mode:
Tested when the circuit is ON with at least 1 compressor ON.  The appropriate circuit mode will be active is the circuit’s current 

Action taken:
No additional  circuit capacity will be added if  the circuit’s current is greater than 79 % of MTA value for the compressor.

If additional capacity is required, the control will look for other circuits to add capacity.

Termination:
This mode will terminate once the affected circuit compressor current is less than 79 % MTA value.
Possible Causes:     
If this condition is encountered low voltage to unit, loose compressor connection, loose connection on compressor current transformer, or bad motor
Sensors  -  The electronic control uses up to 17 thermistors to sense temperatures and 12 transducers to sense pressure foir controlling the chiller operation. These sensors are outlined below. 

THERMISTORS  - Thermistors that are monitoring the chiller include: Cooler Entering Water, Cooler Leaving Water, Dual Chiller Leaving Water, Outdoor Air Temperature, Compressor Suction Gas, Compressor Discharge Gas, Economizer Gas, Compressor Motor. These thermistors are 5 kohm at 77 F(25C) and are identical in temperature vs resistance. The  Space Temperature Thermistor is 10 kohms at 77 F(25C) and has a different temperature vs resistance curve.

Cooler Leaving Water sensor – On all sizes, this thermistor is installed in a friction fit well in the leaving water nozzle of the cooler. See fig below 
Cooler Entering Water sensor – On all sizes, this thermistor is installed in a friction fit well in the entering water nozzle of the cooler.

[image: image25.png]ORING — ~BRASS NUT 38 -24 FOR
'ASSEMEBLY ON BRASS WELL

Fig. 31 — 5K Thermistor

) =

11418 NPT

& MINMUM —
CLEARANCE FOR 1188in—
= THERMISTOR 2815in——
REMOVAL

Fig. 32 — Dual Leaving Water Thermistor Well




Compressor Return Gas sensor – On all sizes, this thermistor is installed in a friction fit well located in the compressor suction. There is one sensor for each circuit.  

Compressor Discharge Gas sensor – On all sizes, this thermistor is installed in a friction fit well located in the compressor discharge end of the compressor. There is one sensor for each circuit.  

Economizer Gas sensor – On all sizes, this thermistor is installed in a friction fit well located in the economizer line of each circuit. There is one sensor for each circuit.
Compressor Motor Temperature – On all sizes, this thermistor is imbedded in the motor winding of each compressor and terminals are located in the compressor electrical box. There is one sensor for each circuit.
Outdoor Air Temperature - – On all sizes, this thermistor located behind the control box. There is one sensor per unit

Table 42 — Thermistor Identification

	THERMISTOR ID
	DESCRIPTION
	RESISTANCE AT 77 F (25 C)
	CONNECTION POINT

	EWT
	Entering Water Thermistor
	5k ~
	MBB-J6-CH2

	LWT
	Leaving Water Thermistor
	5k ~
	MBB-J6-CH1

	OAT
	Outdoor Air Thermistor
	5k ~
	MBB-J6-CH4

	SGTA
	Circuit A Suction Gas Thermistor
	5k ~
	EXVA-J3, THA

	SGTB
	Circuit B Suction Gas Thermistor
	5k ~
	EXVB-J3, THA

	SGTC
	Circuit C Suction Gas Thermistor
	5k ~
	EXVC-J3, THA

	DGTA
	Circuit A Discharge Gas Thermistor
	5k ~
	TCPMA-J9-CH2

	DGTB
	Circuit B Discharge Gas Thermistor
	5k ~
	TCPMB-J9-CH2

	DGTC
	Circuit C Discharge Gas Thermistor
	5k ~
	TCPMC-J9-CH2

	ECTA
	Circuit A Economizer Thermistor
	5k ~
	EXVA-J3, THB

	ECTB
	Circuit B Economizer Thermistor
	5k ~
	EXVB-J3, THB

	ECTC
	Circuit C Economizer Thermistor
	5k ~
	EXVC-J3, THB


	CAMT
	Circuit A Motor Thermistor
	5k ~
	CPMA – J9-CH1

	CBMT
	Circuit B Motor Thermistor
	5k ~
	CPMB – J9-CH1

	CCMT
	Circuit C Motor Thermistor[image: image26.png]Table 43A — 5K Thermistor Temperature (°F) vs Resistance

TEWP | RESISTANCE TEWP [ RESISTANCE TEMP | RESISTANCE
® | (©hms) F) F) Ohms)
=25 | om0 43 T.190
21 | eapor 141 1168
23 | otse 145
2 | sga 146
21 85.486 147
20 | ser 148
S | men 149
-8 | 17212 150
-7 | ragas 151
-6 | 1275 152
-5 | 370 153
-1 | eram 154
-3 | esor2 188
Sz | oe3is 126
11 61070 157
EIN -t 158
o | srie2 159
8 | ssan 160
7 | s3se 161
5| stens 162
= | sz 163
- | assa 164
3| 40w 165
2 | a5 166
El 44066 167
[ 12679 168
1 1339 169
2 0047 170
3 38,800 171
1 37596 172
5 36435 173
8 31 171
7 34231 175
8 3188 178
9 2176 177
10 31202 178
11 30260 179
12 29351 180
13 28473 181
1 27624 182
15 26804 183
16 26011 184
17 25215 185
18 24505 186
19 23780 187
20 23008 188
21 22427 189
2 21779 190
2 21153 191
2 205847 192
2 19,960 193
2 10,303 194
27 18,843 195
2 18,311 196
29 17,795 197
30 17,207 198
31 16614 199
32 16,345 200
33 15,802 201
3 15,453 202
35 15,027 203
36 14614 204
37 14,214 208
38 13,626 208
39 12,419 207
a0 13,084 208
a1 12730 209
a2 12,387 210
43 12,052 211
a1 11,730 212
5 11,418 213
8 10112 211
a7 10816 218
a8 10,529 218
a9 10,250 217
50 9979 218
51 ar1r 219
52 9481 220
53 9212 221
5 8973 222
85 8730 223
56 8511 224
57 8291 225
58 8076




	5k ~
	CPMC – J9-CH1


[image: image27.png]Table 43A — 5K Thermistor Temperature (°F) vs Resistance

TEWP | RESISTANCE TEWP [ RESISTANCE TEMP | RESISTANCE
® | (©hms) F) F) Ohms)
=25 | om0 43 T.190
21 | eapor 141 1168
23 | otse 145
2 | sga 146
21 85.486 147
20 | ser 148
S | men 149
-8 | 17212 150
-7 | ragas 151
-6 | 1275 152
-5 | 370 153
-1 | eram 154
-3 | esor2 188
Sz | oe3is 126
11 61070 157
EIN -t 158
o | srie2 159
8 | ssan 160
7 | s3se 161
5| stens 162
= | sz 163
- | assa 164
3| 40w 165
2 | a5 166
El 44066 167
[ 12679 168
1 1339 169
2 0047 170
3 38,800 171
1 37596 172
5 36435 173
8 31 171
7 34231 175
8 3188 178
9 2176 177
10 31202 178
11 30260 179
12 29351 180
13 28473 181
1 27624 182
15 26804 183
16 26011 184
17 25215 185
18 24505 186
19 23780 187
20 23008 188
21 22427 189
2 21779 190
2 21153 191
2 205847 192
2 19,960 193
2 10,303 194
27 18,843 195
2 18,311 196
29 17,795 197
30 17,207 198
31 16614 199
32 16,345 200
33 15,802 201
3 15,453 202
35 15,027 203
36 14614 204
37 14,214 208
38 13,626 208
39 12,419 207
a0 13,084 208
a1 12730 209
a2 12,387 210
43 12,052 211
a1 11,730 212
5 11,418 213
8 10112 211
a7 10816 218
a8 10,529 218
a9 10,250 217
50 9979 218
51 ar1r 219
52 9481 220
53 9212 221
5 8973 222
85 8730 223
56 8511 224
57 8291 225
58 8076



 [image: image28.png]Table 43B — 5K Thermistor Temperature (-C) vs Resistance/Voltage

TENP [RESISTANCE TENP [RESISTANCE TEP [RESTANCE

(Ohms} (Ohms}
100,260 2 T55 &
atl6s 16 7499 6
88480 17 7,161 6
83170 18 6840 6
78125 19 6,536 8
73580 20 6248 &
60.250 21 5571 &8
65,205 22 5710 6
61420 23 5401 7
57875 21 5225 7
54,555 25 5000 72
51450 2 4786 73
48530 27 4583 7
5807 28 4389 75
43047 29 4204 76
40845 30 4028 el
38892 31 361 78
38470 32 37101 79
34489 33 3549 80
32521 31 3404 81
30,860 35 3266 82
20216 36 31 83
27,533 37 3008 81
26,202 38 2888 85
24857 39 2173 8
23532 a0 2683 87
22313 a1 2,559 88
21183 a2 2459 89
20079 43 2363 90
4 212 of
5 2184 a2
8 2101 a3
a7 2021 o
8 1944 9
49 1871 %
50 1801 a7
51 1734 o8
52 1670 99
53 1609 100
54 15650 101
55 1493 102
56 1439 103
57 1387 104
58 1337 108
59 1290 106
80 1244 107

61 1200






 XE "Service: Refrigerant feed components" 

 XE "Refrigerant feed components"Economizer Assembly  — Each circuit on the 30XA090-500 has an Economizer assembly.

[image: image52.wmf]Valve Handle

Locking  Device

Valve in Locked Position

Valve in Unlocked Position

Suction Service Valve Locking Device

Valve Handle

Locking  Device

Valve in Locked Position

Valve in Unlocked Position

Suction Service Valve Locking Device

Valve Handle

Locking  Device

Valve in Locked Position

Valve in Unlocked Position

Suction Service Valve Locking Device

Valve Handle

Locking  Device

Valve in Locked Position

Valve in Unlocked Position

Suction Service Valve Locking Device


The Economizer assembly is made up of 4 major components

· Main EXV

· Economizer EXV

· Braze Plate HeatExchanger 

· Filter Drier

· Main Liquid Line Shutoff Valve

 XE "Service: Electronic expansion valve (EXV)"  XE "Refrigerant feed components: Electronic expansion valve"

 XE "Electronic expansion valve"ELECTRONIC EXPANSION VALVE (EXV) — See Fig. 15 for a cutaway view of the EXV and Economizer EXV valve. High-pressure liquid refrigerant enters valve through the top.  As refrigerant passes through orifice, pressure drops and refrigerant changes to a 2-phase condition (liquid and vapor).  To control refrigerant flow for different operating conditions, an actuator moves up and down over orifice and modulates orifice size.  A sleeve is moved by a linear stepper motor.  Stepper motor moves in increments and is controlled directly by EXV module.  As stepper motor rotates, motion is transferred into linear movement by lead screw.  Through stepper motor discrete steps of motion are obtained.  The large number of steps and long stroke results in very accurate control of refrigerant flow. 

[image: image29.png]15 Vil pt





Fig. 15 –  XE "Electronic expansion valve: Cutaway view of" Cutaway View of the EXV Valve

The EXV module for each circuit controls both the Main EXV and Economizer EXV for each circuit.

Main EXV Control - Each circuit has a thermistors located in a well in the discharge of the compressor (DGT) and another one located in the compressor motor cavity (SGT). Each circuit also has discharge and suction pressure transducer.  Discharge and Suction pressure as measured by the transducers are converted to a saturated temperatures. The main control logic for the EXV uses discharge superheat to control the position of the EXV.  The difference between the temperature of the discharge gas and the saturated discharge temperature is the superheat.  The EXV module controls the position of the electronic expansion valve stepper motor to maintain discharge superheat set point. 

The EXV control logic has several overrides, which are also used to control the position of the EXV. 

· Pinch between SST and LWT

· MOP- Maximum Operating Pressure

Pinch(Approach) – If the Approach which is the delta between leaving fluid temperature and Saturated Suction temperature is equal to or less than the pinch setpoint then the EXV will not open any further even though discharge superheat setpoint is not met. Pinch setpoint is calculated using Suction superheat, discharge superheat and pinch offset. Pinch offset is used to adjust calculated pinch setpoint do to accuracy of transducers and thermistors.

 MOP - The EXV is also used to limit cooler saturated suction temperature to 50 F (10 C). This makes it possible for the chiller to start at higher cooler fluid temperatures without overloading the compressor.  This is commonly referred to as MOP (maximum operating pressure). If the SST is equal to or greater than  the MOP setpoint then the MBB will try to control the EXV position to maintain the MOP setpoint which willl result in discharge superheat to meeting setpoint.

The discharge superheat leaving the compressor is maintained between approximately 18 ° to 25° F (10° to 14° C), or less.  Because EXV status is communicated to the Main Base Board (MBB) and is controlled by the EXV modules, it is possible to track the valve position.  The unit is then protected against loss of charge and a faulty valve.  During initial start-up, EXV is fully closed. After initialization period, valve position is tracked by the EXV module by constantly monitoring amount of valve movement.

Economizer EXV Control – The economizer EXV is controlled by the circuit EXV board. There is an economizer gas temperature thermistor and economizer pressure transducer located in the line, which runs from the economizer assembly to the compressor. The economizer pressure is converted to saturated temperature and is used to calculate economizer superheat. Economizer superheat equals economizer temperature minus saturated economizer temperature. The economizer EXV is only operation during normal conditions when the capacity of the circuit is approximately 75 % plus or minus 5 % capacity. Once the capacity of the circuit is greater than 75 % the MBB will start controlling the Economizer EXV to maintain economizer superheat setpoint, which is approximately 8 ° to 12° F (4.4° to 6.7° C). If the circuit capacity is less than 75 % the economizer EXV will be closed. 

The economizer EXV has one override. If the discharge gas temperature exceeds 195 F the economizer EXV will start to open. The EXV will be controlled to maintain discharge gas temperature at approximately 195 F.

If it appears that Main EXV or Economizer EXV is not properly controlling circuit operation to maintain correct superheat, there are a number of checks that can be made using test functions and initialization features built into the microprocessor control.  See the Service Test section to test EXVs.

 XE "Electronic expansion valve: Troubleshooting procedure" EXV Troubleshooting Procedure — Follow steps below to diagnose and correct EXV problems.  Check EXV motor operation first. Switch the Enable/Off/Remote (EOR) Contact switch to the Off position.  Press [ESCAPE] on the Navigator until a blank screen is on the display.  Use the arrow keys to select the Service Test mode and press [ENTER].  The display will be TEST.  Use the arrow keys until display shows QUIC.  Press [ENTER] (password entry may be required) and use [(] or [(] to change OFF to ON.  Switch the EOR switch to Enable.  The Quick Test mode is now enabled.  Move the arrow down to the appropriate valve and circuit and press [ENTER].  see table below. The current value of 0 will be displayed.  Press [ENTER] and the value will be flashing.  Using the [(] increase the EXV position to select 100% valve position (hold [(] for quick movement) and press [ENTER].  You should be able to feel the actuator moving by placing your hand on the EXV.  Press [ENTER] again twice if necessary to confirm this has occurred.  This will attempt to force the EXV to 100% again.  To close the valve, press [ENTER], select 0% with [(] and press [ENTER]. The actuator should knock when it reaches the bottom of its stroke.  If it is believed that the valve is not working properly, continue with the following test procedure:

· Service Test Mode/QUIC/EXV.A  - EXV A
· Service Test Mode/QUIC/EXV.B  - EXV B
· Service Test Mode/QUIC/EXV.C  - EXV C
· Service Test Mode/QUIC/ECO.A  - ECONOMIZER EXV A
· Service Test Mode/QUIC/ECO.B  - ECONOMIZER EXV B
· Service Test Mode/QUIC/ECO.C  - ECONOMIZER EXV C
EXV and Economizer Quicktest Access
Check the 8-position DIP switch on the board for the proper address. Check the EXV output signals at appropriate terminals on the EXV module.  

Connect positive test lead to EXV x-J2A terminal 5 for EXV X and EXV X-J2B terminal 5 for Economizer EXV.  Set meter to approximately 20 vdc. Using the Service Test procedure above, move the valve output under test to 100%.  DO NOT short meter leads together or pin 5 to any other pin, as board damage will occur.  During the next several seconds, carefully connect the negative test lead to pins 1,2,3 and 4 in succession.  Digital voltmeters will average this signal and display approximately 6 vdc.  If the output remains at a constant voltage other than 6 vdc or shows 0 volts, remove the connector to the valve and recheck.

There are two different size Economizer EXVs  both of them have total number of steps is 2785.  There are 3 different size Main EXVs all of them have a total number of steps 3690. The EXV motor moves at 150 steps per second.  Commanding the valve to either 0% or 100% will add extra 160 steps to the move, to ensure the value is open or closed completely. 

Press [ENTER] and select 0% to close the valve.  See the EXV Input/Outputs table.  If a problem still exists, replace the EXV module.  If the reading is correct, the expansion valve and EXV wiring should be checked.  Check the EXV terminal strip and interconnecting wiring.

1. Check color-coding and wire connections.  Make sure they are connected to the correct terminals at the EXV driver and EXV plug and that the cables are not crossed. 

2. Check for continuity and tight connection at all pin terminals.  

Check the resistance of the EXV motor windings. Remove the EXV module plug EXVX-J2A for Main EXV and EXV-J2B for economizer EXV and check the resistance of the two windings between pins 1 and 3 for one winding and pins 2 and 4 for the other winding. The resistance should be 52 ohms ± 5.2 ohms.

 XE "Electronic expansion valve: Inspecting/opening" INSPECTING/OPENING ELECTRONIC EXPANSION VALVES

	Important:  Obtain replacement gasket before opening EXV.  Do not re-use gaskets.


To check the physical operation of an EXV, the following steps must be performed.

1. Close the liquid line service valve of the circuit to be checked.  Put the Enable/Off/Remote Contact switch in the Off position.  Using the Navigator, enter the Service Test mode and change Service Test/TEST/T.REQ from OFF to ON.  A password may be required.  Switch the EOR switch to the Enable position.  Under the COMP sub-mode, enable the one of the compressors (Service Test/TEST/CP.xn) for the circuit.  Let compressor run until gage on suction pressure port reads 10 psig. Press [ENTER], [(] and [ENTER] to turn the compressor off.  The compressor will turn off.  Immediately after the compressor shuts off, close the discharge valve and liquid line service valve. If the unit is equipped with Suction service valves and economizer service valves close both valves this will minimize the amount of charge that will have to be removed from the system after pump down.
2. Remove any remaining refrigerant from the system low side and economizer assembly by using proper reclaiming techniques.  The economizer assembly has a ¼ schraeder which can be used to remove charge from the inlet of the EXVs. Turn off the line voltage power supply to the compressors.
CAUTION – Insure refrigerant is removed from both inlet and outlet of EXV assemblies

3. The expansion valve motor is hermetically sealed inside the top portion of the valve.  See Fig. 15. Carefully unscrew the 1‑1/16 in. (27 mm) retaining nut securing the motor portion to the body of the valve making sure the EXV plug is still connected.  The EXV operator will come out with the motor portion of the device.

4. Enter the appropriate EXV test step under the Service Test/QUIC sub-mode in the Service Test mode.  Locate the desired item Service Test/QUIC/EXV.A or ECO.A, Service Test/QUIC/EXV.B or ECO.B, or Service Test/QUIC/EXV.C or ECO.C.  Press [ENTER] twice to make the valve position of 0% flash.  Press and hold [(] until 100% is displayed and press [ENTER].   Observe the operation of the lead screw.  See Fig. 15.  The motor should be turning, raising the operator closer to the motor. Motor actuator movement should be smooth and uniform from fully closed to fully open position.  Press [ENTER] twice, use [(] to select 0% and press [ENTER] again to check open to closed operation.  If the valve is properly connected to the processor and receiving correct signals, yet does not operate as described above, the sealed motor portion of the valve should be replaced.

 XE "Electronic expansion valve: Installing motor" INSTALLING EXV MOTOR

	Important:  Obtain replacement gasket before opening EXV.  Do not re-use gaskets.


If re-installing the motor, be sure to use a new gasket in the assembly.  It is easier to install the motor assembly with the lead screw in the fully closed position.  Using the steps outlined above, move the EXV position to 0.  Insert the motor into the body of the EXV.  Tighten the motor to the body to 36 ft-lbs (50 N-m) and then tighten the valve another 30º.  

 XE "Electronic expansion valve: Moisture liquid indicator" Moisture Liquid Indicator — Clear flow of liquid refrigerant indicates sufficient charge in system. Bubbles in the sight glass indicate undercharged system, system operating with out all condenser fans operating, high filter drier pressure drop or presence of non-condensables.  If  the sightglass is flashing and all condenser fans are not operating it is recommended to increase discharge pressure on the unit by blocking part of each condensor coil until all condenser fans are operating.  Moisture in system measured in parts per million (ppm), changes color of indicator. See Table 39a. Change filter drier at first sign of moisture in system.

Table 39 – Color Indicators when Moisture is Present in Refrigerant

	
	R-134A, 75 F (24 C)
	R-134A , 125 F (52 C)

	Green – Dry
	< 8
	<12

	Yellow-green  - Caution
	8-66
	12-95

	Yellow – Wet
	>66
	>95


 XE "Electronic expansion valve: Filter drier" Filter Drier — Whenever moisture-liquid indicator shows presence of moisture, replace filter drier(s). There is one filter drier assembly  on each circuit with either one core or two cores. 80-120 One core per circuit. 140,160 two cores circuit A one core circuit B, 180-500 two cores per circuit.
	


 Refer to Carrier Standard Service Techniques Manual, Chapter 1, Refrigerants, for details on servicing filter driers.

 XE "Electronic expansion valve: Liquid line service valve" Liquid Line Service Valve — This valve is located immediately ahead of filter drier, and has a 1/4-in. Schrader connection for field charging.  In combination with compressor discharge service valve, each circuit can be pumped down into the high side for servicing.

	IMPORTANT: Unit must be in operation at least 12 hours before moisture indicator can give an accurate reading.

With unit running, indicating element must be in contact with liquid refrigerant to give true reading.


Compressor Assembly
The 30XA units utilize screw compressors with modulating slide valve which varies capacity from 30 % of compressor capacity to 100 % of compressor capacity for each circuit. Figure below shows typical 06T compressor.  The slide valve position is varied by opening and closing the 2 solenoid valves located on the compressor. To unload the compressor both solenoids are deenergized. To increase in capacity both solenoid valves are energized together which will cause the slide valve to slide towards the fully loaded position. To stop the loading process  solenoid 2 is energized and solenoid one is deenergized. This will cause the slide valve to maintain its current position. There is no positive feedback for position of the slide valve, the control utilizes compressor amps as an indicator of the slide valve position. Once the calculated position of the slide valve reaches 100 % circuit capacity the control will try to increase capacity again if compressor current continues to increase the control will continue to load the  compressor until compressor current no longer increases at this time the control will energize both solenoids and the circuit will be considered fully loaded.  
Typical 06T Compressor
[image: image53.wmf]Oil Pressure Transducer 

(OPT A)

Oil Pressure Transducer 

(OPT B)

Suction  Pressure 

Transducer (SPT B)

Suction Pressure 

Transducer (SPT A)

Discharge  Pressure 

Transducer (DPT A)

Discharge  Pressure 

Transducer (DPT B)

Economizer Pressure 

Transducer (EPT B)

Economizer Pressure 

Transducer (EPT A)

Oil Pressure Transducer 

(OPT A)

Oil Pressure Transducer 

(OPT B)

Suction  Pressure 

Transducer (SPT B)

Suction Pressure 

Transducer (SPT A)

Discharge  Pressure 

Transducer (DPT A)

Discharge  Pressure 

Transducer (DPT B)

Economizer Pressure 

Transducer (EPT B)

Economizer Pressure 

Transducer (EPT A)



[image: image30.wmf]text

Fill with

High

Pressure

Oil

Compression

Process

Loaded Position

High Pressure Oil

Energized

NO FLOW

Valve #2 

(NO)

Energized

FLOW

Valve #1 

(NC)

Bleed Line to Low Pressure Suction

Slide Valve

Discharge

Port

Unloader Piston

Chamber



 EMBED Visio.Drawing.6  [image: image31.wmf]text

D

r

a

i

n

 

t

o

L

o

w

 

P

r

e

s

s

u

r

e

Compression

Process

Unloaded Position

High Pressure Oil

De-energized

FLOW

Valve #2 

(NO)

De-energized

NO FLOW

Valve #1 

(NC)

Bleed Line to Low Pressure Suction

Slide Valve

Discharge

Port

Unloader Piston

Chamber


[image: image32.wmf]text

High Pressure Oil

Trapped

Oil at

High

Pressure

Compression

Process

Part Load Position

Energized

NO FLOW

Valve #2 

(NO)

De-energized

NO FLOW

Valve #1 

(NC)

Bleed Line to Low Pressure Suction

Slide Valve

Discharge

Port

Unloader Piston

Chamber


Fully Loaded Operation                             Fully Unloaded Operation                   Maintain Position    
Suction Service Valve Option

     The suction service valve is an option for the unit. It is located in the suction outlet of cooler . The Suction service valve is bolted between the cooler outlet and the suction flange piping. The Suction service valve shaft has a locking  device located on the shaft to lock the valve in either a fully open position or fully closed position. The locking device must be pulled out before moving the valve handle to a full open or full closed position.   

[image: image54.wmf]Oil Solenoid 

Valve

Check 

Valve

Oil Pressure 

Transducer

Oil Filter

Oil Shut

-

off 

valve

Oil Level 

Switch 

(Bottom)

Oil Separator 

Heater (Bottom)

High 

Pressure 

Transducer

Oil Solenoid 

Valve

Check 

Valve

Oil Pressure 

Transducer

Oil Filter

Oil Shut

-

off 

valve

Oil Level 

Switch 

(Bottom)

Oil Separator 

Heater (Bottom)

High 

Pressure 

Transducer


Transducers – 

There are 4 pressure transducers per circuit and two different types of transducers used low pressure and high pressure. 
Low Pressure Type - Suction Pressure (SPT), Economizer Pressure (EPT)
High Pressure Type – Discharge Pressure(DPT), Oil Pressure (OPT)
[image: image55.wmf]Unit Size

CKT A

CKT B

CKT C

80-120 

5.5 Gal

5.5 Gal

140,160

6.25 Gal

5.5 Gal

180,200

6.25 Gal

6.25 Gal

220

6.75 Gal

6.25 Gal

240

6.75 Gal

6.75 Gal

260

7.50 Gal

6.75 Gal

280,300

7.50 Gal

6.75 Gal

325,350

7.50 Gal

7.50 Gal

400

6.75 Gal

6.75 Gal

7.50 Gal

450

6.75 Gal

6.25 Gal

7.50 Gal

500

7.50 Gal

6.75 Gal

7.50 Gal

Oil Charge

Figure below shows typical location in a unit.

Compressor Oil System
[image: image56.wmf]A

P

CompB Comp A

Fan output

1

2

3

5

6

7

E

B1

A2

A1

Contactor #

FC A1

FC A2

FC A3

FC B1

FC B2

FC B3

B

B3

B2

A3

Fan position

FM5

FM3

FM6

FM1

FM4

FM2

FM

#

1

3

5

2

4

6

B-E

P

Comp B

Comp A

Fan output

1

2

3

4

5

6

7

8

E

B1

B2

A2

A1

Contactor #

FC A1

FC A2

FC A3

FC A4

FC B1

FC B2

FC B3

FC B4

B

B3

B4

A4

A3

Fan position

FM7

FM5

FM8

FM6

FM1

FM3

FM2

FM4

FM

#

1

3

5

7

2

4

6

8

F-G

Fan output A

1

2

3

4

5

6

CompB

PEB  

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

B1

B2

A3

A2

A1

Fan position

FM9

FM7

FM5

FM10

FM8

FM6

B3

B4

A6

A5

A4

Fan output B

1

2

3

4

FM

#

1

3

5

7

9

Contactor #

FC B1

FC B2

FC B3

FC B4

2

4

6

8

10

Fan position

FM1

FM3

FM2

FM4

H-I

Fan output A

1

2

3

4

5

6

Comp B

PEB  

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

B1

B2

B3

A3

A2

A1

Fan position

FM11

FM9

FM7

FM12

FM10

FM8

B4

B5

B6

A6

A5

A4

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

8

10

12

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

J-K

Fan output A

1

2

3

4

5

6

7

Comp B

PEB  

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

B1

B2

B3

A4

A3

A2

A1

Fan position

FM13

FM11

FM9

FM7

FM14

FM12

FM10

B4

B5

B6

A7

A6

A5

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

13

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

10

12

14

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

L

Fan output A

1

2

3

4

5

6

7

Comp B

    PEB

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

FC A8

FC A9

B1

B2

B3

A5

A4

A3

A2

A1

Fan position

FM15

FM13

FM11

FM9

FM7

FM16

FM14

FM12

FM10

B4

B5

B6

A9

A8

A7

A6

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

13

15

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

10

12

14

16

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

M

Fan output A

1

2

3

4

5

6

7

Comp B

    PEB

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

FC A8

FC A9

B1

B2

B3

A5

A4

A3

A2

A1

Fan position

FM15

FM13

FM11

FM9

FM7

FM16

FM14

FM12

FM10

B5

B6

B7

B4

A9

A8

A7

A6

Fan output B

1

2

3

4

5

6

7

FM

#

1

3

5

7

9

11

13

15

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

FC B7

2

4

6

8

10

12

14

16

Fan position

FM1

FM3

FM5

FM8

FM2

FM4

FM6

8

8

Each compressor/circuit has its own oil system which includes Oil Filter, Oil Solenoid, Check Valve, Oil Level switch, Oil Separator Heater, Oil Pressure Transducer and Oil Shut-off Valve. Typical Oil System shown below
Oil Quantity per system
Oil Charging/ Low Oil Recharging
[image: image57.wmf]N

Fan output A

1

2

3

4

5

6

Comp B

    PEB

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

FC A8

FC A9

FC A10

B1

B2

B3

A5

A4

A3

A2

A1

Fan position

FM15

FM13

FM11

FM9

FM7

FM16

FM14

FM12

FM10

FM8

B4

B5

B6

A10

A9

A8

A7

A6

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

13

15

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

8

10

12

14

16

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

O-P

Fan output A

1

2

3

4

5

6

7

Comp B

    PEB

Comp A

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

FC A8

FC A9

B1

B2

B3

B4

A5

A4

A3

A2

A1

Fan position

FM17

FM15

FM13

FM11

FM9

FM18

FM16

FM14

FM12

B6

B7

B8

B9

B5

A9

A8

A7

A6

Fan output B

1

2

3

4

5

6

7

FM

#

1

3

5

7

9

11

13

15

17

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

FC B7

FC B8

FC B9

2

4

6

8

10

12

14

16

18

Fan position

FM1

FM3

FM5

FM7

FM10

FM2

FM4

FM6

FM8

Q

Fan output A

1

2

3

4

5

6

7

8

Comp B

     

PEB A/B

Comp A

PEB C 

Comp C

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

B1

B2

B3

A3

A2

A1

C4

C3

C2

C1

Fan position

FM11

FM9

FM7

FM12

FM10

FM8

B4

B5

B6

A6

A5

A4

C8

C7

C6

C5

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

13

15

17

19

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

8

10

12

14

16

18

20

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

Fan output C

1

2

3

4

5

6

7

8

Contactor #

FC C1

FC C2

FC C3

FC C4

FC C5

FC C6

FC C7

FC C8

Fan position

FM19

FM17

FM15

FM13

FM20

FM18

FM16

FM14

R-S

Fan output A

1

2

3

4

5

6

7

8

Comp B

 PEB A/B

Comp A

PEB C 

Comp C

Contactor #

FC A1

FC A2

FC A3

FC A4

FC A5

FC A6

FC A7

FC A8

B1

B2

B3

A4

A3

A2

A1

C4

C3

C2

C1

Fan position

FM13

FM11

FM9

FM7

FM14

FM12

FM10

FM8

B4

B5

B6

A8

A7

A6

A5

C8

C7

C6

C5

Fan output B

1

2

3

4

5

6

FM

#

1

3

5

7

9

11

13

15

17

19

21

Contactor #

FC B1

FC B2

FC B3

FC B4

FC B5

FC B6

2

4

6

8

10

12

14

16

18

20

22

Fan position

FM1

FM3

FM5

FM2

FM4

FM6

Fan output C

1

2

3

4

5

6

7

8

Contactor #

FC C1

FC C2

FC C3

FC C4

FC C5

FC C6

FC C7

FC C8

Fan position

FM21

FM19

FM17

FM15

FM22

FM20

FM18

FM16

8

8

7

8


OIL SPECIFICATION – If oil is added it must meet the following Carrier specifications

Castrol …………………IcematicR  SW-220XL 
Oil Type………………… Inhibited polyolester based synthetic compressor lubricant for use with screw compressors

ISO Viscosity Grade……..220
Quantity  Totaline Part No.
1 Quart - P903-2325
1 Gallon – P903-2301

5 Gallon – P903-2305 
This oil is available in the following quantities from your local Carrier representative 
Addition of oil Charge to 30XA systems

1. If the unit shuts off repeatedly on Low oil level alert this may be an indication of inadequate oil charge. It could also mean simply that the oil is being reclaimed from the low-side of the system.

2. Begin running the unit at full load for 1 ½ hours. Use the manual control feature of the software if the unit does not normally run at full load

3. After running for 1 ½ hours allow the unit to restart and run normally. If low oil alarms persist, continue with the following procedure.

4. Close liquid service valve, and place a pressure gage on the top of the cooler. Enable the Service Test feature using the navigator and turn the EOR switch to enable. Start the desired circuit by turning it on under the TEST function. CP.A for compressor A, CP.B for compressor B, etc

5. When the compressor starts successfully observe the cooler pressure when the pressure reads 10 psig, turn the selected compressor Off from the Navigator and move the EOR switch to the Off position.
6. Open the liquid line service valve and allow the unit to restart normally. If low Oil Level alarms persist, continue with this procedure.

7. If none of the previous steps were successful, the unit is low on oil charge. Add oil to the oil separator using the ¼ Schrader-type fitting that the discharge pressure transducer is mounted to.
8. Make sure that the unit is not running when adding oil, as this will make oil-charging process easier. Because the system is under pressure even when the unit is not running, it is necessary to use a suitable pump to add oil to the system.

9. Using a suitable pump, add ½ gal of Castrol IcematicR  SW-220XL (absolutely no substitutes are approved) to the system. Make sure the oil level switch is not jumpered, and allow the unit to restart a run normally. Do not exceed factory oil charge levels.
10. . If low oil level problems persist, add another ½ gal of oil. Continue adding oil in ½ gal increments until the problem is resolved. If it is necessary to add factory oil charge levels to the system, contact your Carrier representative.
Oil Filter Maintenance – Each circuit has one oil filter located external to the compressor. Oil line pressure drop is monitored by the control. Oil line pressure drop is calculated by subtracting Oil Pressure(OP) from Discharge pressure (DP). If the oil line pressure drop exceeds 30 PSI for 5 minutes the control will generate a High Oil Filter Pressure Drop Alert. This alert will not shut down the compressor but indicates that the oil filter is dirty. If oil pressure line losses exceed 50 psi then the control will shut down the circuit on Maximum Oil Filter Differential Pressure Failure.
[image: image33.wmf]
Replacing the oil filter – Close the oil line ball valve located in front of the oil filter. Connect a charging hose to the Schrader port located down stream of the valve and bleed off oil trapped between the service valve and the oil solenoid valve. A quart of oil is typically what is removed during this process. Remove the charging hose. Unscrew the nuts from both ends of the oil filter and remove oil filter. Remove the protective caps from the new oil filter and install be careful not to lose or damage new O-ring located on new oil filter. Draw a vacuum at the Schrader port. Remove charging hose and open oil line ball valve check both fitting for leaks.
 XE "Service: Cooler protection" 

 XE "Cooler Protection" Cooler Protection

 XE "Cooler protection: Freeze protection" 

 XE "Freeze protection" Freeze Protection — All  coolers  are equipped with cooler heaters, and are controlled  by the Main Base Board based on the outdoor air temperature and the Entering and Leaving Water thermistors controls the cooler heaters.  The Heater Set Point is the sum of the freeze point and Cooler Heater DT Setp Configuration/SERV/HTR.

If the Entering or Leaving Water Temperature is less than the Heater Set Point and the Outdoor Air Temperature is less than the Heater Set Point – 2 F (1.1 C), then the heater will be turned on.

If the Entering or Leaving Water Temperature is less than the Brine Freeze Setpoint Configuration/SERV/LOSP + 1.0 F (0.5 C), then the heater will be turned on along with the pump.

Entire cooler is covered with closed-cell insulation applied over the heater.  Heater plus insulation protect cooler against low ambient temperature freeze-up to -0 F (-17.8 C).

	IMPORTANT: If unit is installed in an area where ambient temperatures fall below 32 F (0° C), it is recommended that a suitable corrosion-inhibited antifreeze solution be used in chilled water circuit.


 XE "Cooler protection: Low fluid protection" 

 XE "Low fluid protection" Low Fluid Temperature — Main Base Board is programmed to shut chiller down if leaving fluid temperature drops below 34 F (1.1 C) for water or below Brine Freeze Setpoint Configuration/SERV/LOSP for brine units.  The unit will shut down without a pumpout.  When fluid temperature rises to 6° F (3.3° C) above leaving fluid set point, safety resets and chiller restarts.  Reset is automatic as long as this is the first occurrence.

 XE "Cooler protection: Loss of fluid flow protection" 

 XE "Loss of fluid flow protection " Loss of Fluid Flow Protection — All 30XA machines include an integral flow switch that protects cooler against loss of cooler flow.
 XE "Cooler protection: Tube plugging" 

 XE "Tube plugging" Tube Plugging — A leaky tube can be plugged until retubing can be done.  The number of tubes plugged determines how soon the cooler must be retubed.  The number of tubes plugged  determines how soon the cooler must be retubed. All tubes in the cooler may be removed. Loss of unit capacity and efficiecy as well as increased pump power will result from plugging tubes. Failed tubes should be replaced as soon as possible.Up to 10 % 0f the total number of tubes can be plugged before retubing is necessary.  Fig. 16 shows an Elliott tube plug and a cross-sectional view of a plug in place. See Table 40 for plug components. If the tube failure occurs in both circuits using tube plugs will not correct the problem. Contact your local Carrier representative for assistance. 
[image: image34.wmf]
Fig. 16 - Elliott Tube Plug

	CAUTION

	Use extreme care when installing plugs to prevent damage to the tube sheet section between the holes.


Table 40 -  XE "Cooler protection: Plug components" 

 XE "Plug components" Plug Components

	Components for Plugging
	Part Number

	For Tubes
	

	
	Brass Pin
	853103-1*

	
	Brass Ring
	853002-640 or 657 **

	For Holes without tubes
	

	
	Brass Pin
	853103-1A

	
	Brass Ring
	853102-738

	Loctite
	No. 675 †

	Locquic
	“N” †

	Roller Extension 
	S82-112/11




Note:  * - Order directly from Elliot Tube Company, Dayton, OH or RCD


           * - Measure tube before ordering
           † - Can be obtained locally.

	
	Inches
	mm

	Tube sheet hole diameter
	0.756
	19.20

	Tube OD
	.750
	19.05

	Tube ID after rolling (includes expansion due to clearance.)
	.650 to .667
	16.51 to 16.94


NOTE: Tubes replaced along heat exchanger head partitions  must be flush with tube sheet (both ends).


Retubing— When retubing is required, obtain service of qualified personnel experienced in boiler maintenance and repair.  Most standard procedures can be followed when retubing the coolers.  An 8% crush is recommended when rolling replacement tubes into the tubesheet.
The following Elliott Co. tube rolling tools are required: 

Expander Assembly -113123


Cage - 2134123




Mandrel - 213123



Rolls - 2115122




Place one drop of Loctite No. 675 or equivalent on top of tube prior to rolling.  This material is intended to “wick” into the area of the tube that is not rolled into the tube sheet, and prevent fluid from accumulating between the tube and the tube sheet. New tubes must also be rolled into the center tubesheet to prevent circuit to circuit leaks.
 XE "Cooler protection: Tightening cooler head bolts" 

 XE "Cooler head bolts: Tightening" Tightening Cooler Head Bolts

Gasket Preparation — When reassembling cooler heads, always use check the conditon of the O-rings first. The O-ring should be replaced if there is visible signs os deterioration, cuts or damage. Apply a thin film of grease to O-ring before installation. This will aid in holding the O-ring in the groove while the head is installed. Torque all bolts to the following specification and in sequence:

 
3/4-in. Diameter Perimeter Bolts (Grade 5). . . . 200 to 225 ft-lb (271 to 305 N-m)



See Fig.  25  (Bolt tightening sequence)
1. Install all bolts finger tight, 
2. Bolt tightening sequence is outlined in the Bolt Tightening Sequence figure. Follow the numbering or lettering sequence so that pressure is evenly applied to O-ring.

3. Apply torque in one-third steps until required torque is reached.  Load all bolts to each one-third step before proceeding to next one-third step.

4. No less than one hour later, retighten all bolts to required torque values.

5. After refrigerant is restored to system, check for refrigerant leaks using recommended industry practices
6. Replace cooler insulation. [image: image35.png]T
nozz e ~——|
3 o
i 4
O 7
1] [
DRE
g g
3 6 [ Z
NoZZLE ]
! DN hl
T 7 0 7
w [ ] [

Fig. 25 — Cooler and Condenser Head Recommended Bolt Torque Sequence




Inspecting/Cleaning Heat Exchangers
COOLERS -  Inspect and clean cooler tubes at the end of the first operating season. Because these tubes have internal ridges, a rotary-type tube cleaning system is necessary to fully clean the tubes. Tube condition in the cooler will determine the scheduled frequency for cleaning, and will indicated whether water treatment is adequate in chilled water/brine circuit. Inspect the entering and leaving water thermistor wells for signs of corrosion or scale. Replace the well if corroded or remove any scale if found.
[image: image36.png]Hard scale may require chemical treatment for its preven-
tion or removal. Consult a waler treatment specialist for
proper treatment procedures.





Water Treatment – Untreated or improperly treated water may result in corrosion, scaling, erosion or algae. The services  of a qualified water treatment specialist should be obtained to develop and monitor a treatment program.
[image: image37.png]Water must be within design flow limits. clean and treated
0 ensure proper machine performance and reducethe
potential of tbing damage due to corrosion, scaling.
erosion. and alga. Carrier assumes no responsibility for
chiller or condenser damage resulting from unireated or
improperly treated water:





 XE "Cooler protection: Chilled water flow switch" 

 XE "Chilled water flow switch" Chilled Water Flow Switch

A factory installed flow switch is installed in entering water  nozzle for all machines.  This is a thermal-dispersion flow switch.  Figure below shows typical installation. If nuissancetrips of the sensor are occurring, follow the steps below to correcdt the situation: 

When power is supplied to the device, a warm-up period is intiated. During this period the green LED is lit and turned off as each LED to the left is sucessevely lit until the left most red LED is lit. The warm-up period may take up to 30 seconds. When some flow is detected but not enough for machine operation, a red LED illuminates at the far left.  With increasing flow, successive red LEDs illuminate. When the switch determines flow is present an amber LED illuminates indicating the switch has closed. This is not an indication that minimum flow has been met. Increasing flow above the amber LED indication illuminates the first green LED. Each successive green LED indicates greater flow.  The switch closure does not indicate minimum flow requirements have been met for the machine. With one green LED lit, minor fluctuations in flow can cause nuisance alarms  Additional green LEDs indicate higher flow rates, and can avoid nuisance alarms.
1. Check to confirm that all strainers are clean, valves are open and pumps are running. For the case of VFD controlled pumps, ensure the minimum speed setting has not been changed.
2. Measure the pressure drop across the cooler and using Appendix for water pressure drop, calculate the flow and compare this to system requirements.

3. If the measured flow rate through the cooler agrees with the system requirements. At least 2 LEDs should be lit

4. If the contacts do not close with two LEDs lit then check wiring connection to the MBB if input signal is not closed then the switch needs to be replaced. 

[image: image38.png]M12x4 PIN MALE

[E—T

e 2 2]

N—eLU—

EXTERNAL RELAY COIL
IRING DIAGRANM

14 NPT

a5 a7
- ] 21




 [image: image39.png]RED ANBER GREEN
r 1 r 1

FLOWEBELOW _OUTPUT FLOW ABOVE
SETPONT  ENERGIZED SETPOINT

Fig. 37 — Chilled Water Flow Switch LED Display





[image: image40.png]H
'ANDARD 2-PASS




 XE "Service:Condenser coils" 

 XE "Condenser coils" Condenser Coils

COIL CLEANING — For standard aluminum, copper and pre-coated aluminum fin coils, clean the coils with a vacuum cleaner, fresh water, compressed air, or a bristle brush (not wire).  Units installed in corrosive environments should have coil cleaning as part of a planned maintenance schedule.  In this type of application, all accumulations of dirt should be cleaned off the coil.
	CAUTION

	Do not use high-pressure water or air to clean coils — fin damage may result.


 XE "Condenser coils: Cleaning e-coated coils" 

 XE "E-coated coils" CLEANING E-COATED COILS — Follow the outlined procedure below for proper care, cleaning and maintenance of E-coated aluminum or copper fin coils:

Coil Maintenance and Cleaning Recommendations — Routine cleaning of coil surfaces is essential to maintain proper operation of the unit.  Elimination of contamination and removal of harmful residues will greatly increase the life of the coil and extend the life of the unit.

Remove Surface Loaded Fibers — Surface loaded fibers or dirt should be removed with a vacuum cleaner.  If a vacuum cleaner is not available, a soft brush may be used.  In either case, the tool should be applied in the direction of the fins.  Coil surfaces can be easily damaged (fin edges bent over) if the tool is applied across the fins.

NOTE: Use of a water stream, such as a garden hose, against a surface loaded coil will drive the fibers and dirt into the coil. This will make cleaning efforts more difficult.  Surface loaded fibers must be completely removed prior to using low velocity clean water rinse.

Periodic Clean Water Rinse — A periodic clean water rinse is very beneficial for coils that are applied in coastal or industrial environments.  However, it is very important that the water rinse is made with very low velocity water stream to avoid damaging the fin edges.  Monthly cleaning as described below is recommended.

Routine Cleaning of Coil Surfaces — Monthly cleaning with Environmentally Sound Coil Cleaner is essential to extend the life of coils.  It is recommended that all coils, including standard aluminum, pre-coated, copper/copper or E-coated coils are cleaned with the Environmentally Sound Coil Cleaner as described below.  Coil cleaning should be part of the units regularly scheduled maintenance procedures to ensure long life of the coil.  Failure to clean the coils may result in reduced durability in the environment.

Environmentally Sound Coil Cleaner is non-flammable, hypoallergenic, non-bacterial, USDA accepted biodegradable and 100% ecologically safe agent that will not harm the coil or surrounding components such as electrical wiring, painted metal surfaces or insulation.  Use of non-recommended coil cleaners is strongly discouraged since coil and unit durability could be affected.

Environmentally Sound Coil Cleaner Application Equipment

• 21/2 Gallon Garden Sprayer

• Water Rinse with Low Velocity Spray Nozzle

Environmentally Sound Coil Cleaner Application Instructions

• Although Environmentally Sound Coil Cleaner is harmless to humans, animals, and marine life, proper eye protection such as safety glasses is recommended during mixing and application.

• Remove all surface loaded fibers and dirt with a vacuum cleaner as described above.

• Thoroughly wet finned surfaces with clean water and a low velocity garden hose being careful not to bend fins.

• Mix Environmentally Sound Coil Cleaner in a 21/2 gallon garden sprayer according to the instructions included with the Enzyme Cleaner.  The optimum solution temperature is 100 F (37 C).

NOTE: DO NOT USE water in excess of 130 F (54 C) as the enzymatic activity will be destroyed.

• Environmentally Sound Coil Cleaner solution to all coil surfaces including finned area, tube sheets and coil headers. 

• Hold garden sprayer nozzle close to finned areas and apply cleaner with a vertical, up-and-down motion.  Avoid spraying in horizontal pattern to minimize potential for fin damage. 

• Ensure cleaner thoroughly penetrates deep into finned areas.

• Interior and exterior finned areas must be thoroughly cleaned.

• Finned surfaces should remain wet with cleaning solution for 10 minutes.

• Ensure surfaces are not allowed to dry before rinsing.  Reapply cleaner as needed to ensure 10-minute saturation is achieved.

• Thoroughly rinse all surfaces with low velocity clean water using downward rinsing motion of water spray nozzle.  Protect fins from damage from the spray nozzle.

	CAUTION

	Harsh Chemical and Acid Cleaners — Harsh chemical, household bleach or acid cleaners should not be used to clean outdoor or indoors coils of any kind.  These cleaners can be very difficult to rinse out of the coil and can accelerate corrosion at the fin/tube interface where dissimilar materials are in contact.  If there is dirt below the surface of the coil, use the Environmentally Sound Coil Cleaner as described above.  

High Velocity Water or Compressed Air — High velocity water from a pressure washer, garden hose or compressed air should never be used to clean a coil. The force of the water or air jet will bend the fin edges and increase airside pressure drop. Reduced unit performance or nuisance unit shutdown may occur.


 XE "Service: Condenser fans" 

 XE "Condenser fans" Condenser Fans — A formed metal mount bolted to fan deck supports each fan and motor assembly.  A shroud and a wire guard provide protection from the rotating fan.  The exposed end of fan motor shaft is protected from weather by grease.  If fan motor must be removed for service or replacement, be sure to regrease fan shaft and reinstall fan guard.  The fan motor has a step in the motor shaft.  For proper performance, fan should be positioned such that it is securely seated on this step.  Tighten the bolt. Plugs are used to make connections to fan motors. If operational issues occur with a fan motor the plug assembly needs to be check for proper connection.
 XE "Service:Refrigerant circuit" 

 XE "Refrigerant circuit" Refrigerant Circuit
LEAK TESTING — Units are shipped with complete operating charge of refrigerant R-134a (see Physical Data tables supplied in the chiller’s installation instructions) and should be under sufficient pressure to conduct a leak test.  If there is no pressure in the system, introduce enough nitrogen to search for the leak.  Repair the leak using good refrigeration practices.  After leaks are repaired, system must be evacuated and dehydrated.

REFRIGERANT CHARGE –  (Refer to Physical Data tables supplied in the chiller’s installation instructions) — Immediately ahead of filter drier in each circuit is a factory-installed liquid line service valve. Each valve has a 1/4-in. Schrader connection for charging liquid refrigerant.

Charging with Unit Off and Evacuated — Close liquid line service valve before charging.  Weigh in charge shown on unit nameplate (also in Physical Data tables supplied in the chiller’s installation instructions).  Open liquid line service valve; start unit and allow it to run several minutes fully loaded.  Check for a clear sight glass.  Be sure clear condition is liquid and not vapor.

Charging with Unit Running — If charge is to be added while unit is operating, all condenser fans and compressors must be operating.  It may be necessary to block condenser coils at low ambient temperatures to raise condensing pressure to approximately 198 psig to turn all condenser fans on.  Do not totally block a coil to do this. Partially block all coils in uniform pattern.  Charge each circuit until sight glass shows clear liquid, and has a liquid line temperature of 103 F (39 C).

	IMPORTANT: When adjusting refrigerant charge, circulate fluid through cooler continuously to prevent freezing and possible damage to the cooler. Do not overcharge, and never charge liquid into low-pressure side of system.







	
	
	

	
	
	



	
















1. 
2. 


	


3. 
4. 
5. 
6. 
7. 
8. 
9. 
10. 
11. 
12. 
13. 
14. 
15. 
16. 
17. 
18. 
19. 
20. 
21. 
22. 

	

	


	

	




· 
· 
· 




1. 
2. 
3. 
4. 
5. 
6. 
7. 

 XE "Maintenance" MAINTENANCE
 XE "Recommended maintenance schedule" Recommended Maintenance Schedule

The following are only recommended guidelines. Jobsite conditions may dictate that maintenance schedule is performed more often than recommended.

 XE "Recommended maintenance schedule: Routine" Routine:

For machines with E-coat Condenser Coils:

· Check condenser coils for debris, clean as necessary with Carrier approved coil cleaner.

· Periodic clean water rinse, especially in coastal and industrial applications.

 XE "Recommended maintenance schedule: Monthly" Every month:

· Check condenser coils for debris, clean as necessary with Carrier approved coil cleaner.

· Check moisture indicating sight glass for possible refrigerant loss and presence of moisture.

 XE "Recommended maintenance schedule: Every 3 months" Every 3 months (for all machines):

· Check refrigerant charge.

· Check all refrigerant joints and valves for refrigerant leaks, repair as necessary.

· Check chilled water flow switch operation.

· Check condenser coils for debris, clean as necessary with Carrier approved coil cleaner.

· Check Sightglass Dry-eye for moisture.

· Check all condenser fans for proper operation.

· Check Oil Filter Pressure Drop
· Check crankcase heater operation.


 XE "Recommended maintenance schedule: Every 12 months" Every 12 months (for all machines):

· Check all electrical connections, tighten as necessary.

· Inspect all contactors and relays, replace as necessary.

· Check accuracy of thermistors, replace if greater than ± 2° F (1.2° C) variance from calibrated thermometer.

· Check accuracy of transducers, replace if greater than ± 5 psi (34.47 kPa) variance.

· Check to be sure that the proper concentration of antifreeze is present in the chilled water loop, if applicable.

· Verify that the chilled water loop is properly treated.

· Check refrigerant filter driers for excessive pressure drop, replace as necessary.

· Check chilled water strainers, clean as necessary.

· Check cooler heater operation
· Check condition of condenser fan blades and that they are securely fastened to the motor shaft.

· Perform Service Test to confirm operation of all components.

Check for excessive cooler approach (Leaving Chilled Water Temperature - Saturated Suction Temperature) which may indicate fouling.  Clean cooler vessel if necessary.

 XE "Troubleshooting" Troubleshooting

[image: image41.png]Table 37 — Troubleshooting

SYMPTOM
Unit Does Not Run

POSSIBLE CAUSE

Check for pawer o unit

POSSIBLE REMEDY

Tieck overcurrent pr
heck non-used dis
- Restors power to unit

) or incorrect it ¢

niiguration

Check unit configuration,

(Active alarm

Check Alarm status. See separate Al and
instru

W Toubisshooting

ot

perating m

Unit Operates too Long or | Low reffigerant charge

o1 Operating Modes, Se= O
) insiructions

o leak and add remgerant

perating Modes and

S Toutle-

Continuously

ompress:

TAir n chiled water

Replace contact

Non-condensables in refr

ant circut.

Tnoperative EXV
heck EXV
heck EXV ¢
Circutt Does Not Run Rctve alarm Check Alarm status. See separate A and follow Foubi=shooting
instruct
Aofive operating T o1 Cperating Modes. 522 Operatng Modes and follow Toubie-
shooting instructions
Circuit Does Not Load | Active alarm W voubiEshootng
e operatng m 1 Operating Modes. S22 Operating Modes and follow Touble
shooting instructions
Tow saturated suction Emperature eraling Modes 21 22 and
Hiah circut suction supermeat The circut capacity s not alowed ncrease ff CiroUl sUpsrheat s oreater
than 36 F (20 C) See Alamms .08, PO and P10 for potential causes.
W Sudtion superhzal “The cireut capaclty s not allowsd 1o Increase f e ireLit superheat s
Iess than 5 F (2.8 C). See Alarms P11, P12 and P13 for potential causes
Compressor Does Not Run | Active alarm ‘Check Alarm stafus. See separate Alam and follow froubleshooing
instructions.
(Actve operating m ‘Check for Operating Modes. 52 Operaing Modes and fallow Touble-
shooting instructiors
Tnoperalive compressor conla ~ Chieck control wiring
heck scroll protection modue.
heck conta ration, r=p

Chilled Water Pump is ON,
but the Machine is OFF

e freez= pr

Chiled water loop temperature Ter heater





Alarms and Alerts – The control system constantly monitors the unit and generates warnings when abnormal or fault conditions occur. Alarms may cause either the circuit (Alert) or the entire machine (Alarm) to shutdown. Alarms and alerts are assigned codes as described in table below. The alarm/alert indicator  LED on the Navigator module is illuminated when any alarm or alert condition is present. If an alert is active, the Alarm Indicator LED will blink. If an alarm is active, the Alarm Indicator LED will remain on. Current active alarms and alerts can be found on the Navigator display under Alarms display. 
The control generates two types of alarms. Automatic reset alarms will reset without any intervention if the condition, which caused the alarm, corrects itself. Manual reset alarms require service technician to check for the alarm cause and reset the alarm. The following method must be followed to reset manual alarms:


Before resetting alarm, first determine the cause of the alarm and correct it. Enter the alarms mode indicated by the LED   on the side of the Navigator display. Press ENTER and submode alarm ALARM   R.ALM(Reset All Current Alarms) is displayed. Press ENTER. The control will prompt you for the password, by displaying PASSWORD. Press ENTER to display 1111. Press enter for each character. The default password is 0113. Use the arrow keys to change each individual character. Use the up or down          
Keys to toggle the display to YES and press ENTER. The alarms will be reset. Indicator light will turn off when switched correctly. Do not reset the chiller at random without investigating and correcting the causes(s) of failure.

Each alarm is described by a three to 4 digit code. The first one or two digits indicate the alarm source and are listed below. The last two digits pinpoint the problem. See table below
The following is an abbreviated list of symptoms, probable causes and potential remedies:
	alarm number


	alarm number viewed by CCN gateway (modbus …)


	High Tier  Display

alarm code


	Comforlink User Display

alarm code


	Alarm text description and ccn message

	
	
	Thermistor failure
	

	1
	1
	th-01
	th.01
	Cooler Entering Fluid Thermistor

	2
	2
	th-02
	th.02
	Cooler Leaving Fluid Thermistor

	3
	3
	th-03
	th.03
	Circuit A Defrost Thermistor

	4
	4
	th-04
	th.04
	Circuit B Defrost Thermistor

	5
	5
	th-06
	th.06
	Condenser Entering Fluid Thermistor

	6
	6
	th-07
	th.07
	Condenser Leaving Fluid Thermistor

	7
	7
	th-08
	th.08
	Reclaim Condenser Entering Thermistor

	8
	8
	th-09
	th.09
	Reclaim Condenser Leaving Thermistor

	9
	9
	th-10
	th.10
	OAT Thermistor                                                 

	10
	10
	th-11
	th.11
	MASTER/Slave Common Fluid Thermistor                           

	11
	11
	th-12
	th.12
	Circuit A Suction Gas Thermistor                               

	12
	12
	th-13
	th.13
	Circuit B Suction Gas Thermistor                               

	13
	13
	th-14
	th.14
	Circuit C Suction Gas Thermistor                               

	14
	14
	th-15
	th.15
	Circuit A Discharge Gas Thermistor                               

	15
	15
	th-16
	th.16
	Circuit B Discharge Gas Thermistor                               

	16
	16
	th-17
	th.17
	Circuit C Discharge Gas Thermistor                               

	17
	17
	th-18
	th.18
	Circuit A Condenser Subcooling Liquid Thermistor

	18
	18
	th-19
	th.19
	Circuit B Condenser  Subcooling Liquid Thermistor

	19
	19
	th-21
	th.21
	Space Temperature Thermistor                                    

	20
	20
	th-23
	th.23
	Cooler heater feedback thermistor                                    

	21
	21
	th-24
	th.24
	Circuit A Economizer Gas Thermistor                               

	22
	22
	th-25
	th.25
	Circuit B Economizer Gas Thermistor                               

	23
	23
	th-26
	th.26
	Circuit C Economizer Gas Thermistor                               

	
	
	Pressure Transducers
	

	24
	24
	Pr-01
	Pr.01
	Circuit A Discharge Transducer

	25
	25
	Pr-02
	Pr.02
	Circuit B Discharge Transducer                                 

	26
	26
	Pr-03
	Pr.03
	Circuit C Discharge Transducer                                 

	27
	27
	Pr-04
	Pr.04
	Circuit A Suction Transducer

	28
	28
	Pr-05
	Pr.05
	Circuit B Suction Transducer

	29
	29
	Pr-06
	Pr.06
	Circuit C Suction Transducer                                   

	30
	30
	Pr-07
	Pr.07
	Circuit A Reclaim Pumpdown Pressure Transducer                 

	31
	31
	Pr-08
	Pr.08
	Circuit B Reclaim Pumpdown Pressure Transducer                 

	32
	32
	Pr-10
	Pr.10
	Circuit A Oil Pressure Transducer          

	33
	33
	Pr-11
	Pr.11
	Circuit B Oil Pressure Transducer          

	34
	34
	Pr-12
	Pr.12
	Circuit C Oil Pressure Transducer          

	35
	35
	Pr-13
	Pr.13
	Circuit A Economizer Pressure Transducer          

	36
	36
	Pr-14
	Pr.14
	Circuit B Economizer Pressure Transducer          

	37
	37
	Pr-15
	Pr.15
	Circuit C Economizer Pressure Transducer          

	 
	 
	Communication with slave boards
	

	38
	38
	Co-a1
	Co.a1
	Loss of communication with Compressor Board A                

	39
	39
	Co-b1
	Co.b1
	Loss of communication with Compressor Board B                 

	40
	40
	Co-C1
	Co.C1
	Loss of communication with Compressor Board C                

	41
	41
	Co-E1
	Co.E1
	Loss of communication with EXV Board Number A                  

	42
	42
	Co-E2
	Co.E2
	Loss of communication with EXV Board Number B                  

	43
	43
	Co-E3
	Co.E3
	Loss of communication with EXV Board Number C                  

	44
	44
	Co-F1
	Co.F1
	Loss of communication with Fan Board Number 1

	45
	45
	Co-F2
	Co.F2
	Loss of communication with Fan Board Number 2                  

	46
	46
	Co-F3
	Co.F3
	Loss of communication with Fan Board Number 3

	47
	47
	Co-O1
	Co.O1
	Loss of communication with Free Cooling Board 1                   

	48
	48
	Co-O2
	Co.O2
	Loss of communication with Free Cooling Board  2

	49
	49
	Co-O3
	Co.O3
	Loss of communication with Energy Management NRCP2  Board  

	50
	50
	Co-O4
	Co.O4
	Loss of communication with Heat Reclaim  Board  

	51
	51
	Co-O5
	Co.O5
	Loss of communication with AUX Board 6

	 
	 
	Process  failure
	

	52
	52
	P-01
	P.01
	Cooler Freeze Protection                                       

	53
	53
	P-02
	P.02
	Circuit A Condenser Freeze Protection                                       

	54
	54
	P-03
	P.03
	Circuit B Condenser Freeze Protection                                       

	55
	55
	P-04
	P.04
	Circuit C Condenser Freeze Protection                                       

	56
	56
	P-05
	P.05
	Circuit A Low Suction Temperature                              

	57
	57
	P-06
	P.06
	Circuit B Low Suction Temperature                              

	58
	58
	P-07
	P.07
	Circuit C Low Suction Temperature

	59
	59
	P-08
	P.08
	Circuit A  High Suction Superheat  

	60
	60
	P-09
	P.09
	Circuit B  High Suction Superheat  

	61
	61
	P-10
	P.10
	Circuit C  High  Suction Superheat  

	62
	62
	P-11
	P.11
	Circuit A Low Suction Superheat

	63
	63
	P-12
	P.12
	Circuit B Low Suction Superheat

	64
	64
	P-13
	P.13
	Circuit C Low Suction Superheat

	65
	65
	P-14
	P.14
	Cooler Interlock Failure

	66
	66
	P-28
	P.28
	Electrical Box Thermostat or Power Reverse Phase Detection

	67
	67
	P-29
	P.29
	Loss of communication with System Manager

	68
	68
	P-30
	P.30
	Master/Slave communication Failure

	69
	69
	P-67
	P.67
	Circuit A Low Oil Pressure 

	70
	70
	P-68
	P.68
	Circuit B Low Oil Pressure 

	71
	71
	P-69
	P.69
	Circuit C Low Oil Pressure 

	72
	72
	P-70
	P.70
	Circuit A Max Oil Filter Differential Pressure 

	73
	73
	P-71
	P.71
	Circuit B Max Oil Filter Differential Pressure

	74
	74
	P-72
	P.72
	Circuit C Max Oil Filter Differential Pressure

	75
	75
	P-84
	P.84
	Circuit A High Oil Filter Drop Pressure 

	76
	76
	P-85
	P.85
	Circuit B High Oil Filter Drop Pressure

	77
	77
	P-86
	P.86
	Circuit C High Oil Filter Drop Pressure

	78
	78
	P-75
	P.75
	Circuit A Low Oil Level

	79
	79
	P-76
	P.76
	Circuit BLow Oil Level

	80
	80
	P-77
	P.77
	Circuit C Low Oil Level

	81
	81
	MC-nn
	MC.nn
	Master chiller configuration error   Number #1 to nn           

	82
	82
	FC-n0
	FC.n0
	No factory configuration

	83
	83
	FC-01
	FC.01
	Illegal factory configuration Number #1 to nn

	84
	84
	P-31
	P.31
	Unit is in CCN emergency stop     

	85
	85
	P-32
	P.32
	Cooler pump #1 default

	86
	86
	P-33
	P.33
	Cooler pump #2 default

	87
	87
	P-15
	P.15
	Condenser Flow Switch  Failure

	88
	88
	P-34
	P.34
	Circuit A Reclaim Operation Failure

	89
	89
	P-35
	P.35
	Circuit A Reclaim Operation Failure

	90
	90
	P-37
	P.37
	Circuit A - Repeated high discharge gas overrides 

	91
	91
	P-38
	P.38
	Circuit B – Repeated high discharge gas overrides

	92
	92
	P-39
	P.39
	Circuit C – Repeated high discharge gas overrides 

	93
	93
	P-40
	P.40
	Circuit A – Repeated low suction temp overrides

	94
	94
	P-41
	P.41
	Circuit B – Repeated low suction temp overrides 

	95
	95
	P-42
	P.42
	Circuit C – Repeated low suction temp overrides 

	96
	96
	P-43
	P.43
	Low entering water temperature in heating

	97
	97
	P-73
	P.73
	Condenser pump #1 default

	98
	98
	P-74
	P.74
	Condenser pump #2 default

	99
	99
	P-78
	P.78
	Circuit A High Discharge Temperature

	100
	100
	P-79
	P.79
	Circuit B High Discharge Temperature

	101
	101
	P-80
	P.80
	Circuit C High Discharge Temperature

	102
	102
	P-81
	P.81
	Circuit A Low Economizer Pressure 

	103
	103
	P-82
	P.82
	Circuit B Low Economizer Pressure 

	104
	104
	P-83
	P.83
	Circuit C Low Economizer Pressure 

	105
	105
	P-87
	P.87
	Circuit A Slide Valve Control Unverifiable 

	106
	106
	P-88
	P.88
	Circuit B Slide Valve Control Unverifiable 

	107
	107
	P-89
	P.89
	Circuit C Slide Valve Control Unverifiable 

	108
	108
	P-90
	P.90
	Cooler flow switch setpoint configuration failure 

	109
	109
	P-91
	P.91
	Cooler flow switch failure 

	 
	 
	
	
	

	
	
	Service failure
	

	110
	110
	Sr-nn
	Sr-nn
	Service maintenance alert Number # nn

	
	
	Compressor failure
	

	111-01
	111
	A1-01
	A1.01
	Compressor A Motor temperature too high                    

	111-02
	112
	A1-02
	A1.02
	Compressor A Motor temperature out of range                

	111-03
	113
	A1-03
	A1.03
	Compressor A High pressure switch protection               

	111-04
	114
	A1-04
	A1.04
	Compressor A Over current                                  

	111-05
	115
	A1-05
	A1.05
	Compressor A Locked rotor                                  

	111-06
	116
	A1-06
	A1.06
	Compressor A Phase loss L1                                 

	111-07
	117
	A1-07
	A1.07
	Compressor A Phase loss L2                                 

	111-08
	118
	A1-08
	A1.08
	Compressor A Phase loss L3                                 

	111-09
	119
	A1-09
	A1.09
	Compressor A Low current alarm                             

	111-10
	120
	A1-10
	A1.10
	Compressor A Y delta starter current increase failure alarm

	111-11
	121
	A1-11
	A1.11
	Compressor A Contactor failure                             

	111-12
	122
	A1-12
	A1.12
	Compressor A Unable to stop motor                          

	111-13
	123
	A1-13
	A1.13
	Compressor A Phase reversal                                

	111-14
	124
	A1-14
	A1.14
	Compressor A MTA configuration fault                       

	111-15
	125
	A1-15
	A1.15
	Compressor A Configuration switch mismatch                 

	111-16
	126
	A1-16
	A1.16
	Compressor A Unexpected switch setting change              

	111-17
	127
	A1-17
	A1.17
	Compressor A Power on reset                                

	111-18
	128
	A1-18
	A1.18
	Compressor A UL 1998 critical section software error       

	111-19
	129
	A1-19
	A1.19
	Compressor A UL 1998 current measure dual channel mismatch 

	112-01
	130
	B1-01
	B1.01
	Compressor B Motor temperature too high                    

	112-02
	131
	B1-02
	B1.02
	Compressor B Motor temperature out of range                

	112-03
	132
	B1-03
	B1.03
	Compressor B High pressure switch protection               

	112-04
	133
	B1-04
	B1.04
	Compressor B Over current                                  

	112-05
	134
	B1-05
	B1.05
	Compressor B Locked rotor                                  

	112-06
	135
	B1-06
	B1.06
	Compressor B Phase loss L1                                 

	112-07
	136
	B1-07
	B1.07
	Compressor B Phase loss L2                                 

	112-08
	137
	B1-08
	B1.08
	Compressor B Phase loss L3                                 

	112-09
	138
	B1-09
	B1.09
	Compressor B Low current alarm                             

	112-10
	139
	B1-10
	B1.10
	Compressor B Y delta starter current increase failure alarm

	112-11
	140
	B1-11
	B1.11
	Compressor B Contactor failure                             

	112-12
	141
	B1-12
	B1.12
	Compressor B Unable to stop motor                          

	112-13
	142
	B1-13
	B1.13
	Compressor B Phase reversal                                

	112-14
	143
	B1-14
	B1.14
	Compressor B MTA configuration fault                       

	112-15
	144
	B1-15
	B1.15
	Compressor B Configuration switch mismatch                 

	112-16
	145
	B1-16
	B1.16
	Compressor B Unexpected switch setting change              

	112-17
	146
	B1-17
	B1.17
	Compressor B Power on reset                                

	112-18
	147
	B1-18
	B1.18
	Compressor B UL 1998 critical section software error       

	112-19
	148
	B1-19
	B1.19
	Compressor B UL 1998 current measure dual channel mismatch 

	113-01
	149
	C1-01
	C1.01
	Compressor C Motor temperature too high                    

	113-02
	150
	C1-02
	C1.02
	Compressor C Motor temperature out of range                

	113-03
	151
	C1-03
	C1.03
	Compressor C High pressure switch protection               

	113-04
	152
	C1-04
	C1.04
	Compressor C Over current                                  

	113-05
	153
	C1-05
	C1.05
	Compressor C Locked rotor                                  

	113-06
	154
	C1-06
	C1.06
	Compressor C Phase loss L1                                 

	113-07
	155
	C1-07
	C1.07
	Compressor C Phase loss L2                                 

	113-08
	156
	C1-08
	C1.08
	Compressor C Phase loss L3                                 

	113-09
	157
	C1-09
	C1.00
	Compressor C Low current alarm                             

	113-10
	158
	C1-10
	C1.10
	Compressor C Y delta starter current increase failure alarm

	113-11
	159
	C1-11
	C1.11
	Compressor C Contactor failure                             

	113-12
	160
	C1-12
	C1.12
	Compressor C Unable to stop motor                          

	113-13
	161
	C1-13
	C1.13
	Compressor C Phase reversal                                

	113-14
	162
	C1-14
	C1.14
	Compressor C MTA configuration fault                       

	113-15
	163
	C1-15
	C1.15
	Compressor C Configuration switch mismatch                 

	113-16
	164
	C1-16
	C1.16
	Compressor C Unexpected switch setting change              

	113-17
	165
	C1-17
	C1.17
	Compressor C Power on reset                                

	113-18
	166
	C1-18
	C1.18
	Compressor C UL 1998 critical section software error       

	113-19
	167
	C1-19
	C1.19
	Compressor C UL 1998 current measure dual channel mismatch 


EXV – Electronic Expansion Valve

OAT – Outdoor Air Temperature

MTA – Must Trip Amp

DIAGNOSTIC ALARM CODES AND POSSIBLE CAUSES

Alarm1
Cooler  Entering  Fluid Thermistor Failure
Criteria For Trip    Tested when the unit is On or Off

1.
If the temperature measured by the cooler entering fluid sensor is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If unit is On the unit shall be stopped through stopping process (refer to stopping function).

2.
ALARM_LED shall be set to On. Alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor reading is inside the range of -40 to 240°F.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the Main Base Board.

· Check for a faulty thermistor.
Alarm 2
Cooler Leaving Fluid Thermistor Failure

Criteria For Trip    Tested when the unit is On or Off

1.
If the temperature measured by the cooler leaving fluid sensor is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If unit is On the unit shall be stopped through stopping process (refer to stopping function).

2.
ALARM_LED shall be set to On. Alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor reading is inside the range of -40 to 240°F.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the Main Base Board.

· Check for a faulty thermistor.
Alarm 3
Circuit A Defrost Thermistor Failure (N/A)

Alarm 4
Circuit B Defrost Thermistor Failure (N/A)

Alarm5
Condenser Entering Fluid Thermistor Failure (N/A)
Alarm6
Condenser Entering Fluid Thermistor Failure (N/A)
Alarm 7
Reclaim Entering Fluid Thermistor Failure (N/A)

Alarm 8
Reclaim Leaving Fluid Thermistor Failure (N/A)

Alarm 9
OAT Thermistor Failure

Criteria For Trip    Tested when the unit is On or Off 

1.
If the temperature measured by the OAT is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
The unit shall be stopped through stopping process (refer to stopping function) and not allowed to start.

2.
ALARM_LED shall be set to hold On and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the OAT thermistor reading is inside the range of -40 to 240°F.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the Main Base Board.

· Check for a faulty thermistor.
Alarm 10
CHWS fluid thermistor failure

Criteria For Trip    Tested when the unit is On or Off

1.
If the unit is configured as a master or a slave (ms_sel  disable) and leaving temperature control is selected (ewt_opt=NO),  if the temperature measured by the CHWS fluid sensor is outside the range of -40 to 240°F then, the alarm shall be tripped. [debounce = 4]

Action to be Taken
1.
Master slave operation shall be disable

2.
ALARM_LED shall be set to On

3.
Chiller shall return to stand alone mode

Reset Method
1. Reset shall be automatic when the thermistor reading is inside the range of -40 to 240°F.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the Main Base Board.

· Check for a faulty thermistor.
Alarm 11, 12,13
Circuit Suction Gas Thermistor Sensor Failure

Alarm 11 for circuit A, Alarm 12 for circuit B and 13 for circuit C

Criteria For Trip    Tested when the circuit is On or Off

1.
If the circuit suction gas sensor reading is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the effected circuit shall be stopped be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED shall be set to hold blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the EXV Board.

· Check for a faulty thermistor.
· Check for a faulty channel on the board.
Alarm 14, 15,16
Circuit Discharge Gas Thermistor Sensor Failure

Alarm 14 for circuit A, Alarm 15 for circuit B and 16 for circuit C

Criteria For Trip    Tested when the circuit is On or Off

1.
If the circuit suction gas sensor reading is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the effected circuit shall be stopped be stopped immediately without going through stopping process (refer to stopping function). 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the TCPM Board.

· Check for a faulty thermistor.
· Check for a faulty channel on the board.
Alarm 17
Circuit A Condenser Subcooling Liquid Thermistor Failure (N/A)

Alarm 18
Circuit B Condenser Subcooling Liquid Thermistor Failure (N/A)

Alarm 19
Space Temperature Thermistor  Failure

Criteria For Trip    Tested when the circuit is On or Off and if energy management module is present and reset has been configured based on space temperature.

1.
If the space temperature reading is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the unit shall continue to run. 

2.
ALARM_LED shall be set to blinking alert relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor returns to normal. 

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the EMM.

· Check for a faulty thermistor.
· Check for a faulty channel on the board.
Alarm 20
Cooler heater feedback Sensor Failure (N/A)

Alarm 21, 22,23
Circuit Economizer Gas Thermistor Failure

Alarm 21 for circuit A, Alarm 22 for circuit B and 23 for circuit C

Criteria For Trip    Tested when the circuit is On or Off

1.
If the economizer gas sensor reading is outside the range of -40 to 240°F then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the effected circuit shall be disable the economizer function by closing economizer EXV. 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the thermistor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the EXV Board.

· Check for a faulty thermistor.
· Check for a faulty channel on the board.
Alarm 24 & 25 & 26
Discharge Pressure Transducer Failure

Alarm 24 for circuit A, Alarm 25 for circuit B and alarm 26 for circuit C

Criteria For Trip    Tested when the unit is On or Off when reading value is below 26 psi

1. if  circuit is running then alarm then the alarm shall be tripped.

2. If circuit is not runnning and chiller is an air cooled units and outside d’air temperatrure is below 35.6°F (2°C) the alarm is not verified

3. if circuit is not running and fluid type is brine then alarm shall not be verified. 

Action to be Taken
1.
If the alarm is tripped then the affected circuit shall be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the sensor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to Main Base Board (Alarm 24 and 25).

· Check the sensor wiring to Fan Board C (Alarm 26).

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Confirm unit configuration.
Alarm 27 & 28 & 29
Suction Pressure Transducer Failure

Alarm 27 for circuit A, Alarm 28 for circuit B or alarm 29 for circuit C

Criteria For Trip    Tested when unit is On or Off

1.
If the sensor voltage reading value is equal to 0 then the alarm shall be tripped.

2.
 If the circuit is running in cooling mode and if the saturated suction temperature (sst_tmp) is higher than the referenced cooler leaving temperature for more than 30s then alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the affected circuit shall be stopped immediately. 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the suction pressure reading is within the range and the sst_tmp is lower than cooler leaving temperature plus 3^F. The affected circuit shall be restarted normally .

2. Reset shall be manual if it has not been occurred more than 3 times during last 24 hours ot if it it has been tripped by criteria 2. 

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to Main Base Board (Alarm 27 and 28).

· Check the sensor wiring to Fan Board C (Alarm 29).

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check for a faulty leaving water tempearature sensor.

· Confirm unit configuration.
Alarm 30 & 31
Reclaim Pumpdown Pressure Transducer Failure (N/A)

Alarm 32 & 33 & 34
Oil Pressure Transducer Failure

Alarm 32 for circuit A, Alarm 33 for circuit B and alarm 34 for circuit C

Criteria For Trip    Tested when the unit is On or Off when reading value is below 26 psi

1. if  circuit is running then alarm then the alarm shall be tripped.

2. If circuit is not runnning and chiller is an air cooled units and outside d’air temperatrure is below 35.6°F (2°C) the alarm is not verified.

3. if circuit is not running and fluid type is brine then alarm shall not be verified. 

Action to be Taken
1.
If the alarm is tripped then the affected circuit shall be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the sensor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to TCPM Board.

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check for a plugged oil filter

· Check for a faulty oil solenoid valve coil.

· Check for a stuck oil solenoid valve.

· Confirm unit configuration.
Alarm 35 & 36 & 37
Economizer Pressure Transducer Failure

Alarm 35 for circuit A, Alarm 36 for circuit B or alarm 37 for circuit C

Criteria For Trip    Tested when unit is On or Off

1.
If the sensor voltage reading value is equal to 0 then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the affected circuit shall be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the sensor returns to normal. The affected circuit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to EXV Board.

· Check the EXV board for a faulty channel.

· Check for a faulty transducer.

· Check for a faulty economizer EXV or EXV wiring.

· Check for a faulty economizer EXV channel on the board.

· Check for a closed or partially closed suction service valve.

· Confirm unit configuration.
Loss of Communication Failures
Communication failure detection shall be made by checking the status of board  via LEN input table. The advantage of LEN input table concerning loss communication diagnostic is that it does not handle so much configurations like SIO protocol. 

Alarm 38, 39 and 40
Loss of Communication with Compressor Board 

Criteria For Trip    Tested when the compressor is On or Off

1.
If the Compressor Board #i exists and if communication with Compressor Board #i is lost (LEN input table  status = 3E or 3F) then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the effected compressor shall be stopped. 

2.
ALARM_LED LED shall be set to blinking

Reset Method
1.
Reset shall be automatic when the communication is re-established (variable status returns to normal).

2. The compressor shall be shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the power supply to the affected TCPM board.

· Check the address of the TCPM board to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Confirm unit configuration.
Alarm 41, 42,43
Loss of Communication with EXV Board 

Alarm 41 for circuit A (board #1), Alarm 42 for circuit B (board #2)or alarm 43 for circuit C (board #3)

Criteria For Trip    Tested when the unit is On or Off

1.
If communication with EXV Board is lost (LEN board input table status  = 3E) then the alarm 33 shall be tripped.

Action to be Taken
1.
If the alarm is tripped then circuit A (alarm 41) or circuit B (alarm 42) or circuit C (alarm 43) the unit shall be stopped immediately . 

2.
ALARM_LED LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the communication is reestablished (variable status returns to normal). 

Possible Causes — If this condition is encountered, check the following items:

· Check the power supply to the affected EXV board.

· Check the address of the EXV board to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Confirm unit configuration.
Alarm 44
Loss of Communication with Fan Board # 1
Action to be Taken
1.
If the alarm 44 is tripped and the number of fans per circuit  of both circuit  is greater then 4 fans then the only circuit A shall be stopped through stopping process (refer to stopping function), circuit B shall continue to run normally.   

2.
If the alarm 44 is tripped and number fans per circuit of both circuit is less then 5 then both circuit  shall be stopped through stopping process (refer to stopping function). 

3.
ALARM_LED shall be set to blinking. 

Reset Method
1. Reset shall be automatic when the communication is reestablished (variable status returns to normal). 

Possible Causes — If this condition is encountered, check the following items:

· Check the power supply to the affected Fan board.

· Check the address of the Fan board to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Confirm unit configuration.
Alarm 45
Loss of Communication with Fan Board # 2

Criteria For Trip    Tested when the unit is On or Off  and only if circuit A or B has more then 4 fans per circuit.  This fan handles fans on circuit B only.

1.
If communication with Fan  Board #2 is lost (LEN board input table status  = 3E) then the alarm 36 shall be tripped.

Action to be Taken
1.
If the alarm 45 is tripped then circuit B shall be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the communication is reestablished (variable status returns to normal). 

Possible Causes — If this condition is encountered, check the following items:

· Check the power supply to the affected Fan board.

· Check the address of the Fan board to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Confirm unit configuration.
Alarm 46
Loss of Communication with Fan Board # 3

Criteria For Trip    Tested when the unit is On or Off and only for the triple circuit as it is used by circuit C

1.
If communication with Fan  Board #3 is lost (LEN board input table status  = 3E) then the alarm 36 shall be tripped.

Action to be Taken
1.
If the alarm 46 is tripped then circuit C shall be stopped through stopping process (refer to stopping function). 

2.
ALARM_LED LED shall be set to blinking and alarm relay shall be energized.

Reset Method
1. Reset shall be automatic when the communication is reestablished (variable status returns to normal). 

Possible Causes — If this condition is encountered, check the following items:

· Check the power supply to the affected Fan board.

· Check the address of the Fan board to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Confirm unit configuration.
Alarm 47
Loss of Communication with Free Cooling board 1 (N/A)

Alarm 48
Loss of Communication with Free Cooling board 2 (N/A)

Alarm 49
Loss of Communication with Energy Management Board 

Criteria For Trip    Tested when the unit is On or Off and only if energy management option is enabled. 

1.
If communication with the energy management based on NRCP2 board is lost (LEN board input table status  = 3E) then the alarm 49 shall be tripped.

Action to be Taken
1.
The alarm shall be announced, all the functions such as three steps demand limit, 4-20mA reset , analog 4-20mA demand limit, space temp reset, occupancy override switch, ice duty function based on this board shall be aborted.  The unit shall continue to run. Alert relay shall be energized.

3.
ALARM_LED shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic when the communication is reestablished (variable status returns to normal).

Possible Causes — If this condition is encountered, check the following items:

· Check configuration to see if the EMM is installed, (Con-figuration ~UNIT~EMM). If (EMM=YES), check for a control option that requires the EMM that may be enabled. Correct configuration if not correct.

· Check the power supply to EMM.

· Check the address of the EMM to be sure that it is correct.

· Check the Local Equipment Network (LEN) wiring to be sure that it is connected properly.

· Check unit configuration to be sure that no options that require the EMM are enabled.
Alarm 50
Loss of Communication with Heat Reclaim Board (N/A)

Alarm 51
Loss of Communication with AUX Board 6 (N/A)

Alarm 52 
Cooler Freeze protection

Criteria For Trip    Tested only when the unit is On or Off.

1.
if fluid_typ = 1 then freeze = 34°F.


else  freeze = brine freeze setpoint (from SERVCE table).

2.
If the water cooler leaving or  entering water temperatures are below freeze, then alarm shall be tripped.

Action to be Taken
1.
If unit is on, then unit shall be stopped. The cooler pump (if the cooler pump is not controlled by the pro_dialog then cooler pump#1 shall be active) shall continue to run until the safety resets.

2.
For 50hz units, if unit is off and the cooler heater has been energized for more than 30 minutes and the heater detection thermistor reading is below 86° then, alarm shall be tripped.  If the cooler pump is not controlled by the pro_dialog then cooler pump#1 shall be active) shall continue to run until the safety resets.

3.
ALARM_LED shall be set to hold on. Alarm relay shall be energized.

Reset Method
1.
If the same alarm did not exist in the alarm history from last 24 hours then the reset shall be automatic when the water exchanger leaving fluid temperature is 6°F above the setpoint. The unit shall  restart normally.

2. Reset shall be manual if the same alarm existed in the alarm history  within 24 hours. The unit shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the entering and leaving fluid thermistors for accuracy.

· Check the water flow rate.

· Check loop volume. Low loop volume at nominal flow rates can in extreme cases bypass cold water to the cooler.

· Check for freezing conditions.

· Check heater tape and other freeze protection items for proper operation.

· Check glycol concentration.
· If the Leaving Water Set Point is above 40 F (4.4 C) and there is glycol in the loop, consider using the Medium Temperature Brine option (Configuration ~SERV~FLUD=2) to utilize the brine freeze point instead of 34F(1.1 C).
Alarm 53, 54 and 55 
Condenser Freeze Protection (N/A)

Alarm 56, 57 and 58 
Low Saturated Suction Temperature

Alarm 56 for circuit A, Alarm 57 for circuit B and 58 for circuit C

Criteria For Trip     Tested only when the circuit is ON.

A) in Cooling

1.
If the circuit is running and the Saturated Suction Temperature (SST) is 6 ^F or more below the freeze point for more than 3 minutes then the circuit shall be unloaded of 1 stage and an override 29 (circuit A), 30 (circuit B) and 31 (circuit C). 

2.
If SST is below - 13°F (-25°C) for more than 30 sec then the alarm shall be tripped.
3.
If SST is below - 22°F (-30°C) for more than 10 sec then the alarm shall be tripped.
Action To Be Taken before going to tripping
1.
If the circuit is running and the Saturated Suction Temperature is  6^F below the freeze point,  or below the freeze point  and pinch and superheat are greater than 15^F  then affected circuit capacity increase shall  be  disabled and the mode_state[LOW_SST_CIR_MODE] shall be set to ON. 

2.
If the circuit is running more than 30% and [the Saturated Suction Temperature is  18 ^F or more below the freeze point for more than 90 seconds or if Saturated Suction Temperature is below –4°F (-20°C) and the Saturated Suction Temperature 30s ago was 18^F lower than freeze point of it was lower than –4°F], then a stage capacity on the affected circuit  shall  be  removed and the mode_state[LOW_SST_CIR_MODE] shall be set to ON. 

3. If the alarm is tripped, the circuit shall be stopped.  ALARM_LED shall be set to blinking. Alarm relay shall be energized.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to Main Base Board (Alarm 56 and 57) or Fan Board C (Alarm 58).

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check cooler water flow.

· Check loop volume.

· Check EXV operation.

· Check for a liquid line refrigerant restriction, filter drier, service valve, etc.

· Check the refrigerant charge.

· If the Leaving Water Set Point is above 40 F (4.4 C) and there is glycol in the loop, consider using the Medium Temperature Brine option (Configuration ~ SERV~FLUD=2) to utilize the brine freeze point instead of 34F(1.1 C).
Alarm 59 & 60&61 
High Suction Superheat 

Alarm 59 for circuit A, Alarm 60 for circuit B and Alarm 61 for circuit C

Criteria For Trip    Tested only when the circuit is On.

1.
If the EXV position is at or above 98% and the suction superheat is 30 ^F greater than superheat control point and the evaporator suction temperature is less than the MOP setpoint for more than 5 minutes then the alarm shall be tripped.

Action to be Taken
1.
If the alarm is tripped then the circuit shall be stopped through stopping process (refer to stopping function).   Alarm relay shall be energized.

2.
ALARM_LED_A shall be set to blinking

Reset Method
1. Reset shall be manual and the circuit shall normally restart.

Possible Causes — If this condition is encountered, check the following items:

· Check the suction pressure transducer wiring to Main Base Board (Alarm 59, 60) or Fan Board C (Alarm 61).

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check the suction gas thermistor wiring to EXV Board.

· Check the suction gas thermistor sensor for accuracy.

· Check for EXV Boards for  faulty channel.

· Check EXV operation.

· Check for a liquid line refrigerant restriction, filter drier, service valve, etc.

· Check the refrigerant charge.

Alarm 62 & 63&64 
Low Suction Superheat 

Alarm 62 for circuit A, Alarm 63 for circuit B and Alarm 64 for circuit C

Criteria For Trip    Tested only when the circuit is On.

1.
If the EXV position is less than or equal to the 5% and either the (suction superheat is less than the superheat setpoint - 5°F or the evaporator suction temperature is greater than the MOP setpoint) for more than 5 minutes then the alert shall be tripped.

Action to be Taken
1.
The circuit shall be stopped after going through stopping process (refer to stopping function and alarm shall not be issued.

2.
If the above safety is tripped again within 24 hours then the circuit shall be stopped through stopping process (refer to stopping function) and alarm shall be issued. Alarm relay shall be energized.

3.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual and the unit shall normally restart.

Possible Causes — If this condition is encountered, check the following items:

· Check the suction pressure transducer wiring to Main Base Board (Alarm 62, 63) or Fan Board C (Alarm 64).

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check the suction gas thermistor wiring to EXV Boards.

· Check the suction gas thermistor sensor for accuracy.

· Check for EXV Boards for faulty channel.

· Check EXV operation.

· Confirm Maximum Operating Pressure Set Point.

· Check the refrigerant charge.
Alarm 65

Interlock Failure 

Criteria For Trip    

If the customer interlock switch (located on energy management module ) is “CLOSED” during normal operation then the alarm shall be tripped. 

Action to be Taken
1.
All compressors shall be stopped without going through pumpdown. The unit shall not started.

2.
ALARM_LED shall be set to On. Alarm relay shall be energized.

Reset Method
1. Reset shall be automatic if has not been occurred during last 24 hours. Otherwise, reset shall be manual.

Possible Causes — If this condition is encountered, check the following items:

· Check the chilled water flow switch operation.

· Check for water flow. Be sure all water isolation valves are open. Check the water strainer for a restriction.

· Check the interlock wiring circuit.

· Check for a power supply to the pump.

· Check for a control signal to the pump controller.

· Check the chilled water pump operation.

· Check the cooler pump contactor for proper operation.
ALARM  66
 Electrical Box Thermostat or Power Reverse Phase Detection (N/A)
Alarm 67
Loss of Communication with System Manager
Criteria For Trip    Tested when the unit is On and Off

1.
If the System Manager POC has established communication with the control and the communication is lost (for more than 2 minutes) then the alert shall be tripped.

Action to be Taken
1.
If auto_sm from SERVICVE table has been enabled then the control will force the CHIL_S_S variable to enable.

2.
All points forced by the System Manager (CHIL_S_S, CTRL_PNT, LCW_STPT, DEM_LIM) shall be autoed. The unit shall revert to standalone operation.

3.
ALARM_LED shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic upon regaining communication with the System Manager.

Possible Causes — If this condition is encountered, check the following items:

· Check communication wiring.

· Check the power supply to the System Manager and unit controls.
Alarm 68
Communication Failure between Master and Slave
Criteria For Trip    Tested when the unit is On and Off

1.
If the master_enabled = true or Slave_ enable = true and the communication is lost between  the master or slave (for more than 3 minutes) then the alert shall be tripped.

Action to be Taken
1.
See section  Master/slave function.

2.
ALARM_LED shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic upon regaining communication.

Possible Causes — If this condition is encountered, check the following items:

· Check the CCN wiring.

· Check for control power to each Main Base Board, Master and Slave.

· Confirm correct configuration.
ALARM 69,70,71
LOW OIL PRESSURE
Alarm 69 for circuit A, Alarm 70 for circuit B and Alarm 71 for circuit C

Criteria For Trip     Tested only when the compressor is ON.

`Poil' is the Oil Pressure transducer reading for the appropriate compressor.

sp is the Suction Pressure reading for the circuit involved.

dp is the discharge Pressure reading for the circuit involved.

    oil_sp1 = 0.7x (dp  - sp) + sp 

    oil_sp2 = sp + 7.2 psi  15 sec after start

    oil_sp2 = sp + 14.5 psi  45 sec after start


A. Compressor has started with normal ambient (oat > 2°C) or has run more than 30s 

1.
If the compressor is running and oil pressure is lower than the oil_sp1 or oil_sp 2 for more than than 15 seconds and then the alarm shall be tripped.

B. Compressor has started with Low Ambient (oat < 2°C) 

   1. 
If the compressor has been running for more than 30s and oil pressure is lower than the oil_sp1 or oil_sp 2 for more than than 15 seconds and then the alarm shall be tripped.

Action To Be Taken
1.
If the alarm is tripped  then the affected  compressor  shall be stopped. The other compressors  shall continue to run.

2.
ALARM_LED shall be set to blinking.

Reset Method
1.
Reset shall be automatic 3 minutes after if the same alarm has not been appeared ln last 24 hours


and compressor shall be then available,  else manual reset is required.

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to TCPM Board.

· Check the board for a faulty channel.

· Check for a faulty transducer.

· Check for a plugged oil filter

· Check for a faulty oil solenoid valve coil.

· Check for a stuck oil solenoid valve.

· Confirm unit configuration.
ALARM 72,73,74
MAX OIL FILTER DIFFERENTIAL PRESSURE FAILURE
Alarm 72 for circuit A, Alarm 73 for circuit B and Alarm 74 for circuit C

Criteria For Trip
Tested when compressor running for at least 5 seconds.

1.
If the difference between the Circuit Discharge Pressure and the Compressor Oil Pressure is greater than 50 PSI for more than 30 seconds, then the alarm shall be tripped.

Action to be Taken
1.
The compressor affected shall be turned off.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual. The affected compressor shall be restarted normally.

Possible Causes — If this condition is encountered, check the following items:

· Check the discharge and oil sensor wiring to the Main Base Board and TCPM Board.

· Check the boards for a faulty channel.

· Check for a faulty transducer.

· Check for a plugged oil filter

· Check for a faulty oil solenoid valve coil.

· Check for a stuck oil solenoid valve.
ALARM 75,76,77
HIGH OIL FILTER DROP PRESSURE 
Alarm 75 for circuit A, Alarm 76 for circuit B and Alarm 76 for circuit C

Criteria For Trip Tested when compressor running for at least 5 seconds.

1.
If the difference between the Circuit Discharge Pressure and the Compressor Oil Pressure is greater than 30 PSI for more than 5 minutes, then the alert shall be tripped.

Action to be Taken
1.
The compressor shall continue to run.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual. 

Possible Causes — If this condition is encountered, check the following items:

· Check the discharge and oil sensor wiring to the Main Base Board and TCPM Board.

· Check the boards for a faulty channel.

· Check for a faulty transducer.

· Check for a plugged oil filter

· Check for a faulty oil solenoid valve coil.

· Check for a stuck oil solenoid valve.
ALARM78,79,80
LOW OIL LEVEL FAILURE
Alarm 78 for circuit A, Alarm 79 for circuit B and Alarm 80 for circuit C

Criteria For Trip Tested when compressor running or off.

1.
If compressor is not running and capacity increase is required, then the compressor is not allowed to start. If it happens then the alarm shall be tripped.

2.
If the compressor is running and the oil level switch is opened for more than 45 seconds, then the alarm shall be tripped.

Action to be Taken
1.
The compressor affected shall be turned off.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be automatic when the oil level is high and the affected circuit shall be restarted normally.

2. Reset shall be manual if it has not been occurred more than 3 times during last 24 hours.

Possible Causes — If this condition is encountered, check the following items:

· Check the oil level in the oil separator

· Check the oil level switch wiring to TCPM Board.

· Check the TCPM boards for a faulty channel.

· Check for a faulty oil level switch.

Alarm 81
Master/Slave Operation error
Criteria For Trip    Tested when the unit is On and Off

1.
If the unit is master (ms_sel = master) and is in Master operating type and a master/slave configuration error (ms_error) from 1 to 11 is detected then the alert shall be tripped.

2.
If the unit is slave (ms_sel = slave) and is in CCN operating type and a master/slave configuration error (ms_error, see master/slave error code description) shall be tripped.

Action to be Taken
1.
The machine shall be prevented from starting in master slave operation. 

2.
ALARM_LED shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic when the master/slave configuration returns to normal or if unit is no more in Master operating type.

Possible Causes — If this condition is encountered, check the following items:

· Check the CCN wiring.

· Check for control power to each Main Base Board, Master and Slave.

· Confirm correct configuration.
Alarm 82
Initial factory configuration required
Criteria For Trip    Tested when the unit is On and Off

1.
If the Factory configuration parameters unitsize = 0 then the alarm shall be tripped. 

Action to be Taken
1.
The machine shall be prevented from starting. 

2.
ALARM_LED shall be set to hold on. Alarm relay shall be energized.

3.
Reinitialize all the other factory configuration parameters to 0.

Reset Method
1. Reset shall be automatic and shall require initial configuration.

Possible Causes — If this condition is encountered, confirm the unit configuration.

Alarm 83
Illegal configuration
Criteria For Trip    Tested when the unit is On and Off

1.
If one of the following is verified then the alarm shall be tripped. [debounce = 0]. Following is the illegal configuration number

1
Unit size is unknown

2
reclaim option select on heat pump

3
hot gas bypass configuration on heat pump

4
nb fan controlled by a varifan is bigger than expected. 

Action to be Taken
1.
The machine shall be prevented from starting. 

2.
ALARM_LED shall be set to hold on. Alarm relay shall be energized.

Reset Method
1.
Reset shall be automatic and shall require factory configuration modification.

Note: alarm shall be displayed as FC-x through the main interface alarm menu with x providing the illegal configuration number. 

Possible Causes — If this condition is encountered, confirm the unit configuration.

Alarm 84
Emergency Stop

Criteria For Trip    Tested when the unit is On and Off

1.
The only way this safety can be tripped is when the CCN command for an Emergency Stop is sent across the network.

Action to be Taken
1.
The unit shall be stopped.

2. ALARM_LED shall be set to hold on. Alarm relay shall be energized.

Reset Method
1. Reset shall be automatic after the CCN variable EMSTOP returns to normal. The unit shall be normally restarted.

Possible Causes — If this condition is encountered, check for CCN Emergency Stop command.

Alarm 85 
Cooler Pump #1 fault
Criteria For Trip    Tested only when the unit is On or Off.

1.
If the cooler pump run contact (PUMP_DEF) opens when pump #1 is commanded to be on then, the alarm shall be tripped. [debounce = 3 when starting the pump, debounce = 0 when unit is running]

Action to be Taken
1.
If the cooler pump #2 exists (pump_seq > 1) and if it is not failed (alarm[86] = no) then, the unit and the pump #1 shall be turned off. The pump #2 shall be started immediately and the unit shall be allowed to restart, ALARM_LED shall be set to blinking and alert relay shall be energized, 

2.
Else, then the pump and the unit shall be stopped. ALARM_LED shall be set to hold ON and alarm relay shall be energized.  

Reset Method
1. Reset shall be manual.

Possible Causes — If this condition is encountered, check the following items:

· Check the interlock wiring circuit.

· Check for a control signal to the pump controller.

· Check the cooler pump contactor for proper operation.

Alarm 86 
Cooler Pump #2 default
Criteria For Trip    Tested only when the unit is On or Off.

1.
If the cooler pump run contact (PUMP_DEF) opens when cooler pump #2 is commanded to be on then, the alarm shall be tripped. [debounce = 3 when starting the pump, debounce = 0 when unit is running]

Action to be Taken
1.
If the pump #1 is not failed (alarm[85] = no) then, the unit and the cooler pump #2 shall be turned off. The pump #1 shall be started immediately and the unit shall be allowed to restart, ALARM_LED shall be set to blinking and alert relay shall be energized, 

2.
Else, then the pump and the unit shall be stopped. ALARM_LED shall be set to hold ON and alarm relay shall be energized.  

Reset Method
1. Reset shall be manual.

Possible Causes — If this condition is encountered, check the following items:

· Check the interlock wiring circuit.

· Check for a control signal to the pump controller.

Check the cooler pump contactor for proper operation.
ALARM  
87  Condenser Flow Switch Failure  (N/A)

ALARM  
88, 89
Reclaim Operation Failure  refer to reclaim operation (N/A)

Alarm 90 & 91 & 92
Repeated high discharge gas temperature protection

Alarm 90 for circuit A, Alarm 91 for circuit B and Alarm 92 for circuit C

Criteria For Trip    Tested only when the circuit is On.

1. If the circuit is running and if more than 8 successive circuit capacity decreases have occurred because of high  discharge gas temperature overrides (based on compressor envelope) then, the circuit alarm shall be tripped. If  no override has occurred for more than 30 minutes then, the override counter shall be reset to zero (high_discharge_count = 0). This alarm can happen more in heating mode then cooling (cooling mode can happen on low brine application).

Action to be Taken
1.
 ALARM_LED shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic when the override counter returns to zero. In case of manual reset the override counter shall be forced to zero

Possible Causes — If this condition is encountered, check the following items:

· Check the Maximum Condensing Temperature (MCT) for the proper setting.

· Check for noncondensables in the refrigerant circuit.

· Check for condenser air re-circulation.

· Check for the proper refrigerant charge (overcharged).

· Check for operation beyond the limit of the machine.

· Check the condenser coils for debris or restriction.

· Check the condenser fans and motors for proper rotation and operation.

· Check the discharge service valve to be sure that it is open. check the discharge pressure transducer for accuracy.

· Confirm unit configuration.
Alarm 93 & 94 & 95
Repeated low suction temperature protection 

Alarm 93 for circuit A, Alarm 94 for circuit B Alarm 95 for circuit C

Criteria For Trip    Tested only when the circuit is On.

1. If the circuit operates and if more than 8 successive circuit capacity decreases (stop the compressor)  have occurred because of low suction temperature protection overrides then, the circuit alarm shall be tripped.  If no override has occurred for more than 30 minutes then, the override counter shall be reset to zero (low_suction_count. = 0).

Action to be Taken
1.
ALARM_LED  shall be set to blinking. Alert relay shall be energized.

Reset Method
1. Reset shall be automatic when the override counter returns to zero. In case of manual reset the override counter shall be forced to zero

Possible Causes — If this condition is encountered, check the following items:

· Check suction transducer for accuracy.

· Check suction transducer wiring.

· Check EXV operation.

· Check for the proper refrigerant charge (undercharged).

· Check evaporator loop for low water flow

· Check evaporator leaving water temperature

· Check the suction service valve to be sure that it is open. check the discharge pressure transducer for accuracy.

· Confirm unit configuration.
Alarm 96
Low entering water temperature in heating (N/A)

Alarm 97 
Condenser Pump #1 default (N/A)
Alarm 98 
Condenser Pump #2 default (N/A)
ALARM 99,100,101
  High Discharge Gas Temperature 
Alarm 99 for circuit A, Alarm 100 for circuit B and Alarm 101 for circuit C

Criteria For Trip
Tested when compressor is running.

1.
If the discharge gas temperature is higher than 100°C (212°F) for more than 90s then the alarm shall be tripped.

Action to be Taken
1.
The compressor shall be stopped.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual. 

Possible Causes — If this condition is encountered, check the following items:

· Check the Maximum Condensing Temperature (MCT) for the proper setting.

· Check for noncondensables in the refrigerant circuit.

· Check for condenser air re-circulation.

· Check for the proper refrigerant charge (overcharged).

· Check for operation beyond the limit of the machine.

· Check the condenser coils for debris or restriction.

· Check the condenser fans and motors for proper rotation and operation.

· Check the discharge service valve to be sure that it is open. check the discharge pressure transducer for accuracy.

· Confirm unit configuration.
ALARM 102,103,104
  Low Economizer Pressure 
Alarm 102 for circuit A, Alarm 103 for circuit B and Alarm 104 for circuit C on economizer units

Criteria For Trip
Tested when compressor is running to prevent pumpdown condition when suction check valve is closed.

1.
If the economizer pressure is below the suction pressure more than 1 bar (14.5 psi) for more than 10s then alarm shall be tripped.

Action to be Taken
1.
The compressor shall be stopped.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual. 

Possible Causes — If this condition is encountered, check the following items:

· Check if the suction service valve is closed.

· Check the sensor wiring to EXV boards.

· Check the boards for a faulty channels.
· Check for a faulty transducer.
· Check economizer EXV operations
ALARM 105,106,107
  Slide Valve Control Unverifiable 

Alarm 105 for circuit A, Alarm 106 for circuit B and Alarm 107 for circuit C

Criteria For Trip
Tested when compressor is running.

1. If the circuit is at 100 percent of capacity and the measured current is less than 1.3 current at 30% for more than consecutive times then alarm shall be tripped.

2. If the circuit is running and is at minimum load (30 percent of capacity)  and the measured current is greater than 0.78 * expected current at 100% of capacity then alarm shall be tripped.

Action to be Taken
1.
The compressor shall continue to run.

2.
ALARM_LED shall be set to blinking.

Reset Method
1. Reset shall be manual. 

Possible Causes — If this condition is encountered, check the following items:

· Check for faulty unloader solenoid valves.

· Check for faulty unloader solenoid coils.

· Check the wiring of the unloader solenoid valves.

· Check  the TCPM board for faulty channels

· Check the current transformer reading for accuracy

ALARM 108
  Cooler Flow Switch setpoint configuration failure (N/A)
Alarm 109

Cooler Flow Switch Failure 

Criteria For Trip    

A. Tested only when the unit is On.
1.
If the flow switch fails to close after the Off to On delay (m_state=ON) then the alarm shall be tripped.

2.
If the master/slave control is active and if the unit is the lag and if the cooler  flow switch fails to close within 1 minute after the cooler pump was restarted then the alarm shall be tripped (the lag pump is stopped when the lag chiller is forced off through a command emitted by the master - see section  master/slave). Alarm shall be ignored when the lag cooler pump is stopped due to master/slave control.

3.
flow switch is opened during normal operation then the alarm shall be tripped. 

B. Tested only when the unit is OFF.
1.
If the cooler pump control is enabled (pump_seq > 0) and cooler_flow _checking_when_pump_stop is enabled (in USER table) and If the cooler flow switch is closed after the cooler pump is commended OFF for more than 2 minutes then the alarm shall be tripped. 

2.
If the flow switch fails to close within the off to on delay after the cooler pump has been turned  to protect cooler from freezing (pump_seq > 0)  then the alarm shall be tripped.

Action to be Taken
1.
 For criteria for trip A1 and A2, the compressors shall not be started.

2.
 For criteria for trip A3, all compressors shall be stopped without going through pumpdown. Cooler pump shall be stopped with no delay.

3. 
 For criteria for trip B1,  the unit shall not  start.

4.
ALARM_LED shall be set to On. Alarm relay shall be energized.

Reset Method
1. Reset shall be shall be manual if at least one compressor is running. Otherwise, reset is automatic.

Possible Causes — If this condition is encountered, check the following items:

· Check for faulty flow switch

· Check flow switch wiring.

· Check Main Base Board for faulty channel.
Alarm 110
Service maintenance alert
Criteria For Trip    Tested when the unit is On and Off and If the Servicing Alert decision is enabled

. 

1.
If any of the following is true then, the alert shall be tripped. 

· Refrigerant charge is low (charge_m = enable and charge_c = low)

· Water loop size is low (wloop_m = enable and wloop_c = low)

· Air exchanger (aexch_m = enable and aexch_c = dirty

· Cooler Pump #1 service (pump1_m > 0 and pump1_c = alert)

· Cooler Pump #2 service (pump2_m > 0 and pump2_c = alert)

· Condenser Pump #1 service (hpump1_m > 0 and hpump1_c = alert)

· Condenser Pump #2 service (hpump2_m > 0 and hpump2_c = alert)

· Water filter service (wfilte_m > 0 and wfilte_c = alert)

· Compressor A Oil filter service (oilfia_m > 0 and oilfta_c = alert)

· Compressor B Oil filter service (oilfib_m > 0 and oilftb_c = alert)

· Compressor C Oil filter service (oilfic_m > 0 and oilftc_c = alert)

· Loss of charge is tested only in on mode

Action to be Taken
1. No action. ALARM_LED shall be set to blinking. Alert relay shall be energized. 

Reset Method
1.
Reset shall be manual. After reset, this alert shall not be issued anymore even if the maintenance alert point (S_RESET) has not been reset and is still zero.

Note: alarm shall be displayed as Sr-x on High Tier display or Sr.x on Comforlink display through alarm menu with x providing the operation or servicing delay identification.

Sr-01: Circuit A Loss of charged (refer to control capacity, low refrigerant charge override)

Sr-02: Circuit B Loss of charged (refer to control capacity, low refrigerant charge override)

Sr-03: Circuit C Loss of charged (refer to control capacity, low refrigerant charge override)

Sr-04: water loop size warning

Sr-05: Air exchanger cleanness warning

Sr-06: Cooler pump 1 servicing required

Sr-07: Cooler pump 2 servicing required

Sr-08: Condener pump 1 servicing required

Sr-09: Condenser pump 2 servicing required

Sr-10: water filter servicing required

Sr-11: Compressor A oil filter servicing required

Sr-12: Compressor B oil filter servicing required

Sr-13: Compressor C oil filter servicing required

Possible Causes — If this condition is encountered, check the following items:

· Check the sensor wiring to the Main Base Board.

· Check the sensor for accuracy.

For thermistor descriptions, identifiers and connections, see Thermistors List Below

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	







Service Test — Main power and control circuit power must be on for Service Test.

The Service Test function is used to verify proper operation of various devices within the chiller, such as condenser fan(s), compressors, minimum load valve solenoid (if installed), cooler pump(s) and remote alarm relay. This is helpful during the start-up procedure to determine if devices are installed correctly. See Fig. 34-37 for 30XA wiring diagrams.

To use the Service Test mode, the Enable/Off/Remote Con-tact switch must be in the OFF position. Use the display keys to move to the Service Test mode. The items are described in the Service Test table. There are two sub-modes available. Service Test~T.REQ allows for manual control of the compressors and minimum load control. In this mode the compressors will operate only on command. The capacity control and head pres​sure control algorithms will be active. The condenser fans will operate along with the EXVs. There must be a load on the chiller of operate for an extended period of time. All circuit safeties will be honored during the test. Service Test~QUIC allows for test of EXVs, condenser fans, pumps, low ambient head pressure control speed control, oil separator and cooler heat​ers, oil solenoids, unloader solenoids and status points (alarm relays, running status and chiller capacity). This mode allows for the testing of non-refrigeration items. If there are no keys pressed for 5 minutes, the active test mode will be disabled.

To enter the Manual Control mode, the Enable/Off/Remote Contact switch must be in the OFF position. Move the LED to
	password if required. Use either arrow key to change the

T.REQ value to ON and press

. Manual Control
ENTER
mode is now active. Press the arrow keys to move to the appro​priate item. To activate an item locate the item, press  
ENTER
and the display will show OFF. Press

and OFF will
ENTER
flash. Use either arrow key to change the value to ON and

press

. The item should be active. To turn the item
ENTER
off, locate the item, press
and the display will show
ENTER


	
ON. The chiller must be enabled by turning the Enable/Off/

Remote Contact switch to Enable. Press
and ON will ENTER
flash. Use either arrow key to change the value to OFF and

press
. The item should be inactive. ENTER


	To enter the Quick Test mode, the Enable/Off/Remote Contact switch must be in the OFF position. Move the LED to the Service Test mode. Press
to access TEST. Use
ENTER
the
key until the display reads QUIC. Press
to

ENTER access Q.REQ. Press
and the display will show OFF.

ENTER
Press
and OFF will flash. Enter the password if
ENTER
required. Use either arrow key to change the QUIC value to ON and press
. Quick Test mode is now active. Fol‑
ENTER
low the same instructions for the Manual Control mode to acti​vate a component.

Power must be applied to the unit. Enable/Off/Remote Contact switch must be in the OFF position.

Test the condenser fans, cooler pump(s) and alarm relay by changing the item values from OFF to ON. These discrete outputs are then turned off if there is no keypad activity for 10 minutes. Test the compressor and minimum load valve sole​noid (if installed) outputs in a similar manner. The minimum load valve solenoids will be turned off if there is no keypad activity for 10 minutes. Compressors will stay on until the operator turns them off. The Service Test mode will remain enabled for as long as there is one or more compressors running. All safeties are monitored during this test and will turn a compressor, circuit or the machine off if required. Any other mode or sub-mode can be accessed, viewed, or changed during the Manual Control mode only. The STAT item (Run Status ~VIEW) will display “0” as long as the Service mode is enabled. The TEST sub-mode value must be changed back to OFF before the chiller can be switched to Enable or Remote contact for normal operation.

NOTE: There may be up to a one-minute delay before the selected item is energized.


[image: image44.png]THUNDERBOLT

LOW VOLTAGE CONTROL SCHEMATIC 080

e i |8 .
o 2 ec| | B
PRl
MAIN BASE
BOARD
JiB @pL e
| | BE
Ji2 @y
J70 |3 o>
- o
5 7B [5| @5
E i e
7| R
5 J7A ] o>
3 ey
- —
E.;.J‘«m % ="
el [ 2eC
R3CEE] [ @
B I Al <a)
T[] R
S Tfvee  [sl o> =
5| 22
Blams=
ce@o T
D —— ]
cree el
<@ <]
SRR
[ ——
BN —EO) 2 J2C
<13

JTLYHIHIS.
04INDD Ave

0Z| Y0OZBZIODSNSOO |

T0
CPM-B
Jz

FROM
CPM-A
Ji2

!
L g
w01 |

J2§
ot

i’ gzt:;:@
e |Ga

[t momo ol

S
- Someor
B3 D
Sy o™
[ i cal
O

Sraoe

HiGE R e ey S

Som
it

ROUTE 70 EMN COMN PLUS
FOR EWH 0PTIo ONLY.
ROUTE T FAK DOARD 18
OMH PLUG' TOR ALL
GTHER SPTIONS.

&0

oo s 3

JOB  J9A
J78
EMM J7A|
BOARD
FIOP/ACCESSORY

J6






[image: image45.png]THUNDERBOLT LOW VOLTAGE CONTROL SCHEMATIC 090-350

JE
Joc
Jaa
i
Peeoey) MAN BASE

il S

§

§

ST
ERAERT
g
E R

oot
T —

0Z| YOOERZI00SNSHO00 |
P
iy





[image: image46.png]THUNDERBOLT LOW VOLTAGE CONTROL SCHEMATIC 400,450,500

] !
Joc
Jaa
i
Peeoey) MAN BASE
KT i

Rl

& :
@3 ] e

B Ea
bE
ta

I —— AT
&

11335
01N> A2

02| VO080W00SNSd00 |

/

e 1o g com puE T
R ta T kot in

n
e 1

FAN
BOARD
]

@ g






APPENDIX A — LOCAL DISPLAY TABLES
 

	
	
	
	
	
	STANDARD TIER DISPLAY MENU
	  Item Access: Password protect / Write;  Y = Password protected / Y = Write to Item

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM 

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	RUN STATUS
	VIEW
	EWT
	EWT
	XXX.X
	DEG F
	0 to 100
	Auto View of Run  Status
	Entering Fluid Temp
	N / N

	
	
	LWT
	LWT
	XXX.X
	DEG F
	0 to 100
	
	Leaving Fluid Temp 
	N / N

	
	
	SETP
	SP
	XXX.X
	DEG F
	0 to 100
	
	Active Setpoint
	N / N

	
	
	CTPT
	CTRL_PNT
	XXX.X
	DEG F
	0 to 100
	
	Control Point
	N / N

	
	
	STAT
	m_state
	X
	N/A
	0 to 3
	
	Unit Run Status
	N / N

	
	
	
	
	0
	
	
	
	OFF 
	

	
	
	
	
	1
	
	
	
	RUNNING
	

	
	
	
	
	2
	
	
	
	STOPPING
	

	
	
	
	
	3
	
	
	
	DELAY
	

	
	
	OCC
	CHIL_OCC
	NO-YES
	N/A
	NO-YES
	
	Occupied
	N / N

	
	
	CTRL
	ctr_type
	X
	N/A
	0 to 3
	
	Status Unit Control Type
	N / N

	
	
	
	
	0
	
	
	
	LOCAL OFF 
	

	
	
	
	
	1
	
	
	
	LOCAL ON
	

	
	
	
	
	2
	
	
	
	CCN
	

	
	
	
	
	3
	
	
	
	REMOTE
	

	
	
	CAP
	CAP_T
	XXX
	%
	0 to 100
	
	Percent Total Capacity
	N / N

	
	
	CAP.A
	CAPA_T
	XXX
	%
	0 to 100
	
	Percent Capacity cir A
	N / N

	
	
	CAP.B
	CAPB_T
	XXX
	%
	0 to 100
	
	Percent Capacity cir B
	N / N

	
	
	CAP.C
	CAPC_T
	XXX
	%
	0 to 100
	
	Percent Capacity cir C
	N / N

	
	
	LIM
	DEM_LIM
	XXX
	%
	0 to 100
	
	Active Demand Limit Val
	N / N

	
	
	CURR
	TOT_CURR
	XXXX
	amps
	0 to 1800
	
	Actual Chiller Current 
	N / N

	
	
	CUR.L
	CURR_LIM
	XXX
	amps
	0 to 100
	
	Chiller Current Limit
	N / N

	
	
	ALRM
	ALARM
	X
	N/A
	0 to 2
	
	Alarm State
	N / N

	
	
	
	
	0
	
	
	
	NORMAL 
	

	
	
	
	
	1
	
	
	
	PARTIAL
	

	
	
	
	
	2
	
	
	
	SHUTDOWN
	

	
	
	HC.ST
	HEATCOOL
	X
	N/A
	0 to 2
	
	Heat cool Status
	N / N

	
	
	
	
	0
	
	
	
	COOLING
	

	
	
	
	
	1
	
	
	
	HEATING
	

	
	
	
	
	2
	
	
	
	STANDBY
	

	
	
	RC.ST
	reclaim_sel
	NO-YES
	N/A
	NO-YES
	
	Reclaim Select Status
	N / N

	
	
	TIME
	TIME
	XX.XX
	N/A
	00.00-23.59
	
	Time of Day
	N / N

	
	
	MNTH
	moy
	XX
	N/A
	1-12
	
	Month of Year                              JAN-DEC
	N / N

	
	
	DATE
	dom
	XX
	N/A
	1-31
	
	Day of Month
	N / N

	
	
	YEAR
	yoc
	XX
	N/A
	00-99
	
	Year of Century
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM 

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	RUN
	HRS.U
	hr_mach
	XXXX
	HRS
	0-999999
	Unit Run Hour and Start
	Machine Operating Hours
	Y / Y

	
	
	STR.U
	st_mach
	XXXX
	N/A
	0-999999
	
	Machine Starts
	Y / Y

	
	
	HR.P1
	hr_cpump1
	XXXX
	HRS
	0-999999
	Water Pumps Hour
	Water Pump 1 Run Hours
	Y / Y

	
	
	HR.P2
	hr_cpump2
	XXXX
	HRS
	0-999999
	
	Water Pump 2 Run Hours
	Y / Y

	
	
	HR.P3
	hr_hpump1
	XXXX
	HRS
	0-999999
	
	Condenser Pump 1 Hours
	Y / Y

	
	
	HR.P4
	hr_hpump2
	XXXX
	HRS
	0-999999
	
	Condenser Pump 2 Hours
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	HOUR
	HR.A
	hr_cp_a
	XXXX
	HRS
	0-999999
	Compressors Run Hours
	Compressor A Run Hours
	Y / Y

	
	
	HR.B
	hr_cp_b
	XXXX
	HRS
	0-999999
	
	Compressor B Run Hours
	Y / Y

	
	
	HR.C
	hr_cp_c
	XXXX
	HRS
	0-999999
	
	Compressor C Run Hours
	Y / Y

	
	
	
	
	 
	 
	 
	
	
	

	
	STRT
	ST.A
	st_cp_a
	XXXX
	N/A
	0-999999
	Compressors Starts
	Compressor A Starts
	Y / Y

	
	
	ST.B
	st_cp_b
	XXXX
	N/A
	0-999999
	
	Compressor B Starts
	Y / Y

	
	
	ST.C
	st_cp_c
	XXXX
	N/A
	0-999999
	
	Compressor C Starts
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	FAN
	FR.A1
	hr_fana1
	XXXX
	HRS
	0-999999
	Fan Run Hours
	Fan 1 Run Hours Cir A
	Y / Y

	
	
	FR.A2
	hr_fana2
	XXXX
	HRS
	0-999999
	
	Fan 2 Run Hours Cir A
	Y / Y

	
	
	FR.A3
	hr_fana3
	XXXX
	HRS
	0-999999
	
	Fan 3 Run Hours Cir A
	Y / Y

	
	
	FR.A4
	hr_fana4
	XXXX
	HRS
	0-999999
	
	Fan 4 Run Hours Cir A
	Y / Y

	
	
	FR.A5
	hr_fana5
	XXXX
	HRS
	0-999999
	
	Fan 5 Run Hours Cir A
	Y / Y

	
	
	FR.A6
	hr_fana6
	XXXX
	HRS
	0-999999
	
	Fan 6 Run Hours Cir A
	Y / Y

	
	
	FR.A7
	hr_fana7
	XXXX
	HRS
	0-999999
	
	Fan 7 Run Hours Cir A
	Y / Y

	
	
	FR.A8
	hr_fana8
	XXXX
	HRS
	0-999999
	
	Fan 8 Run Hours Cir A
	Y / Y

	
	
	FR.A9
	hr_fana9
	XXXX
	HRS
	0-999999
	
	Fan 9 Run Hours Cir A
	Y / Y

	
	
	F.A10
	hrfana10
	XXXX
	HRS
	0-999999
	
	Fan 10 Run Hours Cir A
	Y / Y

	
	
	FR.B1
	hr_fanb1
	XXXX
	HRS
	0-999999
	
	Fan 1 Run Hours Cir B
	Y / Y

	
	
	FR.B2
	hr_fanb2
	XXXX
	HRS
	0-999999
	
	Fan 2 Run Hours Cir B
	Y / Y

	
	
	FR.B3
	hr_fanb3
	XXXX
	HRS
	0-999999
	
	Fan 3 Run Hours Cir B
	Y / Y

	
	
	FR.B4
	hr_fanb4
	XXXX
	HRS
	0-999999
	
	Fan 4 Run Hours Cir B
	Y / Y

	
	
	FR.B5
	hr_fanb5
	XXXX
	HRS
	0-999999
	
	Fan 5 Run Hours Cir B
	Y / Y

	
	
	FR.B6
	hr_fanb6
	XXXX
	HRS
	0-999999
	
	Fan 6 Run Hours Cir B
	Y / Y

	
	
	FR.B7
	hr_fana7
	XXXX
	HRS
	0-999999
	
	Fan 7 Run Hours Cir B
	Y / Y

	
	
	FR.B8
	hr_fana8
	XXXX
	HRS
	0-999999
	
	Fan 8 Run Hours Cir B
	Y / Y

	
	
	FR.B9
	hr_fanb9
	XXXX
	HRS
	0-999999
	
	Fan 9 Run Hours Cir B
	Y / Y

	
	
	F.B10
	hrfanb10
	XXXX
	HRS
	0-999999
	
	Fan 10 Run Hours Cir B
	Y / Y

	
	
	FR.C1
	hr_fanc1
	XXXX
	HRS
	0-999999
	
	Fan 1 Run Hours Cir C
	Y / Y

	
	
	FR.C2
	hr_fanc2
	XXXX
	HRS
	0-999999
	
	Fan 2 Run Hours Cir C
	Y / Y

	
	
	FR.C3
	hr_fanc3
	XXXX
	HRS
	0-999999
	
	Fan 3 Run Hours Cir C
	Y / Y

	
	
	FR.C4
	hr_fanc4
	XXXX
	HRS
	0-999999
	
	Fan 4 Run Hours Cir C
	Y / Y

	
	
	FR.C5
	hr_fanc5
	XXXX
	HRS
	0-999999
	
	Fan 5 Run Hours Cir C
	Y / Y

	
	
	FR.C6
	hr_fanc6
	XXXX
	HRS
	0-999999
	
	Fan 6 Run Hours Cir C
	Y / Y

	
	
	FR.C7
	hr_fanc7
	XXXX
	HRS
	0-999999
	
	Fan 7 Run Hours Cir C
	Y / Y

	
	
	FR.C8
	hr_fanc8
	XXXX
	HRS
	0-999999
	
	Fan 8 Run Hours Cir C
	Y / Y

	
	
	FR.C9
	hr_fana9
	XXXX
	HRS
	0-999999
	
	Fan 9 Run Hours Cir C
	Y / Y

	
	
	F.C10
	hrfana10
	XXXX
	HRS
	0-999999
	
	Fan 10 Run Hours Cir C
	Y / Y

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM 

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	
	CP.UN
	A.UN
	un_cp_a
	NO/YES
	N/A
	NO/YES
	Compressors Disable
	Compressor A Disable
	Y / Y

	
	
	B.UN
	un_cp_b
	NO/YES
	N/A
	NO/YES
	
	Compressor B Disable
	Y / Y

	
	
	C.UN
	un_cp_c
	NO/YES
	N/A
	NO/YES
	
	Compressor C Disable
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	MAIN
	
	
	
	
	
	Predictive Maintenance 
	
	N / N

	
	
	CHRG
	charge_m
	
	
	
	
	Refrigerant Charge
	N / N

	
	
	WATE
	wloop_m
	
	
	
	
	Water Loop Size
	N / N

	
	
	PMP.1
	cpump1_m
	
	
	
	
	Pump 1 (Days)
	N / N

	
	
	PMP.2
	cpump2_m
	
	
	
	
	Pump 2 (Days)
	N / N

	
	
	PMP.3
	hpump1_m
	
	
	
	
	Cond Pump 1 (Days)
	N / N

	
	
	PMP.4
	hpump2_m
	
	
	
	
	Cond Pump 1 (Days)
	N / N

	
	
	W.FIL
	wfilte_m
	
	
	
	
	Water Filter (days)
	N / N

	
	
	A.FIL
	ofilta_m
	
	
	
	
	Comp A Oil Filter (days)
	N / N

	
	
	B.FIL
	ofiltb_m
	
	
	
	
	Comp B Oil Filter (days)
	N / N

	
	
	C.FIL
	ofiltc_m
	
	
	
	
	Comp C Oil Filter (days)
	N / N

	
	
	
	
	
	
	
	
	
	

	
	VERS
	APPL
	PD5_APPL
	
	
	
	SOFTWARE VERSION NUMBER
	CSA-XXXXXXXXX
	N / N

	
	
	MARQ
	STDU
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	NAVI
	Navigator
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	EXVA
	EXV_BRDA
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	EXVB
	EXV_BRDB
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	EXVC
	EXV_BRDC
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	AUX1
	AUX_BRD1
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	AUX2
	AUX_BRD2
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	AUX3
	AUX_BRD3
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	AUX4
	AUX_BRD4
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	AUX5
	AUX_BRD5
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	SPMA
	SPM_CPA
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	SPMB
	SPM_CPB
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	SPMB
	SPM_CPC
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	EMM
	EMM_NRCP
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	R.BRD
	REC_NRCP
	
	
	
	
	XXXXXX-XX-XX
	N / N

	
	
	
	
	
	
	
	
	
	 

	SERVICE TEST
	TEST
	T.REQ
	service_test
	OFF-ON
	N/A
	OFF-ON
	Service Test Mode
	Manual Sequence
	Y / Y

	
	
	CP.A
	comp_serv_a
	OFF-ON
	N/A
	OFF-ON
	
	Compressor A Output
	Y / Y

	
	
	SLI.A
	comp_ser_sld_a
	0-2
	N/A
	0-2
	
	Slide Valve Capacity A
	Y / Y

	
	
	
	
	0
	
	
	
	UNCHANGED
	

	
	
	
	
	1
	
	
	
	INCREASE
	

	
	
	
	
	2
	
	
	
	DECREASE
	

	
	
	CP.B
	comp_serv_b
	OFF-ON
	N/A
	OFF-ON
	
	Compressor B Output
	Y / Y

	
	
	SLI.B
	comp_ser_sld_b
	0-2
	N/A
	0-2
	
	Slide Valve Capacity B
	Y / Y

	
	
	
	
	0
	
	
	
	UNCHANGED
	

	
	
	
	
	1
	
	
	
	INCREASE
	

	
	
	
	
	2
	
	
	
	DECREASE
	

	
	
	
	
	
	
	
	
	
	

	
	
	CP.C
	comp_serv_c
	OFF-ON
	N/A
	OFF-ON
	
	Compressor C Output
	Y / Y

	
	
	SLI.C
	comp_ser_sld_c
	0-2
	N/A
	0-2
	
	Slide Valve Capacity C
	Y / Y

	
	
	
	
	0
	
	
	
	UNCHANGED
	

	
	
	
	
	1
	
	
	
	INCREASE
	

	
	
	
	
	2
	
	
	
	DECREASE
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	QUIC
	Q.REQ
	test_request
	OFF-ON
	N/A
	OFF-ON
	
	QUICK TEST MODE
	Y / Y

	
	
	EXV.A
	exv_qck_a
	XXX
	%
	0-100
	
	Circuit A EXV % Open 
	Y / Y

	
	
	EXV.B
	exv_qck_b
	XXX
	%
	0-100
	
	Circuit B EXV % Open 
	Y / Y

	
	
	EXV.C
	exv_qck_a
	XXX
	%
	0-100
	
	Circuit C EXV % Open 
	Y / Y

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM 

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	   
	

	
	
	ECO.A
	eco_exv_qck_a
	XXX
	%
	0-100
	
	Circ A eco EXV % Open 
	Y / Y

	
	
	ECO.B
	eco_exv_qck_b
	XXX
	%
	0-100
	
	Circ B eco EXV % Open 
	Y / Y

	
	
	ECO.C
	eco_exv_qck_c
	XXX
	%
	0-100
	
	Circ C eco EXV % Open 
	Y / Y

	
	
	FAN.A
	fan_qck_a
	X
	N/A
	0-6
	
	Circuit A Fan Stages
	Y / Y

	
	
	FAN.B
	fan_qck_b
	X
	N/A
	0-6
	
	Circuit B Fan Stages
	Y / Y

	
	
	FAN.C
	fan_qck_c
	X
	N/A
	0-6
	
	Circuit C Fan Stages
	Y / Y

	
	
	SPD.A
	hd_qck_a
	XXX
	%
	0-100
	
	Cir A Head Press Speed
	Y / Y

	
	
	SPD.B
	hd_qck_b
	XXX
	%
	0-100
	
	Cir B Varifan position
	Y / Y

	
	
	SPD.C
	hd_qck_c
	XXX
	%
	0-100
	
	Cir C Varifan position
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	HT.A
	oil_ht_qck_a
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit A
	Y / Y

	
	
	SL1.A
	slid1_qck_a
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir A
	Y / Y

	
	
	SL2.A
	slid2_qck_a
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir A
	Y / Y

	
	
	OLS.A
	oil_sl_qck_a
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir A
	Y / Y

	
	
	DGT.A
	dgt_gascool_qck_a
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid A
	Y / Y

	
	
	HT.B
	oil_ht_qck_b
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit B
	Y / Y

	
	
	SL1.B
	slid1_qck_b
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir B
	Y / Y

	
	
	SL2.B
	slid2_qck_b
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir B
	Y / Y

	
	
	OLS.B
	oil_sl_qck_b
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir B
	Y / Y

	
	
	DGT.B
	dgt_gascool_qck_b
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid B
	Y / Y

	
	
	HT.C
	oil_ht_qck_c
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit C
	Y / Y

	
	
	SL1.C
	slid1_qck_c
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir C
	Y / Y

	
	
	SL2.C
	slid2_qck_c
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir C
	Y / Y

	
	
	OLS.C
	oil_sl_qck_c
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir C
	Y / Y

	
	
	DGT.C
	dgt_gascool_qck_c
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid C
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	FRV.A
	fr_qck_1a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Free Cooling Heater A 
	Y / Y

	
	
	FRP.A
	fr_qck_2a
	OFF-ON
	N/A
	OFF_ON
	
	Refrigerant Pump  A  
	Y / Y

	
	
	FRV.B
	fr_qck_1b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Free Cooling Heater B 
	Y / Y

	
	
	FRP.B
	fr_qck_2b
	OFF-ON
	N/A
	OFF_ON
	
	Refrigerant Pump  B  
	Y / Y

	
	
	FRV.C
	fr_qck_1c
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Free Cooling Heater C 
	Y / Y

	
	
	FRP.C
	fr_qck_2c
	OFF-ON
	N/A
	OFF_ON
	
	Refrigerant Pump  C  
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	RV.A
	rv_qck_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	4 Way Valve Circuit A
	Y / Y

	
	
	RV.B
	rv_qck_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	4 Way Valve Circuit B
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	HR1.A
	hr_ea_qck_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Enter Valve A
	Y / Y

	
	
	HR2.A
	hr_la_qck_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Leaving Valv  A
	Y / Y

	
	
	HR3.A
	hr_ew_qck_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Enter Valv A
	Y / Y

	
	
	HR4.A
	hr_lw_qck_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Leav Valve  A
	Y / Y

	
	
	HR1.B
	hr_ea_qck_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Enter Valve B
	Y / Y

	
	
	HR2.B
	hr_la_qck_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Leaving Valv  B
	Y / Y

	
	
	HR3.B
	hr_ew_qck_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Enter Valv B
	Y / Y

	
	
	HR4.B
	hr_lw_qck_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Leav Valve  B
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	PMP.1
	cpump1_qck
	OFF-ON
	N/A
	OFF-ON
	
	Water Exchanger Pump 1 
	Y / Y

	
	
	PMP.2
	cpump2_qck
	OFF-ON
	N/A
	OFF-ON
	
	Water Exchanger Pump 2 
	Y / Y

	
	
	PMP.3
	hpump1_qck
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Pump 1
	Y / Y

	
	
	PMP.4
	hpump2_qck
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Pump 2
	Y / Y

	
	
	CL.HT
	coo_heat_qck
	OFF-ON
	N/A
	OFF-ON
	
	Cooler heater Ouput 
	Y / Y

	
	
	BVL.A
	ref_iso_a_qck
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position A 
	N / N

	
	
	BVL.B
	ref_iso_b_qck
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position B 
	N / N

	
	
	BVL.C
	ref_iso_c_qck
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position C 
	N / N

	
	
	CP.HT
	cond_htr_qck
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Heater Output 
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	Q.RDY
	ready_qck
	OFF-ON
	N/A
	OFF-ON
	
	Chiller Readiy status
	Y / Y

	
	
	Q.RUN
	running_qck
	OFF-ON
	N/A
	OFF-ON
	
	Chiller Running status
	Y / Y

	
	
	SHUT
	shutdown_qck
	OFF-ON
	N/A
	OFF-ON
	
	Customer Shutdown Stat
	Y / Y

	
	
	CATO
	CAPT_010_qcK
	nn.n
	N/A
	nn.n
	
	Chiller capacity in 0-10v
	Y / Y

	
	
	ALRM
	alarm_qck
	OFF-ON
	N/A
	OFF-ON
	
	Alarm Relay
	Y / Y

	
	
	ALRT
	alert_qck
	OFF-ON
	N/A
	OFF-ON
	
	Alert Relay
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	TEMPERATURES
	UNIT
	CEWT
	COOL_EWT
	XXX.X
	DEG F
	-40 to 245
	Ent and Leave Unit Temp
	Cooler Entering Fluid
	N / N

	
	
	CLWT
	COOL_LWT
	XXX.X
	DEG F
	-40 to 245
	
	Cooler Leaving Fluid
	N / N

	
	
	CD.LT
	COND_LWT
	XXX.X
	DEG F
	-40 to 245
	
	Cooler Leaving Fluid
	N / N

	
	
	CD.ET
	COND_EWT
	XXX.X
	DEG F
	-40 to 245
	
	Cooler Entering Fluid
	N / N

	
	
	OAT
	OAT
	XXX.X
	DEG.F
	-40 to 245
	
	Outside Air Temperature
	N / N

	
	
	CHWS
	CHWS
	XXX.X
	DEG.F
	-40 to 245
	
	Lead/lag Leaving Fluid
	N / N

	
	
	HEWT
	HR_EWT
	XXX.X
	DEG F
	-40 to 245
	
	Heat Reclaim Entering 
	N / N

	
	
	HLWT
	HR_LWT
	XXX.X
	DEG F
	-40 to 245
	 
	Heat Reclaim Leaving 
	N / N

	
	
	SPT
	SPACETMP
	XXX.X
	DEG.F
	-40 to 245
	
	Optional Space Temp
	N / N

	
	
	THHR
	TH_HEATER
	XXX.X
	DEG.F
	-40 to 245
	
	Cooler Heater Temp
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	(Circuit A Temperatures)
	

	
	CIR.A
	SCT.A
	SCT_A
	XXX.X
	DEG F
	XXX.X
	Temperatures Circuit A
	Sat Cond Temp Circ A
	N / N

	
	
	SST.A
	SST_A
	XXX.X
	DEG F
	XXX.X
	 
	Sat Suction Temp Circ A
	N / N

	
	
	DGT.A
	DGT_A
	XXX.X
	DEG F
	XXX.X
	
	Discharge Gas Temp Cir A
	N / N

	
	
	SGT.A
	SUCT_T_A
	XXX.X
	DEG F
	XXX.X
	
	Suction Gas Temp Circ A
	N / N

	
	
	SUP.A
	SH_A
	XXX.X
	 ^F
	XXX.X
	
	Superheat Temp Circ A
	N / N

	
	
	ECT.A
	ECO_TP_A
	XXX.X
	DEG F
	XXX.X
	
	Economizer Gas Temp A
	N / N

	
	
	ESH.A
	ECO_SH_A
	XXX.X
	DEG F
	XXX.X
	
	Economizer Superheat A
	N / N

	
	
	CTP.A
	CP_TMP_A
	XXX.X
	DEG F
	XXX.X
	
	Motor Temperature Cir A
	N / N

	
	
	DEF.A
	DEFRT_A
	XXX.X
	DEG F
	-40 to 245
	
	Defrost Temp Circ A
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	(Circuit B Temperatures)
	

	
	CIR.B
	SCT.B
	SCT_B
	XXX.X
	DEG F
	XXX.X
	Temperatures Circuit B
	Sat Cond Temp Circ B
	N / N

	
	
	SST.B
	SST_B
	XXX.X
	DEG F
	XXX.X
	 
	Sat Suction Temp Circ B
	N / N

	
	
	DGT.B
	DGT_B
	XXX.X
	DEG F
	XXX.X
	
	Discharge Gas Temp Cir B
	N / N

	
	
	SGT.B
	SUCT_T_B
	XXX.X
	DEG F
	XXX.X
	
	Suction Gas Temp Circ B
	N / N

	
	
	SUP.B
	SH_B
	XXX.X
	 ^F
	XXX.X
	
	Superheat Temp Circ B
	N / N

	
	
	ECT.B
	ECO_TP_B
	XXX.X
	DEG F
	XXX.X
	
	Economizer Gas Temp B
	N / N

	
	
	ESH.B
	ECO_SH_B
	XXX.X
	DEG F
	XXX.X
	
	Economizer Superheat B
	N / N

	
	
	CTP.B
	CP_TMP_B
	XXX.X
	DEG F
	XXX.X
	
	Motor Temperature Cir B
	N / N

	
	
	DEF.B
	DEFRT_.B
	XXX.X
	DEG F
	-40 to 245
	
	Defrost Temp Circ B
	N / N

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	(Circuit C Temperatures)
	

	
	CIR.C
	SCT.C
	SCT_C
	XXX.X
	DEG F
	XXX.X
	Temperatures Circuit C
	Sat Cond Temp Circ C
	N / N

	
	
	SST.C
	DGT_C
	XXX.X
	DEG F
	XXX.X
	 
	Sat Suction Temp Circ C
	N / N

	
	
	DGT.C
	DGT_C
	XXX.X
	DEG F
	XXX.X
	
	Discharge Gas Temp Cir C
	N / N

	
	
	SGT.C
	SUCT_T_C
	XXX.X
	DEG F
	XXX.X
	
	Suction Gas Temp Circ C
	N / N

	
	
	SUP.C
	SH_C
	XXX.X
	 ^F
	XXX.X
	
	Superheat Temp Circ C
	N / N

	
	
	ECT.C
	ECO_TP_C
	XXX.X
	DEG F
	XXX.X
	
	Economizer Gas Temp C
	N / N

	
	
	ESH.C
	ECO_SH_C
	XXX.X
	DEG F
	XXX.X
	
	Economizer Superheat C
	N / N

	
	
	CTP.C
	CP_TMP_C
	XXX.X
	DEG F
	XXX.X
	
	Motor Temperature Cir C
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	(Circuit A)
	

	PRESSURES
	PRC.A
	DP.A
	DP_A
	XXX.X
	PSIG
	XXX.X
	Pressures Circuit A
	Discharge Pressure Cir A
	N / N

	
	
	SP.A
	SP_A
	XXX.X
	PSIG
	XXX.X
	 
	Suction Pressure Circ A
	N / N

	
	
	OP.A
	OP_A
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Circ A
	N / N

	
	
	DOP.A
	DOP_A
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Diff A
	N / N

	
	
	ECP.A
	ECON_P_A
	XXX.X
	PSIG
	XXX.X
	 
	Economizer Pressure  A
	N / N

	
	
	PDP.A
	PMPD_P_A
	XXX.X
	PSIG
	XXX.X
	 
	Reclaim Pressure  A
	N / N

	
	
	
	
	
	
	
	
	(Circuit B)
	

	
	PRC.B
	DP.B
	DP.B
	XXX.X
	PSIG
	XXX.X
	Pressures Circuit B
	Discharge Pressure Cir B
	N / N

	
	
	SP.B
	SP.B
	XXX.X
	PSIG
	XXX.X
	 
	Suction Pressure Circ B
	N / N

	
	
	OP.B
	OP_B
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Circ B
	N / N

	
	
	DOP.B
	DOP_B
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Diff B
	N / N

	
	
	ECP.B
	ECON_P_B
	XXX.X
	PSIG
	XXX.X
	 
	Economizer Pressure  B
	N / N

	
	
	PDP.B
	PMPD_P_B
	XXX.X
	PSIG
	XXX.X
	 
	Reclaim Pressure B
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	(Circuit C)
	

	
	PRC.C
	DP.C
	DP.C
	XXX.X
	PSIG
	XXX.X
	Pressures Circuit C
	Discharge Pressure Cir C
	N / N

	
	
	SP.C
	SP.C
	XXX.X
	PSIG
	XXX.X
	 
	Suction Pressure Circ C
	N / N

	
	
	OP.C
	OP_C
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Circ C
	N / N

	
	
	DOP.C
	DOP_C
	XXX.X
	PSIG
	XXX.X
	 
	Oil Pressure Diff C
	N / N

	
	
	ECP.C
	ECON_P_C
	XXX.X
	PSIG
	XXX.X
	 
	Economizer Pressure C
	N / N

	
	
	PDP.C
	PMPD_P_C
	XXX.X
	PSIG
	XXX.X
	 
	Reclaim Pressure  C
	N / N

	
	
	
	
	
	
	
	
	
	

	SETPOINTS
	COOL
	CSP.1
	csp1
	XXX.X
	DEG F
	 - 20 to 70
	Cooling Setpoints
	Cooling Setpoint 1
	N / Y

	
	
	CSP.2
	csp2
	XXX.X
	DEG F
	 - 20 to 70
	
	Cooling Setpoint 2
	N / Y

	
	
	CSP.3
	ice_sp
	XXX.X
	DEG F
	-20 to 32
	
	Ice Setpoint
	N / Y

	
	
	CRV1
	v_cr_no
	XXX.X
	ma
	0 to 20
	
	Current no Reset Val
	Y / Y

	
	
	CRV2
	v_cr_fu
	XXX.X
	ma
	0 to 20
	
	Current Full  Reset Val
	Y / Y

	
	
	CRT1
	dt_cr_no
	XXX.X
	^F
	0 to 125
	
	Delta T No Reset Temp
	Y / Y

	
	
	CRT2
	dt_cr_fu
	XXX.X
	^F
	0 to 125
	
	Delta T Full Reset Temp
	Y / Y

	
	
	CRO1
	oatcr_no
	XXX.X
	DEG F
	0 to 125
	
	OAT No Reset Temp
	Y / Y

	
	
	CRO2
	oatcr_fu
	XXX.X
	DEG F
	0 to 125
	
	OAT Full Reset Temp
	Y / Y

	MODE
	SUB-MODE
	ACRONYM
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	          ITEM                               VALUE
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION              DESCRIPTION
	ACCESS

	
	
	CRS1
	spacr_no
	XXX.X
	DEG F
	0 to 125
	
	Space T No Reset Temp
	Y / Y

	
	
	CRS2
	spacr_fu
	XXX.X
	DEG F
	0 to 125
	
	Space T Full Reset Temp
	Y / Y

	
	
	DGRC
	cr_deg
	XX.X
	^F
	 - 30 to 30
	
	Degrees Cool Reset
	Y / Y

	
	
	CAUT
	cauto_sp
	XXX.X
	°F
	39 to 122
	
	Cool Changeover Setpt
	Y / Y

	
	
	CRMP
	cramp_sp
	X.X
	^F
	0.2 to 2.0
	
	Cool Ramp Loading
	Y / Y

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	HEAT
	HSP.1
	HSP.1
	XXX.X
	DEG F
	80 to 140
	Heating Setpoints
	Heating Setpoint 1
	Y / Y

	
	
	HSP.2
	HSP.2
	XXX.X
	DEG F
	80 to 140
	
	Heating Setpoint 2
	Y / Y

	
	
	HRV1
	v_hr_no
	XXX.X
	ma
	0 to 20
	
	Current No Reset Val
	Y / Y

	
	
	HRV2
	v_hr_fu
	XXX.X
	ma
	0 to 20
	
	Current Full  Reset Val
	Y / Y

	
	
	HRT1
	dt_hr_no
	XXX.X
	^F
	0 to 125
	
	Delta T No Reset Temp
	Y / Y

	
	
	HRT2
	dt_hr_fu
	XXX.X
	^F
	0 to 125
	
	Delta T Full Reset Temp
	Y / Y

	
	
	HRO1
	oathr_no
	XXX.X
	DEG F
	0 to 125
	
	OAT T No Reset Temp
	Y / Y

	
	
	HRO2
	oathr_fu
	XXX.X
	DEG F
	0 to 125
	
	OAT Full Reset Temp
	Y / Y

	
	
	DGRH
	DGRH
	XX.X
	^F
	 - 30 to 30
	
	Degrees Heat Reset
	Y / Y

	
	
	HAUT
	hauto_sp
	XX.X
	°F
	39 to 122
	
	Heat Changeover Setpt
	Y / Y

	
	
	HRMP
	hramp_sp
	X.X
	^F
	0.2 to 2.0
	
	Heat Ramp Loading
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	MISC
	DLS1
	lim_sp1
	XXX
	%
	0-100
	Miscellaneous Setpoints
	Switch Limit Setpoint 1
	Y / Y

	
	
	DLS2
	lim_sp2
	XXX
	%
	0-100
	
	Switch Limit Setpoint 2
	Y / Y

	
	
	DLS3
	lim_sp3
	XXX
	%
	0-100
	
	Switch Limit Setpoint 3
	Y / Y

	
	
	W.SCT
	w_sct_sp
	XXX.X
	DEG F
	80 to 140
	
	Water Val Condensing Stp 
	N / Y

	
	
	
	
	
	
	
	
	
	

	
	
	RSP
	rsp
	XXX.X
	DEG F
	80 to 140
	Head Reclaim  Setpoints
	Head Reclaim Setpoint 
	N / Y

	
	
	RDB
	hr_deadb
	XXX.X
	^F
	-18 to 18
	 
	Reclaim deadband 
	N / Y

	
	
	
	
	
	
	
	
	
	

	INPUTS
	GEN.I
	ONOF
	ONOF
	OPEN-CLSE
	N/A
	OPEN-CLSE
	General Inputs
	On Off Switch
	N / N

	
	
	LOCK
	LOCK_1
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Cooler interlock
	N / N

	
	
	COND
	CONFLOW
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Condenser Flow Switch
	N / N

	
	
	DLS1
	LIM_SW1
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Demand Limit Switch 1
	N / N

	
	
	DLS2
	LIM_SW2
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Demand Limit Switch 2
	N / N

	
	
	ICE.D
	ICE_SW
	OFF-ON
	N/A
	OFF-ON
	
	Ice Done
	N / N

	
	
	DUAL
	SETP_SW
	OFF-ON
	N/A
	OFF-ON
	
	Dual Setpoint Switch 
	N / N

	
	
	ELEC
	ELEC_BOX
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Electrical Box Safety
	N / N

	
	
	PUMP
	PUMP_DEF
	OFF-ON
	N/A
	OFF-ON
	
	Cooler Pump Feedback 
	N / N

	
	
	OCCS
	OCC_OVSW
	OFF-ON
	N/A
	OFF-ON
	
	Occupancy Override Swit
	N / N

	
	
	RECL
	RECL_SW
	OFF-ON
	N/A
	OFF-ON
	
	Heat Reclaim Switch 
	N / N

	
	
	HC.SW
	HC_SW
	OFF-ON
	N/A
	OFF-ON
	
	Heat Cool Switch Status 
	N / N

	
	
	RLOC
	REM_LOCK
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Remote Interlock Switch
	N / N

	
	
	OIL.A
	OIL_L_A
	LOW-HIGH
	N/A
	LOW_HIGH
	
	Oil Level Circuit A
	N / N

	
	
	OIL.B
	OIL_L_B
	LOW-HIGH
	N/A
	LOW_HIGH
	
	Oil Level Circuit B
	N / N

	
	
	OIL.C
	OIL_L_C
	LOW-HIGH
	N/A
	LOW_HIGH
	
	Oil Level Circuit C
	N / N

	
	
	
	
	
	
	
	
	
	 

	
	
	CUR.A
	CURR_A
	XXX.X
	AMPS
	0 to 600
	
	Motor Current Circuit A
	N / N

	
	
	CUR.B
	CURR_B
	XXX.X
	AMPS
	0 to 600
	
	Motor Current Circuit B
	N / N

	
	
	CUR.C
	CURR_C
	XXX.X
	AMPS
	0 to 600
	
	Motor Current Circuit C
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	DMND
	LIM_ANAL
	XX.X
	mA
	4 to 20
	
	4-20mA Demand Signal
	N / N

	
	
	RSET
	SP_RESET
	XX.X
	mA
	4 to 20
	
	4-20mA Reset/Setpoint
	N / N

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	OUTPUTS
	CIR.A
	CP.A
	CP_A
	OFF-ON
	N/A
	OFF-ON
	Outputs Circuit A
	Compressor A Relay
	N / N

	
	
	HT.A
	OIL_HT_A
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit A
	N / N

	
	
	SL1.A
	SLID1_A
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir A
	N / N

	
	
	SL2.A
	SLID2_A
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir A
	N / N

	
	
	OLS.A
	OIL_SL_A
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir A
	N / N

	
	
	FAN.A
	FAN_ST_A
	X
	N/A
	0-6
	
	Circuit A Fan Stages
	N / N

	
	
	SPD.A
	hd_pos_a
	XXX
	%
	0-100
	
	Circ A Variable Speed
	N / N

	
	
	EXV.A
	EXV_A
	XXX
	%
	0-100
	
	Circuit A EXV % Open 
	N / N

	
	
	ECO.A
	EXV_EC_A
	XXX
	%
	0-100
	
	Circ A EXV eco % Open
	N / N

	
	
	DGT.A
	dgt_gascool_a
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid A
	N / N

	
	
	FRP.A
	FR_PMP_A
	OFF-ON
	N/A
	OFF_ON
	
	Refrigerant Pump Out A 
	N / N

	
	
	FRH.A
	FR_HEATA
	OFF-ON
	N/A
	OFF_ON
	
	Free Cooling Heater A
	N / N

	
	
	HR1.A
	HR1.A
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Enter Valve A
	N / N

	
	
	HR2.A
	HR2.A
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Leaving Valv  A
	N / N

	
	
	HR3.A
	HR3.A
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Enter Valv A
	N / N

	
	
	HR4.A
	HR4.A
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Leav Valve  A
	N / N

	
	
	RV.A
	RV.A
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	4 Way Valve Circuit A
	N / N

	
	
	
	
	
	
	
	
	
	

	
	CIR.B
	CP.B1
	CP_B1
	OFF-ON
	N/A
	OFF-ON
	Outputs Circuit B
	Compressor B Relay
	N / N

	
	
	HT.B
	OIL_HT_B
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit B
	N / N

	
	
	SL1.B
	SLID1_B
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir B
	N / N

	
	
	SL2.B
	SLID2_B
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir B
	N / N

	
	
	OLS.B
	OIL_SL_B
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir B
	N / N

	
	
	FAN.B
	FAN_ST_B
	X
	N/A
	0-6
	
	Circuit B Fan Stages
	N / N

	
	
	SPD.B
	hd_pos_b
	XXX
	%
	0-100
	
	Circ B Varifan position
	N / N

	
	
	EXV.B
	EXV_B
	XXX
	%
	0-100
	
	Circuit B EXV % Open 
	N / N

	
	
	ECO.B
	EXV_EC_B
	XXX
	%
	0-100
	
	Circ B EXV eco % Open
	N / N

	
	
	DGT.B
	dgt_gascool_b
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid B
	N / N

	
	
	FRP.B
	FR_BMP_B
	OFF-ON
	N/A
	OFF-ON
	
	Refrigerant Pump Out B
	N / N

	
	
	FRHB
	FR_HEATB
	OFF-ON
	N/A
	OFF_ON
	
	Free Cooling Heater B
	N / N

	
	
	FRB2
	FR_BP2_B
	OFF-ON
	N/A
	OFF_ON
	
	Bypass Valv 2 Output
	N / N

	
	
	HR1.B
	HR1.B
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Enter Valve A
	N / N

	
	
	HR2.B
	HR2.B
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Air Cond Leaving Valv  A
	N / N

	
	
	HR3.B
	HR3.B
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Enter Valv A
	N / N

	
	
	HR4.B
	HR4.B
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Water Cond Leav Valve  A
	N / N

	
	
	RV.B
	RV.B
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	4 Way Valve Circuit B
	N / N

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	CIR.C
	CP.C1
	CP_C1
	OFF-ON
	N/A
	OFF-ON
	Outputs Circuit C
	Compressor C1 Relay
	N / N

	
	
	HT.C
	OIL_HT_C
	OFF-ON
	N/A
	OFF-ON
	
	Oil Heater Circuit C
	N / N

	
	
	SL1.C
	SLID1_C
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 1 Cir C
	N / N

	
	
	SL2.C
	SLID2_C
	OFF-ON
	N/A
	OFF-ON
	
	Slide Valve 2 Cir C
	N / N

	
	
	OLS.C
	OIL_SL_C
	OFF-ON
	N/A
	OFF-ON
	
	Oil Solenoid Cir C
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	FAN.C
	FAN_St_C
	X
	N/A
	0-6
	
	Circuit C Fan Stages
	N / N

	
	
	SPD.C
	hd_pos_c
	XXX
	%
	0-100
	
	Circ C Varifan position
	N / N

	
	
	EXV.C
	EXV_C
	XXX
	%
	0-100
	
	Circuit C EXV % Open 
	N / N

	
	
	ECO.C
	EXV_EC_C
	XXX
	%
	0-100
	
	Circ C EXV eco % Open
	N / N

	
	
	DGT.C
	dgt_gascool_c
	OFF-ON
	N/A
	OFF-ON
	
	DGT Cool Solenoid C
	N / N

	
	
	FRP.C
	FR_BMP_C
	OFF-ON
	N/A
	OFF-ON
	
	Refrigerant Pump Out C
	N / N

	
	
	FRHC
	FR_HEATC
	OFF-ON
	N/A
	OFF_ON
	
	Free Cooling Heater C
	N / N

	
	
	
	
	
	
	
	
	
	

	
	GEN.O
	PMP.1
	CPUMP_1
	OFF-ON
	N/A
	OFF-ON
	General outputs
	Water Exchanger Pump 1 
	N / N

	
	
	PMP.2
	CPUMP_2
	OFF-ON
	N/A
	OFF-ON
	
	Water Exchanger Pump 2 
	N / N

	
	
	PMP.3
	HPUMP_1
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Pump 1
	Y / Y

	
	
	PMP.4
	HPUMP_2
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Pump 2
	Y / Y

	
	
	CO.HT
	COOLHEAT
	OFF-ON
	N/A
	OFF-ON
	
	Cooler heater Ouput 
	N / N

	
	
	BVL.A
	ref_iso_a
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position A 
	N / N

	
	
	BVL.B
	ref_iso_b
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position B 
	N / N

	
	
	BVL.C
	ref_iso_c
	OPEN-CLSE
	N/A
	OPEN-CLSE
	
	Ball Valve Position C 
	N / N

	
	
	CN.HT
	cond_htr
	OFF-ON
	N/A
	OFF-ON
	
	Condenser Heater Output 
	N / N

	
	
	REDY
	ready
	OFF-ON
	N/A
	OFF-ON
	
	Chiller Readiy status
	Y / Y

	
	
	RUN
	running
	OFF-ON
	N/A
	OFF-ON
	
	Chiller Running status
	Y / Y

	
	
	SHUT
	shutdown
	OFF-ON
	N/A
	OFF-ON
	
	Customer Shutdown Stat
	Y / Y

	
	
	CATO
	CAPT_010
	nn.n
	N/A
	nn.n
	
	Chiller capacity 0-10v
	Y / Y

	
	
	ALRM
	alarm
	OFF-ON
	N/A
	OFF-ON
	
	Alarm Relay
	N / N

	
	
	ALRT
	alert
	OFF-ON
	N/A
	OFF-ON
	
	Alert Relay 
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	CONFIGURATION
	DISP
	TEST
	display_test
	OFF-ON
	N/A
	OFF-ON
	Display Configuration
	Test Display LED's
	N / Y

	
	
	METR
	DISPUNIT
	X
	N/A
	US-METR
	
	Metric Display 
	Y / Y

	
	
	LANG
	LANGUAGE
	 X
	N/A
	0-4
	
	Language Selection
	Y / Y

	
	
	
	
	0
	
	
	
	ENGLISH
	

	
	
	
	
	1
	
	
	
	ESPANOL
	

	
	
	
	
	2
	
	
	
	FRANCAIS
	

	
	
	
	
	3
	
	
	
	PORTUGUES
	

	
	
	
	
	4
	
	
	
	TRANSLATED
	

	
	UNIT
	TYPE
	unit_typ
	X
	N/A
	1 to 2
	Unit Configuration
	Unit Type 
	N / N

	
	
	
	
	1
	
	
	
	Air Cooled
	

	
	
	
	
	2
	
	
	
	Heatpump
	

	
	
	
	
	3
	
	
	
	Water Cooled
	

	
	
	
	
	4
	
	
	
	Heat Machine
	

	
	
	TONS
	unitsize
	XXX
	TONS
	50to 300
	
	Unit Size
	Y / Y

	
	
	VAR.A
	varfan_a
	0-6
	0-6
	0 to 6
	
	NB Fans on Varifan Cir A
	Y / Y

	
	
	VAR.B
	varfan_b
	0-6
	0-6
	0 to 6
	
	NB Fans on Varifan Cir B
	Y / Y

	
	
	VAR.C
	varfan_c
	0-6
	0-6
	0 to 6
	
	NB Fans on Varifan Cir C
	Y / Y

	
	
	VOLT
	voltage
	XXX
	VOLT
	208 to 690
	
	Power Supply Voltage
	Y / Y

	
	
	60HZ
	freq_60H
	NO-YES
	N/A
	NO-YES
	
	60HZ frequency 
	Y / Y

	
	
	STAR
	softstar
	NO-YES
	N/A
	NO-YES
	
	Soft Starter Select
	Y / Y

	
	
	Y.D
	wye_delt
	NO-YES
	N/A
	NO-YES
	
	Wye Deltat Start Select
	Y / Y

	
	
	MTA.A
	cpa_mtac
	XXX
	Amps
	0 to 1500
	
	Must Trip Amps cir A
	

	
	
	R.MT.A
	cpa_mtam
	XXX
	Amps
	0 to 1500
	
	Read Must Trip Amps A
	

	
	
	MTA.B
	cpb_mtac
	XXX
	Amps
	0 to 1500
	
	Must Trip Amps cir B
	

	
	
	R.MT.B
	cpb_mtam
	XXX
	Amps
	0 to 1500
	
	Read Must Trip Amps B
	

	
	
	MTA.C
	cpc_mtac
	XXX
	Amps
	0 to 1500
	
	Must Trip Amps cir C
	

	
	
	R.MT.C
	cpb_mtam
	XXX
	Amps
	0 to 1500
	
	Read Must Trip Amps C
	

	
	
	C.SW.A
	cpa_s1_c
	XXX
	N/A
	0 to 255
	
	S1 Config switch cir A
	

	
	
	R.CS.A
	cpa_s1_m
	XXX
	N/A
	0 to 255
	
	Read S1 Config switch A
	

	
	
	C.SW.B
	cpb_s1_c
	XXX
	N/A
	0 to 255
	
	S1 Config switch cir B
	

	
	
	R.CS.B
	cpb_s1_m
	XXX
	N/A
	0 to 255
	
	Read S1 Config switch B
	

	
	
	C.SW.C
	cpc_s1_c
	XXX
	N/A
	0 to 255
	
	S1 Config switch cir C
	

	
	
	R.CS.C
	cpc_s1_m
	XXX
	N/A
	0 to 255
	
	Read S1 Config switch C
	

	
	
	RECL
	recl_opt
	NO-YES
	N/A
	NO-YES
	
	Heat Reclaim Select
	Y / Y

	
	
	EHS
	ehs_sel
	0-4
	0-4
	0 to 4
	
	Electrical Heater Stage
	Y / Y

	
	
	EMM
	emm_nrcp
	NO-YES
	N/A
	NO-YES
	
	EMM module installed
	Y / Y

	
	
	PAS.E
	pass_ebl
	NO-YES
	N/A
	NO-YES
	
	Password Enable
	Y / Y

	
	
	PASS
	fac_pass
	XXX
	N/A
	1-255
	
	Factory Password
	Y / Y

	
	
	CO.HT
	heat_sel
	NO-YES
	N/A
	NO-YES
	
	Cooler Heater Select
	Y / Y

	
	
	CON.V
	cond_val
	NO-YES
	N/A
	NO-YES
	
	Condenser Valve Select
	Y / Y

	
	
	FREE
	freecool
	NO-YES
	N/A
	NO-YES
	
	Free cooling Select
	Y / Y

	
	
	HI.TI
	highdisp
	NO-YES
	N/A
	NO-YES
	
	High Tiers display Selec
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	SERV
	FLUD
	flui_typ
	1-2
	N/A
	1-3
	
	Cooler Fluid Type
	Y / Y

	
	
	
	
	1
	
	
	
	WATER
	

	
	
	
	
	2
	
	
	
	BRINE
	

	
	
	CFLU
	cond_typ
	1-2
	N/A
	1-2
	
	Condenser Fluid Type
	Y / Y

	
	
	
	
	1
	
	
	
	WATER
	

	
	
	
	
	2
	
	
	
	BRINE
	

	
	
	MOP
	mop_sp
	XX.X
	°F
	40-60
	 
	EXV MOP Setpoint
	Y / Y

	
	
	HP.TH
	hp_th
	XXX.X
	psi
	500-640
	 
	High Pressure  Threshold
	Y / Y

	
	
	SHP.A
	sh_sp_a
	XX.X
	^F
	3 TO 14
	
	Cir A Superheat Setp
	Y / Y

	
	
	SHP.B
	sh_sp_b
	XX.X
	^F
	3 TO 14
	
	Cir B Superheat Setp
	Y / Y

	
	
	SHP.C
	sp_sp_c
	XX.X
	^F
	3 TO 14
	
	Cir C Superheat Setp
	Y / Y

	
	
	HTR
	heatersp
	XX.X
	^F
	0.5 TO 9
	
	Cooler Heater DT Setp
	Y / Y

	
	
	EWTO
	ewt_opt
	NO-YES
	N/A
	NO-YES
	
	Entering water control
	Y / Y

	
	
	AU.SM
	auto_sm
	NO-YES
	N/A
	NO-YES
	
	Auto Start when SM lost
	Y / Y

	
	
	LOSP
	lowestsp
	XX.X
	°F
	-20 to 50
	
	Brine Freeze Setpoint
	Y / Y

	
	
	HD.PG
	hd_pg
	XX.X
	N/A
	-10 to 10
	
	Varifan Proportion Gain 
	Y / Y

	
	
	HD.DG
	hd_dg
	XX.X
	N/A
	-10 to 10
	
	Varifan Derivative Gain 
	Y / Y

	
	
	HD.IG
	hd_ig
	XX.X
	N/A
	-10 to 10
	
	Varifan Integral Gain 
	Y / Y

	
	
	HR.MI
	min_3w
	XXX.X
	%
	0 to 100
	
	Reclaim Water Valve Min 
	Y / Y

	
	
	HR.MA
	max_3w
	XXX.X
	%
	0 to 100
	
	Reclaim Water Valve Max 
	Y / Y

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	OPTN
	CCNA
	CCNA
	XXX
	N/A
	1-239
	Unit Options 2 Controls
	CCN  ADDRESS 
	Y / Y

	
	
	CCNB
	CCNB
	XXX
	N/A
	0-239
	
	CCN  BUS NUMBER 
	Y / Y

	
	
	BAUD
	BAUD
	X
	N/A
	1-5
	
	CCN BAUD RATE
	Y / Y

	
	
	
	
	1
	
	
	
	2400
	

	
	
	
	
	2
	
	
	
	4800
	

	
	
	
	
	3
	
	
	
	9600
	

	
	
	
	
	4
	
	
	
	19200
	

	
	
	
	
	5
	
	
	
	38400
	

	
	
	
	
	
	
	
	
	
	

	
	
	LLCS
	seq_typ
	X
	N/A
	0-1-2-3
	
	Lead/Lag Circuit Select
	Y / Y

	
	
	
	
	0
	
	
	
	AUTOMATIC
	

	
	
	
	
	1
	
	
	
	CIR A LEADS
	

	
	
	
	
	2
	
	
	
	CIR B LEADS
	

	
	
	
	
	3
	
	
	
	CIR C LEADS
	

	
	
	LOAD
	lead_cir
	X
	N/A
	0-1
	
	Loading Sequence Select
	Y / Y

	
	
	
	
	0
	
	
	
	EQUAL
	

	
	
	
	
	1
	
	
	
	STAGED
	

	
	
	RL.S
	ramp_sel
	ENBL-DSBL
	N/A
	ENBL-DSBL
	
	Ramp Load Select
	Y / Y

	
	
	DELY
	off_on_d
	XX
	MIN
	0-15
	
	Minutes Off Time
	Y / Y

	
	
	ICE.M
	ice_cnfg
	ENBL-DSBL
	N/A
	ENBL-DSBL
	
	Ice Mode Enable
	Y / Y

	
	
	HPUM
	hpum_seq
	X
	N/A
	0-1-2-3-4
	
	Condenser Pumps Sequence
	Y / Y

	
	
	
	
	0
	
	
	
	NO PUMP
	

	
	
	
	
	1
	
	
	
	1 PUMP ONLY
	

	
	
	
	
	2
	
	
	
	2 PUMPS AUTO
	

	
	
	
	
	3
	
	
	
	 PMP 1 MANUAL
	

	
	
	
	
	4
	
	
	
	 PMP 2 MANUAL
	

	
	
	PUMP
	pump_seq
	X
	N/A
	0-1-2-3-4
	
	Cooler Pumps Sequence
	Y / Y

	
	
	
	
	0
	
	
	
	NO PUMP
	

	
	
	
	
	1
	
	
	
	1 PUMP ONLY
	

	
	
	
	
	2
	
	
	
	2 PUMPS AUTO
	

	
	
	
	
	3
	
	
	
	 PMP 1 MANUAL
	

	
	
	
	
	4
	
	
	
	 PMP 2 MANUAL
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	
	ROT.P
	pump_del
	XX
	
	24 to 3000
	
	Pump Rotation delay
	Y / Y

	
	
	PM.PS
	pump_per
	NO-YES
	N/A
	NO-YES
	
	Periodic Pump Start
	Y / Y

	
	
	PSBY
	pump_sby
	NO-YES
	N/A
	NO-YES
	
	Stop Pump In Standby 
	Y / Y

	
	
	P.LOC
	pump_loc
	NO-YES
	N/A
	NO-YES
	
	Flow checked if Pmp Off  
	Y / Y

	
	
	LS.ST
	nh_start
	XX.XX
	N/A
	00.00-23.59
	
	Night Low Noise Start 
	Y / Y

	
	
	LS.ND
	nh_end
	XX.XX
	N/A
	00.00-23.59
	
	Night Low noise End
	Y / Y

	
	
	LS.LT
	nh_limit
	XXX
	%
	0 to 100
	
	Low noise Capacity Lim
	Y / Y

	
	
	RV.AL
	al_rever
	NO-YES
	N/A
	NO-YES
	
	Reverse Alarms Relay  
	Y / Y

	
	
	OATH
	heat_th
	XX.X
	N/A
	-4 to 32
	
	Heat Mode OAT Threshold
	Y / Y

	
	
	FREE
	free_oat
	XX.X
	N/A
	-4 to 37.4
	
	Free Cooling OAT Limit
	Y / Y

	
	
	CUR.S
	curr_sel
	NO-YES
	N/A
	NO-YES
	
	Current Limit Select  
	Y / Y

	
	
	CUR.F
	curr_ful
	XXXX
	N/A
	0 to 5000
	
	Current Limit at 100%
	Y / Y

	
	
	EHST
	ehs_th
	XX.XX
	N/A
	23-70
	
	Elec Stag OAT Threshold
	Y / Y

	
	
	EHSB
	ehs_back
	NO-YES
	N/A
	NO-YES
	
	Last Heat Elec Backup
	Y / Y

	
	
	E.DEF
	ehs_defr
	NO-YES
	N/A
	NO-YES
	
	Quick EHS in Defrost 
	Y / Y

	
	
	EHSP
	ehs_pull
	XX
	MIN
	0 to 60
	
	Elec Heating pulldown
	Y / Y

	
	
	AUTO
	auto_sel
	NO-YES
	N/A
	NO-YES
	
	Auto Changeover Select
	Y / Y

	 
	RSET
	CRST
	cr_sel
	X
	N/A
	0-1-2-3-4
	Reset Cool  and Heat Tmp
	Cooling Reset Type
	Y / Y

	
	
	
	
	0
	
	
	
	NO RESET
	

	
	
	
	
	1
	
	
	
	OUT AIR TEMP
	

	
	
	
	
	2
	
	
	
	DELTAT TEMP 
	

	
	
	
	
	3
	
	
	
	4-20mA INPUT
	

	
	
	
	
	4
	
	
	
	SPACE TEMP
	

	
	
	
	
	
	
	
	
	
	

	
	
	HRST
	hr_sel
	X
	N/A
	0-1-2-3
	
	Heating Reset Type
	Y / Y

	
	
	
	
	0
	
	
	
	NO RESET
	

	
	
	
	
	1
	
	
	
	OUT AIR TEMP
	

	
	
	
	
	2
	
	
	
	DELTAT TEMP 
	

	
	
	
	
	3
	
	
	
	4-20mA INPUT
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	
	
	
	
	
	
	
	
	

	
	
	DMDC
	lim_sel
	X
	N/A
	0-1-2
	
	Demand Limit Select
	Y / Y

	
	
	
	
	0
	
	
	
	NONE
	

	
	
	
	
	1
	
	
	
	SWITCH
	

	
	
	
	
	2
	
	
	
	4-20mA INPUT
	

	
	
	DMMX
	lim_mx
	XX.X
	mA
	0-20.0
	
	mA for 100% demand lim
	Y / Y

	
	
	DMZE
	lim_ze
	XX.X
	%
	0-20.0
	
	mA for 0% demand limit
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	MSSL
	ms_sel
	X
	N/A
	0-1-2-
	
	Master/Slave Select
	Y / Y

	
	
	
	
	0
	
	
	
	DISABLE
	

	
	
	
	
	1
	
	
	
	MASTER 
	

	
	
	
	
	2
	
	
	
	SLAVE
	

	
	
	SLVA
	slv_addr
	XXX
	N/A
	1-236
	
	Slave Address
	Y / Y

	
	
	LLBL
	ll_bal
	ENBL-DSBL
	N/A
	ENBL-DSBL
	
	Lead/Lag Balance Select
	Y / Y

	
	
	LLBD
	ll_bal_d
	XXX
	HRS
	40-400
	
	Lead/Lag Balance Delta
	Y / Y

	
	
	LLDY
	lsrt_tim
	XX
	MIN
	1-30
	
	Lag Start Delay
	Y / Y

	
	
	LAGP
	lag_pump
	X
	N/A
	0-1-2-
	
	Lag Unit Pump Select
	Y / Y

	
	
	
	
	0
	
	
	
	Off if U stp
	

	
	
	
	
	1
	
	
	
	On if U stop 
	

	
	
	LPUL
	lead_pul
	XX
	MIN
	0 to 60
	
	Lead Pulldown Time
	Y / Y

	
	
	SERI
	ll_serie
	NO-YES
	N/A
	NO-YES
	
	Chillers in series 
	Y / Y

	
	
	
	
	
	
	
	
	
	 

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	TIME CLOCK
	TIME
	HH.MM
	HH.MM
	XX.XX
	N/A
	00.00-23.59
	Time of Day
	Hour and Minute
	N / Y

	
	
	
	
	
	
	
	
	
	

	
	DATE
	MNTH
	MNTH
	XX
	N/A
	1-12
	Month Date Day and Year
	Month of Year                              JAN-DEC
	N / Y

	
	
	DOM
	DOM
	XX
	N/A
	1 to 31
	
	Day of Month
	N / Y

	
	
	DAY
	DAY
	X
	N/A
	1-7
	
	Day of Week                              MON-SUN
	N / Y

	
	
	YEAR
	YEAR
	XX
	N/A
	 00-99
	
	Year of Century
	N / Y

	
	
	
	
	
	
	
	
	
	

	
	SCH1
	OCC_1
	occ_1
	XX.XX
	N/A
	00.00-23.59
	Time Schedule 1
	Occupied Time
	Y / Y

	
	
	UNO_1
	uno_1
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER1
	MON.1
	monday_1
	NO-YES
	N/A
	NO-YES
	Period 1 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.1
	tuesda_1
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.1
	wednes_1
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.1
	thursd_1
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.1
	friday_1
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.1
	saturd_1
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.1
	sunday_1
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.1
	holida_1
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_2
	occ_2
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_2
	uno_2
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER2
	MON.2
	monday_2
	NO-YES
	N/A
	NO-YES
	Period 2 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.2
	tuesda_2
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.2
	wednes_2
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.2
	thursd_2
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.2
	friday_2
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.2
	saturd_2
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.2
	sunday_2
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.2
	holida_2
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_3
	occ_3
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_3
	uno_3
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER3
	MON.3
	monday_3
	NO-YES
	N/A
	NO-YES
	Period 3 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.3
	tuesda_3
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.3
	wednes_3
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.3
	thursd_3
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.3
	friday_3
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.3
	saturd_3
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.3
	sunday_3
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.3
	holida_3
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_4
	occ_4
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_4
	uno_4
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER4
	MON.4
	monday_4
	NO-YES
	N/A
	NO-YES
	Period 4 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.4
	tuesda_4
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.4
	wednes_4
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.4
	thursd_4
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.4
	friday_4
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.4
	saturd_4
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.4
	sunday_4
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.4
	holida_4
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_5
	occ_5
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_5
	uno_5
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER5
	MON.5
	monday_5
	NO-YES
	N/A
	NO-YES
	Period 5 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.5
	tuesda_5
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.5
	wednes_5
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.5
	thursd_5
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.5
	friday_5
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.5
	saturd_5
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.5
	sunday_5
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.5
	holida_5
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_6
	occ_6
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_6
	uno_6
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER6
	MON.6
	monday_6
	NO-YES
	N/A
	NO-YES
	Period 6 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.6
	tuesda_6
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.6
	wednes_6
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.6
	thursd_6
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.6
	friday_6
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.6
	saturd_6
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.6
	sunday_6
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.6
	holida_6
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_7
	occ_7
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_7
	uno_7
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER7
	MON.7
	monday_7
	NO-YES
	N/A
	NO-YES
	Period 7 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.7
	tuesda_7
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.7
	wednes_7
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.7
	thursd_7
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.7
	friday_7
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.7
	saturd_7
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.7
	sunday_7
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.7
	holida_7
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_8
	occ_8
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_8
	uno_8
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER8
	MON.8
	monday_8
	NO-YES
	N/A
	NO-YES
	Period 8 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.8
	tuesda_8
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.8
	wednes_8
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.8
	thursd_8
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.8
	friday_8
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.8
	saturd_8
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.8
	sunday_8
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.8
	holida_8
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	SCH2
	OCC_1
	occ_1
	XX.XX
	N/A
	00.00-23.59
	Time Schedule 2
	Occupied Time
	Y / Y

	
	
	UNO_1
	uno_1
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER1
	MON.1
	monday_1
	NO-YES
	N/A
	NO-YES
	
	Monday Select
	Y / Y

	
	
	TUE.1
	tuesda_1
	NO-YES
	N/A
	NO-YES
	Period 1 Occ/Unocc Se
	Tuesday Select
	Y / Y

	
	
	WED.1
	wednes_1
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.1
	thursd_1
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.1
	friday_1
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.1
	saturd_1
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.1
	sunday_1
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.1
	holida_1
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_2
	occ_2
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_2
	uno_2
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER2
	MON.2
	monday_2
	NO-YES
	N/A
	NO-YES
	Period 2 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.2
	tuesda_2
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.2
	wednes_2
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.2
	thursd_2
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.2
	friday_2
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.2
	saturd_2
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.2
	sunday_2
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.2
	holida_2
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_3
	occ_3
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_3
	uno_3
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER3
	MON.3
	monday_3
	NO-YES
	N/A
	NO-YES
	Period 3 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.3
	tuesda_3
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.3
	wednes_3
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.3
	thursd_3
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.3
	friday_3
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.3
	saturd_3
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.3
	sunday_3
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.3
	holida_3
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_4
	occ_4
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_4
	uno_4
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER4
	MON.4
	monday_4
	NO-YES
	N/A
	NO-YES
	Period 4 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.4
	tuesda_4
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.4
	wednes_4
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.4
	thursd_4
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.4
	friday_4
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.4
	saturd_4
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.4
	sunday_4
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.4
	holida_4
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_5
	occ_5
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_5
	uno_5
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER5
	MON.5
	monday_5
	NO-YES
	N/A
	NO-YES
	Period 5 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.5
	tuesda_5
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.5
	wednes_5
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.5
	thursd_5
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.5
	friday_5
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.5
	saturd_5
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.5
	sunday_5
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.5
	holida_5
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_6
	occ_6
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_6
	uno_6
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER6
	MON.6
	monday_6
	NO-YES
	N/A
	NO-YES
	Period 6 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.6
	tuesda_6
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.6
	wednes_6
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.6
	thursd_6
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.6
	friday_6
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.6
	saturd_6
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.6
	sunday_6
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.6
	holida_6
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_7
	occ_7
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_7
	uno_7
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER7
	MON.7
	monday_7
	NO-YES
	N/A
	NO-YES
	Period 7 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.7
	tuesda_7
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.7
	wednes_7
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.7
	thursd_7
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.7
	friday_7
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.7
	saturd_7
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.7
	sunday_7
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.7
	holida_7
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	OCC_8
	occ_8
	XX.XX
	N/A
	00.00-23.59
	
	Occupied Time
	Y / Y

	
	
	UNO_8
	uno_8
	XX.XX
	N/A
	00.00-23.59
	
	Unoccupied Time
	Y / Y

	
	PER8
	MON.8
	monday_8
	NO-YES
	N/A
	NO-YES
	Period 8 Occ/Unocc Sel
	Monday Select
	Y / Y

	
	
	TUE.8
	tuesda_8
	NO-YES
	N/A
	NO-YES
	
	Tuesday Select
	Y / Y

	
	
	WED.8
	wednes_8
	NO-YES
	N/A
	NO-YES
	
	Wednesday Select
	Y / Y

	
	
	THU.8
	thursd_8
	NO-YES
	N/A
	NO-YES
	
	Thursday Select
	Y / Y

	
	
	FRI.8
	friday_8
	NO-YES
	N/A
	NO-YES
	
	Friday Select
	Y / Y

	
	
	SAT.8
	saturd_8
	NO-YES
	N/A
	NO-YES
	
	Saturday Select
	Y / Y

	
	
	SUN.8
	sunday_8
	NO-YES
	N/A
	NO-YES
	
	Sunday Select
	Y / Y

	
	
	HOL.8
	holida_8
	NO-YES
	N/A
	NO-YES
	
	Holiday Select
	Y / Y

	
	
	
	
	
	
	
	
	
	Y / Y

	
	HOLI
	
	
	
	
	
	Holidays configuration
	
	

	
	HOL.1
	MON.1
	t60f_b2[0][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.1
	t60f_b2[0][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.1
	t60f_b2[0][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.2
	MON.2
	t60f_b2[1][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.2
	t60f_b2[1][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.2
	t60f_b2[1][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.3
	MON.3
	t60f_b2[2][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.3
	t60f_b2[2][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.3
	t60f_b2[2][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.4
	MON.4
	t60f_b2[3][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.4
	t60f_b2[3][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.4
	t60f_b2[3][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.5
	MON.5
	t60f_b2[4][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.5
	t60f_b2[4][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.5
	t60f_b2[4][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.6
	MON.3
	t60f_b2[5][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.3
	t60f_b2[5][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.3
	t60f_b2[5][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.7
	MON.7
	t60f_b2[6][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.7
	t60f_b2[6][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.7
	t60f_b2[6][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.8
	MON.8
	t60f_b2[7][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.8
	t60f_b2[7][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.8
	t60f_b2[7][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HOL.9
	MON.9
	t60f_b2[8][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DAY.9
	t60f_b2[8][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DUR.9
	t60f_b2[8][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.10
	MO.10
	t60f_b2[9][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.10
	t60f_b2[9][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.10
	t60f_b2[9][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.11
	MO.11
	t60f_b2[10][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.11
	t60f_b2[10][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.11
	t60f_b2[10][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.12
	MO.12
	t60f_b2[11][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.12
	t60f_b2[11][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.12
	t60f_b2[11][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.12
	MO.12
	t60f_b2[11][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.12
	t60f_b2[11][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.12
	t60f_b2[11][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.13
	MO.13
	t60f_b2[12][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.13
	t60f_b2[12][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.13
	t60f_b2[12][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.14
	MO.14
	t60f_b2[13][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.14
	t60f_b2[131][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.14
	t60f_b2[13][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.15
	MO.15
	t60f_b2[14][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.15
	t60f_b2[14][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.15
	t60f_b2[14][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	HO.16
	MO.16
	t60f_b2[15][0]
	XX
	N/A
	0-12
	Holidays config nb
	Holiday Start Month
	Y / Y

	
	
	DA.16
	t60f_b2[15][1]
	XX
	N/A
	0-31
	
	Holiday Start Day
	Y / Y

	
	
	DU.16
	t60f_b2[15][2]
	XX
	N/A
	0-99
	
	Holiday Duration in day
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	MCFG
	AL.SV
	s_alert
	NO-YES
	N/A
	NO-YES
	Service Maintenance Conf
	Servicing Warning Select
	Y / Y

	
	
	CHRG
	charge_m
	NO-YES
	N/A
	NO-YES
	
	Refrigerant Charge
	Y / Y

	
	
	WATE
	wloop_c
	NO-YES
	N/A
	NO-YES
	
	Water Loop Size
	Y / Y

	
	
	PMP.1
	cpump1_c
	nnnn
	N/A
	nnnn
	
	Pump 1 (days)
	Y / Y

	
	
	PMP.2
	cpump2_c
	nnnn
	N/A
	nnnn
	
	Pump 2 (days)
	Y / Y

	
	
	PMP.3
	hpump1_c
	nnnn
	N/A
	nnnn
	
	Cond Pump 1 (days)
	Y / Y

	
	
	PMP.4
	hpump2_c
	nnnn
	N/A
	nnnn
	
	Cond Pump 2 (days)
	Y / Y

	
	
	W.FIL
	wfilte_c
	nnnn
	N/A
	nnnn
	
	Water Filter (days)
	Y / Y

	
	
	A.FIL
	ofilta_c
	nnnn
	N/A
	nnnn
	
	Comp A Oil Filter (days)
	Y / Y

	
	
	B.FIL
	ofiltb_c
	nnnn
	N/A
	nnnn
	
	Comp B Oil Filter (days)
	Y / Y

	
	
	C.FIL
	ofiltc_c
	nnnn
	N/A
	nnnn
	
	Comp C Oil Filter (days)
	Y / Y

	
	
	RS.SV
	s_reset
	0 to 11
	N/A
	0 to 11
	
	Servicing Alert Reset
	Y / Y

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	MODE
	SUB-MODE
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	(LEVEL 2)
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	OPERATING MODES
	SLCT
	OPER
	stdu_opertype
	X
	N/A
	0-1-2
	Operating Type Control 
	Operating Type Control
	Y / Y

	
	
	
	
	0
	
	
	
	SWITCH CTRL  
	

	
	
	
	
	1
	
	
	
	TIME SCHED 
	

	
	
	
	
	2
	
	
	
	CCN CONTROL  
	

	
	
	SP.SE
	sp_sel
	X
	N/A
	0-1-2-3-4
	Setpoint  Load
	Setpoint Select
	Y / Y

	
	
	
	
	0
	
	
	
	SETPOINT OCC
	

	
	
	
	
	1
	
	
	
	SETPOINT1
	

	
	
	
	
	2
	
	
	
	SETPOINT2
	

	
	
	
	
	3
	
	
	
	4-20MA SETP
	

	
	
	
	
	4
	
	
	
	DUAL SETP SW  
	

	
	
	HC.SE
	hc_sel
	X
	N/A
	0-1-2
	
	Heat Cool  Select
	Y / Y

	
	
	
	
	0
	
	
	
	COOLING
	

	
	
	
	
	1
	
	
	
	HEATING
	

	
	
	
	
	2
	
	
	
	AUTO CHGOVER
	

	
	
	
	
	3
	
	
	
	HEAT COOL SW
	

	
	
	RL.SE
	recl_sel
	X
	N/A
	0-1-2
	
	Reclaim  Select
	Y / Y

	
	
	
	
	0
	
	
	
	NO
	

	
	
	
	
	1
	
	
	
	YES
	

	
	
	
	
	2
	
	
	
	 Switch Ctrl
	

	
	
	
	
	
	
	
	
	
	

	MODE
	 
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	 
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	
	MODE
	MD01
	MD01
	0-30
	N/A
	0-30
	Modes Controlling Unit 
	First active mode 
	N / N

	
	
	MD02
	MD02
	0-30
	N/A
	0-30
	 
	second active mode 
	N / N

	
	
	MD03
	MD03
	0-30
	N/A
	0-30
	
	Third active mode      
	N / N

	
	
	MD04
	MD04
	0-30
	N/A
	0-30
	
	Fourth active mode
	N / N

	
	
	MD05
	MD05
	0-30
	N/A
	0-30
	
	Fifth active mode
	N / N

	
	
	MD06
	MD06
	0-30
	N/A
	0-30
	
	Sixth active mode
	N / N

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	MODE
	 
	ACRONYM 
	ITEM 
	ITEM 
	ITEM 
	ITEM 
	SUB-MODE
	ITEM 
	ITEM

	(LEVEL 1 W/ LED)
	 
	(LEVEL 3)
	(LEVEL 3)
	VALUE
	UNITS
	RANGE 
	DESCRIPTION
	DESCRIPTION
	ACCESS

	ALARMS
	
	R.ALM
	reset_alarm
	NO-YES
	N/A
	NO-YES
	
	Reset all Current Alarms
	Y / Y

	
	 ALRM
	ALM1
	alarm_1
	A000-A999
	N/A
	A000-A999
	 Currently Active Alarms
	Current Alarm 1
	N / N

	
	
	ALM2
	alarm_2
	A000-A999
	N/A
	A000-A999
	 
	Current Alarm 2
	N / N

	
	
	ALM3
	alarm_3
	A000-A999
	N/A
	A000-A999
	 
	Current Alarm 3
	N / N

	
	
	ALM4
	alarm_4
	A000-A999
	N/A
	A000-A999
	 
	Current Alarm 4
	N / N

	
	
	ALM5
	alarm_5
	A000-A999
	N/A
	A000-A999
	 
	Current Alarm 5
	N / N

	
	 H.ALM
	HA.01
	alm_history_01
	A000-A999
	N/A
	A000-A999
	 Alarm history
	Alarm History #1
	N / N

	
	
	HA.02
	alm_history_02
	A000-A999
	N/A
	A000-A999
	 
	Alarm History #2
	N / N

	
	
	---
	---
	---
	---
	---
	
	---
	---

	
	
	HA.49
	alm_history_49
	A000-A999
	N/A
	A000-A999
	 
	Alarm History #49
	N / N

	
	
	HA.50
	alm_history_50
	A000-A999
	N/A
	A000-A999
	 
	Alarm History #50
	N / N


	AIR COOLED, COOLING 60HZ UNITS

COMPRESSOR , FANS & EXV’s ARRANGEMENT

	comp_a
	fan_a
	fan_a

shared
	exv_a

setps
	economizer A exv steps
	comp_b
	fan_b
	fan_B

shared
	exv_b

setps
	economizer B exv steps
	comp_c
	fan_c
	fan_c

shared
	exv_c

setps
	economizer C exv steps

	TS45
	3
	2_B
	  3690
	0
	TS45
	3
	2_A
	3690
	0
	0
	0
	0
	0
	0

	TS45
	4
	0
	3690
	2785
	TS45
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TS50
	4
	0
	3690
	2785
	TS50
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TS60
	4
	0
	3690
	2785
	TS50
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TS60
	4
	0
	3690
	2785
	TS60
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT90
	6
	0
	3690
	2785
	TS50
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT100
	6
	0
	3690
	2785
	TS60
	4
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT90
	6
	0
	3690
	2785
	TT90
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT100
	6
	0
	3690
	2785
	TT100
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT120
	7 
	0
	3690
	2785
	TT100
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TT120
	7
	0
	3690
	2785
	TT120
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TU165
	9
	0
	3690
	2785
	TT100
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TU165
	9 
	4_B
	3690
	2785
	TT120
	7
	5_A
	3690
	2785
	0
	0
	0
	0
	0

	TU185
	10
	0
	3690
	2785
	TT120
	6
	0
	3690
	2785
	0
	0
	0
	0
	0

	TU165
	9
	5_B
	3690
	2785
	TU165
	9
	5_A
	3690
	2785
	0
	0
	0
	0
	0

	TU185
	9
	5_B
	3690
	2785
	TU165
	9
	5_A
	3690
	2785
	0
	0
	0
	0
	0

	TT120
	6
	0
	3690
	2785
	TT120
	6
	0
	3690
	2785
	TU165
	8
	0
	3690
	2785

	TU185
	8
	0
	3690
	2785
	TT90
	6
	0
	3690
	2785
	TU185
	8
	0
	3690
	2785

	TU185
	8
	0
	3690
	2785
	TT120
	6
	0
	3690
	2785
	TU185
	8
	0
	3690
	2785


DISPLAY SCREEN
TABLE NAME: GENUNIT      PIC TABLE TYPE : 11H, instance 1

DESCRIPTION
STATUS
UNITS
  POINTS   FORCEABLE
1
GENERAL PARAMETERS

2

3
Control Type
Local/CCN/Remote1
-
ctr_type
N

4
Run Status
running/Off/Stopping/Delay2
-
STATUS
N

5
CCN Chiller Start/Stop
Enable/Dsable3
-
CHIL_S_S
Y

6
Chiller Occupied?
Yes/No4
-
CHIL_OCC
Y

7
Minutes Left for Start
0-15
min
min_left
N

8
Heat/Cool Status
Heat/Cool/Standby11
-
HEATCOOL

9
Heat/Cool Select
0/1/25
-
HC_SEL
Y

10 
 0=Cool  1=Heat 2=Auto


11
Heat Reclaim Select
Yes/No10
-
RECL_SEL
Y

12

13
Alarm State
Normal6
-
ALM
N

14
Current Alarm 1
nnnnn
-
alarm_1
N

15
Current Alarm 2
nnnnn
-
alarm_2
N

16
Current Alarm 3
nnnnn
-
alarm_3
N

17
Current Alarm 4
nnnnn
-
alarm_4
N

18
Current Alarm 5
nnnnn
-
alarm_5
N

19

20
Percent Total Capacity
nnn
%
CAP_T
N

21
Active Demand Limit Val
nnn7
%
DEM_LIM
Y

22
Lag Capacity Limit Value
nnn
%
LAG_LIM
N

22
Actual Chiller Current
nnn12
amps
TOT_CURR
N

23
Chiller Current Limit
nnn
amps
CURR_LIM
Y

24
Current Setpoint
±nnn.n
°F
SP
N

25
Setpoint Occupied?
Yes/No
-
SP_OCC
Y

26
Setpoint Control 
Setpt 1/Setpt 2/Ice_sp/4-20mA/Auto
-
sp_ctrl
N

27
Control Point
±nnn.n8
°F
CTRL_PNT
Y

28
Controlled Water Temp
±nnn.n
°F
CTRL_WT
N

29
External Temperature
±nnn.n
°F
OAT
N

30

31
Emergency Stop
Enable/Emstop9
-
EMSTOP
Y

32

1 : Unit control type in effect as described in section 4.7.

2 : Unit current status as described in section 4.7.

running/Off/Stopping/Delay/Tripout/Ready/Override/Defrost/Test/Run Test.

STATUS sio variable provides following values corresponding to strings above:


“Off”  
> STATUS = 0


“Running” 
> STATUS = 1


“Stopping” 
> STATUS = 2


“Delay” 
> STATUS = 3


“Tripout” 
> STATUS = 4


“Ready” 
> STATUS = 5


“Override” 
> STATUS = 6


“Defrost” 
> STATUS = 7


“Run Test” 
> STATUS = 8


“Test” 
> STATUS = 9

3 : Allows to Start/Stop the chiller only when unit under CCN control type. Forced value is displayed but unused when the unit is not under CCN control.

4 : Occupied state. This item can be forced. If the unit is in CCN mode, the forced value shall be used instead of the real occupancy state. If the unit is not in CCN mode the forced value shall be unused and the regular time schedule shall be used. Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control. 

5: Heat/cool select. This item can be forced. If the unit is in CCN mode, the forced value shall be used whatever the status of the remote heat/cool contacts. If the unit is not in CCN mode the forced value shall be unused.  Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control.

6 : Alarm status

Normal (no alarm)

Partial (alarm but unit is not down)

Shutdown (unit is down)

7: Active Demand Limit Value. This item can be forced. If the unit is in CCN mode, the forced value shall be used whatever the status of the external limit switch contact and whatever the value of the demand limit switch setpoint. If the unit is not in CCN mode the forced value shall be unused. Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control.

8: Control Point. This item can be forced. If the unit is in CCN mode, the forced value shall be used instead of the real control point calculation. If the unit is not in CCN mode the forced value shall be unused. Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control.

9 : Active all the time even if the unit is not in CCN control type.

10: Heat Reclaim Select. This item can be forced. If the unit is in CCN mode, the forced value shall be used whatever the status of the remote reclaim switch. Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control.

11 : Unit current heat cool status.

Heat/Cool/Standby.

HEATCOOL sio variable provides following values corresponding to strings above:


“Cool”  
> STATUS = 0


“HEAT” 
> STATUS = 1


“Standby” 
> STATUS = 2

12: Active Total Compressor Current Demand Limit Value. This item can be forced. If the unit is in CCN mode, the forced value shall be used whatever the status of the external limit switch contact and whatever the value of the demand limit switch setpoint. If the unit is not in CCN mode the forced value shall be unused. Forced value and force code shall appear in the GENUNIT Points Display table only if the unit is under CCN control.

DISPLAY SCREEN 

TABLE NAME: CIRCA_AN      PIC TABLE TYPE : 11H, instance 2

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
CIRCUIT A ANALOG VALUES

2

3
Percent Total Capacity
0 - 100
%
CAPA_T
N

4
Discharge Pressure
nnn.n
psi
DP_A
N

5
Suction Pressure
nnn.n
psi
SP_A
N

6
Economizer Pressure
nnn.n
psi
ECON_P_A
N

6
Oil Pressure
nnn.n
psi
OP_A
N

7
Oil Pressure Difference
nnn.n
psi
DOP_A
N

8
Motor Current 
nnn.n
AMPS
CURREN_A
N

10
Motor Temperature  
nnnn
°F
CP_TMP_A
N

11
Discharge  Gas Temp
nnnn
°F
DGT_A
N

11
Economizer Gas Temp
nnnn
°F
ECO_TP_A
N

14
Saturated Condensing Tmp
±nnn.n
°F
SCT_A
N

15
Saturated Suction Temp
±nnn.n
°F
SST_A
N

16
Compressor Suction Temp
±nnn.n
°F
SUCT_T_A
N

18
EXV Position
0 - 100
%
EXV_A
N

19
Head Press Actuator Pos
0 - 100
%
hd_pos_a
N

DISPLAY SCREEN 

TABLE NAME: CIRCA_D      PIC TABLE TYPE : 11H, instance 3

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCIBLE
1
CIRCUIT A DISCRETE

2

3
Compressor  Output
On/Off
-
COMP_A
N

4
Slide Valve 1 Output
On/Off
-
SLID_1_A
N

5
Slide Valve 2 Output
On/Off
-
SLID_2_A
N

6
Oil Heater Output
On/Off
-
OIL_HT_A
N

7
Oil Solenoid Output
On/Off
-
OIL_SL_A
N

9
Oil Level Input
Low/High
-
OIL_L_A
N

10
DGT Cooling Solenoid
On/Off
-
GASCOOLA
N

11

12
FANS OUTPUT

13
Fan Output DO # 1
On/Off
-
fan_a1
N

14
Fan Output DO # 2
On/Off
-
fan_a2
N

15
Fan Output DO # 3
On/Off
-
fan_a3
N

16
Fan Output DO # 4
On/Off
-
fan_a4
N

17
Fan Output DO # 5
On/Off
-
fan_a5
N

18
Fan Output DO # 6
On/Off
-
fan_a6
N

19
Fan Output DO # 7
On/Off
-
fan_a7
N

20
Fan Output DO # 8
On/Off
-
fan_a8
N

21
Fan Staging Number
0 - 10
-
FAN_ST_A
N

22

23
FREE COOLING OUT

24
Refrigerant Pump Out
On/Off
-
FR_PMP_A
N

25
Circuit Heater  Output 
On/Off
-
FR_HEATA
N

26

27
MISCELLANOUS 

28
Ball Valve Position
Clos/Open
-
ISO_REFA
N

29
Ball Valve Closing Out
On/Off
-
ISO_CL_A
N

30
Ball Valve Opening Out        
On/Off
-
ISO_OP_A
N

31
4 Way Refrigerant Valve
On/Off
-
RV_A
N

DISPLAY SCREEN

TABLE NAME: CIRCB_AN      PIC TABLE TYPE : 11H, instance 4

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
CIRCUIT B ANALOG VALUES

2

3
Percent Total Capacity
0 - 100
%
CAPB_T
N

4
Discharge Pressure
nnn.n
psi
DP_B
N

5
Suction Pressure
nnn.n
psi
SP_B
N

6
Economizer Pressure
nnn.n
psi
ECON_P_B
N

6
Oil Pressure
nnn.n
psi
OP_B
N

7
Oil Pressure Difference
nnn.n
psi
DOP_B
N

8
Motor Current 
nnn.n
AMPS
CURREN_B
N

10
Motor Temperature  
nnnn
°F
CP_TMP_B
N

11
Discharge  Gas Temp
nnnn
°F
DGT_B
N

11
Economizer Gas Temp
nnnn
°F
ECO_TP_B
N

14
Saturated Condensing Tmp
±nnn.n
°F
SCT_B
N

15
Saturated Suction Temp
±nnn.n
°F
SST_B
N

16
Compressor Suction Temp
±nnn.n
°F
SUCT_T_B
N

18
EXV Position
0 - 100
%
EXV_B
N

19
Head Press Actuator Pos
0 - 100
%
hd_pos_b
N

DISPLAY SCREEN  

TABLE NAME: CIRCB_D      PIC TABLE TYPE : 11H, instance 5

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
CIRCUIT B DISCRETE

2

3
Compressor  Output
On/Off
-
COMP_B
N

4
Slide Valve 1 Output
On/Off
-
SLID_1_B
N

5
Slide Valve 2 Output
On/Off
-
SLID_2_B
N

6
Oil Heater Output
On/Off
-
OIL_HT_B
N

7
Oil Solenoid Output
On/Off
-
OIL_SL_B
N

9
Oil Level Input
Low/High
-
OIL_L_B
N

10
DGT Cooling Solenoid
On/Off
-
GASCOOLB
N

11

12
FANS OUTPUT

13
Fan Output DO # 1
On/Off
-
fan_b1
N

14
Fan Output DO # 2
On/Off
-
fan_b2
N

15
Fan Output DO # 3
On/Off
-
fan_b3
N

16
Fan Output DO # 4
On/Off
-
fan_b4
N

17
Fan Output DO # 5
On/Off
-
fan_b5
N

18
Fan Output DO # 6
On/Off
-
fan_b6
N

19
Fan Output DO # 7
On/Off
-
fan_b7
N

20
Fan Output DO # 8
On/Off
-
fan_b8
N

21
Fan Staging Number
0 - 10
-
FAN_ST_B
N

22

23
FREE COOLING OUT

24
Refrigerant Pump Out
On/Off
-
FR_PMP_B
N

25
Circuit Heater  Output 
On/Off
-
FR_HEATB
N

26

27
MISCELLANOUS 

28
Ball Valve Position
Clos/Openf
-
ISO_REFB
N

29
Ball Valve Closing Out
On/Off
-
ISO_CL_B
N

30
Ball Valve Opening Out        
On/Off
-
ISO_OP_B
N

31
4 Way Refrigerant Valve
On/Off
-
RV_B
N

DISPLAY SCREEN 

TABLE NAME: CIRCC_AN      PIC TABLE TYPE : 11H, instance 6

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
CIRCUIT C ANALOG VALUES

2

3
Percent Total Capacity
0 - 100
%
CAPC_T
N

4
Discharge Pressure
nnn.n
psi
DP_C
N

5
Suction Pressure
nnn.n
psi
SP_C
N

6
Economizer Pressure
nnn.n
psi
ECON_P_C
N

6
Oil Pressure
nnn.n
psi
OP_C
N

7
Oil Pressure Difference
nnn.n
psi
DOP_C
N

8
Motor Current 
nnn.n
AMPS
CURREN_C
N

10
Motor Temperature  
nnnn
°F
CP_TMP_C
N

11
Discharge  Gas Temp
nnnn
°F
DGT_C
N

11
Economizer Gas Temp
nnnn
°F
ECO_TP_C
N

14
Saturated Condensing Tmp
±nnn.n
°F
SCT_C
N

15
Saturated Suction Temp
±nnn.n
°F
SST_C
N

16
Compressor Suction Temp
±nnn.n
°F
SUCT_T_C
N

18
EXV Position
0 - 100
%
EXV_C
N

19
Head Press Actuator Pos
0 - 100
%
hd_pos_c
N

DISPLAY SCREEN 

TABLE NAME: CIRCC_D      PIC TABLE TYPE : 11H, instance 7

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
CIRCUIT C DISCRETE

2

3
Compressor  Output
On/Off
-
COMP_C
N

4
Slide Valve 1 Output
On/Off
-
SLID_1_C
N

5
Slide Valve 2 Output
On/Off
-
SLID_2_C
N

6
Oil Heater Output
On/Off
-
OIL_HT_C
N

7
Oil Solenoid Output
On/Off
-
OIL_SL_C
N

9
Oil Level Input
Low/High
-
OIL_L_C
N

10
DGT Cooling Solenoid
On/Off
-
GASCOOLC
N

11

12
FANS OUTPUT

13
Fan Output DO # 1
On/Off
-
fan_c1
N

14
Fan Output DO # 2
On/Off
-
fan_c2
N

15
Fan Output DO # 3
On/Off
-
fan_c3
N

16
Fan Output DO # 4
On/Off
-
fan_c4
N

17
Fan Output DO # 5
On/Off
-
fan_c5
N

18
Fan Output DO # 6
On/Off
-
fan_c6
N

19
Fan Output DO # 7
On/Off
-
fan_c7
N

20
Fan Output DO # 8
On/Off
-
fan_c8
N

21
Fan Staging Number
0 - 10
-
FAN_ST_C
N

22

23
FREE COOLING OUT

24
Refrigerant Pump Out
On/Off
-
FR_PMP_C
N

25
Circuit Heater  Output 
On/Off
-
FR_HEATC
N

26

27
MISCELLANOUS 

28
Ball Valve Position
Clos/Openf
-
ISO_REFC
N

29
Ball Valve Closing Out
On/Off
-
ISO_CL_C
N

30
Ball Valve Opening Out        
On/Off
-
ISO_OP_C
N

31
4 Way Refrigerant Valve
On/Off
-
RV_C
N

DISPLAY SCREEN
TABLE NAME: STATEGEN     PIC TABLE TYPE : 11H, instance 8

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
UNIT DISCRETE IN

2
On/Off – Remote Switch
Open/Close
-
ONOFF_SW
N

3
Remote Heat/Cool Switch
Open/Close
-
HC_SW
N

4
Current Control
Off, On Cool, On Heat, On Auto
on_ctrl
N

5
Remote Reclaim Switch
Open/Close
-
RECL_SW
N

6
Remote Setpoint Switch
Open/Close
-
SETP_SW
N

7
Limit Swicth 1 Status
Open/Close
-
LIM_SW1
N

8
Limit Swicth 2 Status
Open/Close
-
LIM_SW2
N

9
Occupied Override Switch
Open/Close
-
OCC_OVSW
N

10
Ice Done Storage Switch
Open/Close
-
ICE_SW
N

11
Cooler Flow Switch 
Open/Close
-
FLOW_SW
N

12
Cooler Pump Run Status
On/Off
-
CPUMPDEF
N

13
Condenser Flow Status
On/Off
-
CONDFLOW
N

14
Remote Interlock Status
Open/Close
-
REM_LOCK
N

15
Electrical Box Interlock
Open/Close
-
ELEC_BOX
N

16

17
UNIT DISCRETE OUT

18
Cooler Flow Setpoint Out
On/Off
-
SET_FLOW
Y

19
Electrical Heat Stage
0-4
-
EHS_STEP
N

20
Cooler Pump #1 Command
On/Off1
-
CPUMP_1
Y

21
Cooler Pump #2 Command
On/Off1
-
CPUMP_2
Y

22
Rotate Cooler Pumps ?
Yes/No1
-
ROTCPUMP
Y

23
Condenser Pump #1 Out
On/Off2
-
HPUMP_1
Y

24
Condenser Pump #2 Out
On/Off2
-
HPUMP_2
Y

25
Rotate Condenser Pumps ?
Yes/No1
-
ROTHPUMP
Y

26
Cooler Heater Command
On/Off
-
COOLHEAT
N

27
Shutdown Indicator State
On/Off
-
SHUTDOWN
N

28
Alarm Relay Status
On/Off
-
ALARMOUT
N

29
Alert Relay Status
On/Off
-
ALERT
N

30
Ready or Running Status
On/Off
-
READY
N

31
Running Status
On/Off
-
RUNNING
N

32

33
UNIT ANALOG

34
Cooler Entering Fluid
±nnn.n
°F
COOL_EWT
N

35
Cooler Leaving Fluid
±nnn.n
°F
COOL_LWT
N

36
Condenser Entering Fluid
±nnn.n
°F
COND_EWT
N

38
Condenser Leaving Fluid
±nnn.n
°F
COND_LWT
N

39
Cooler Heater  Temp
±nnn.n
°F
TH_HEATER
N

40
Optional Space Temp 
±nnn.n
°F
SPACETMP
N

41
CHWS  Temperature
±nnn.n
°F
CHWSTEMP
N

42
Reset /Setpoint 4-20mA In
±nn.n
ma
SP_RESET
N

43
Limit  4-20mA Signal 
±nn.n
ma
LIM_ANAL
N

44
Chiller Capacity Signal
±nn.n
volts
CAPT_010
N

1: Cooler pump control. This item can be forced On or Off if the unit is in CCN mode and if the CHIL_S_S is disabled. If the unit is not in CCN mode the forced value shall be unused and the regular calculation shall be used. Forced value and force code shall appear in the OPTIONS Points Display table only if the unit is under CCN control and if CHIL_S_S is disabled.  

If CPUMP#1 is forced, no force shall be allowed on CPUMP_2 and vice versa.

2: Condenser pump control. This item can be forced On but not Off. If the unit is in CCN mode, the forced value shall be used instead of regular pump control point. If the unit is not in CCN mode the forced value shall be unused and the regular calculation shall be used. Forced value and force code shall appear in the OPTIONS Points Display table only if the unit is under CCN control.

If HPUMP#1 is forced, no force shall be allowed on HPUMP_2 and vice versa.

DISPLAY SCREEN
TABLE NAME: RECLAIM      PIC TABLE TYPE : 11H, instance 9

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE
1
Heat Reclaim Select
Yes/no

RECL_SEL
N

2
Reclaim Condenser Pump
On/Off
-
HPUMP_1
N

3
Reclaim Condenser Flow
On/Off
-
CONDFLOW
N

4
Reclaim Condenser Heater
On/Off
-
cond_htr
N

5
Reclaim Entering Fluid
±nnn.n
°F
HR_EWT
N

6
Reclaim Leaving Fluid
±nnn.n
°F
HR_LWT
N

7
Reclaim Fluid Setpoint
±nnn.n
°F
RSP
Y

8
Reclaim Valve Position
±nnn.n
%
hr_v_pos
N

9
HEAT RECLAIM CIRCUIT A

-

N

10
Reclaim Status Circuit A
n

hrstat_a
N

11
Pumpdown Pressure Cir A
±nnn.n
psi
PD_P_A
N

12
Sub Condenser Temp Cir A
±nnn.n
°F
hr_subta
N

13
Pumdown Saturated Tmp A
±nnn.n
°F
hr_sat_a
N

14
Subcooling Temperarure A
±nnn.n
^F
hr_subca
N

15
Air Cond Entering Valv A
On/Off
-
hr_ea_a
N

16
Water Cond Enter Valve A
On/Off
-
hr_ew_a
N

17
Air Cond Leaving Valve A
On/Off
-
hr_la_a
N

18
Water Cond Leaving Val A
On/Off
-
hr_lw_a
N

19
HEAT RECLAIM CIRCUIT B

-

N

20
Reclaim Status Circuit B
n

hrstat_b
N

21
Pumpdown Pressure Cir B
±nnn.n
psi
PD_P_B
N

22
Sub Condenser Temp Cir B
±nnn.n
°F
hr_subtb
N

23
Pumdown Saturated Tmp B
±nnn.n
°F
hr_sat_b
N

24
Subcooling Temperarure B
±nnn.n
^F
hr_subcb
N

25
Air Cond Entering Valv B
On/Off
-
hr_ea_b
N

26
Water Cond Enter Valve B
On/Off
-
hr_ew_b
N

27
Air Cond Leaving Valve B
On/Off
-
hr_la_b
N

28
Water Cond Leaving Val B
On/Off
-
hr_lw_b
N

TABLE NAME: MODES      PIC TABLE TYPE : 11H, instance 10

DESCRIPTION
STATUS
UNITS
 POINTS
  FORCEABLE

Startup Delay in Effect
Yes/No
-
Mode_01
N


Second Setpoint in Use
Yes/No
-
Mode_02
N


Reset in Effect
Yes/No
-
Mode_03
N


Demand Limit Active
Yes/No
-
Mode_04
N


Ramp Loading Active
Yes/No
-
Mode_05
N


Cooler Heater Active
Yes/No
-
Mode_06
N


Cooler Pumps Rotation
Yes/No
-
Mode_07
N

 
Pump Periodic Start
Yes/No
-
Mode_08
N


Night Low Noise Active
Yes/No
-
Mode_09
N


System Manager Active
Yes/No
-
Mode_10
N


Master Slave Active
Yes/No
-
Mode_11
N


Auto Changeover Active
Yes/No
-
Mode_12
N


Free Cooling Active
Yes/No
-
Mode_13
N


Reclaim Active
Yes/No
-
Mode_14
N


Electric Heat Active
Yes/No
-
Mode_15
N
Heating Low EWT Lockout
Yes/No
-
Mode_16
N


Condenser Pumps Rotation
Yes/No
-
Mode_17
N


Ice Mode in Effect 
Yes/No
-
Mode_18
N


Defrost Active On Cir A
Yes/No
-
Mode_19
N


Defrost Active On Cir B
Yes/No
-
Mode_20
N


Low Suction Circuit A
Yes/No
-
Mode_21
N


Low  Suction Circuit B
Yes/No
-
Mode_22
N

Low  Suction Circuit C
Yes/No
-
Mode_23
N


High DGT Circuit A
Yes/No
-
Mode_24
N


High DGT Circuit B
Yes/No
-
Mode_25
N


High DGT Circuit C
Yes/No
-
Mode_26
N


High Pres Override Cir A
Yes/No
-
Mode_27
N


High Pres Override Cir B
Yes/No
-
Mode_28
N


High Pres Override Cir C
Yes/No
-
Mode_29
N


Low Superheat Circuit A
Yes/No
-
Mode_30
N


Low Superheat Circuit B
Yes/No
-
Mode_31
N


Low Superheat Circuit C
Yes/No
-
Mode_32
N

TABLE NAME: STRTHOUR         PIC TABLE TYPE : 11, instance 11

DESCRIPTION
STATUS
UNITS      
POINT
1
Machine Operating Hours
nnnnn
hours
HR_MACH

2
Machine Starts Number
nnnnn
 -
st_mach

3
Compressor A Hours
nnnnn
hours
HR_CP_A

4
Compressor A Starts
nnnnn
 -
st_cp_a

5
Compressor B Hours
nnnnn
hours
HR_CP_B

6
Compressor B Starts
nnnnn
 -
st_cp_b

7
Compressor C Hours
nnnnn
hours
HR_CP_C

8
Compressor C Starts
nnnnn
 -
st_cp_c

9

10
WATER PUMPS

11
Cooler Pump #1 Hours
nnnnn
hours
hr_cpum1

12
Cooler Pump #2 Hours
nnnnn
hours
hr_cpum2

13
Condenser Pump #1 Hours
nnnnn
hours
hr_hpum1

14
Condenser Pump #2 Hours
nnnnn
hours
hr_hpum2

15

16
DEFROST CYCLES

17
 Circuit A Defrost Numer
nnnnn
  -
nb_def_a

18
 Circuit B Defrost Number 
nnnnn
  -
nb_def_b

Note: Table for display only.

MAINTENANCE SCREEN
TABLE NAME: STRTHOUR         PIC TABLE TYPE : 11, instance 12

DESCRIPTION
STATUS
UNITS      
POINT
1
FAN Operating Hours

2
Circuit A Fan #1 Hours
nnnnn
hours
hr_fana1

3
Circuit A Fan #2 Hours
nnnnn
hours
hr_fana2

4
Circuit A Fan #3 Hours
nnnnn
hours
hr_fana3

5
Circuit A Fan #4 Hours
nnnnn
hours
hr_fana4

6
Circuit A Fan #5 Hours
nnnnn
hours
hr_fana5

7
Circuit A Fan #6 Hours
nnnnn
hours
hr_fana6

8
Circuit A Fan #7 Hours
nnnnn
hours
hr_fana7

9
Circuit A Fan #8 Hours
nnnnn
hours
hr_fana8

10
Circuit A Fan #9 Hours
nnnnn
hours
hr_fana9

11
Circuit A Fan #10 Hours
nnnnn
hours
hrfana10

12
Circuit B Fan #1 Hours
nnnnn
hours
hr_fanb1

13
Circuit B Fan #2 Hours
nnnnn
hours
hr_fanb2

14
Circuit B Fan #3 Hours
nnnnn
hours
hr_fanb3

15
Circuit B Fan #4 Hours
nnnnn
hours
hr_fanb4

16
Circuit B Fan #5 Hours
nnnnn
hours
hr_fanb5

17
Circuit B Fan #6 Hours
nnnnn
hours
hr_fanb6

18
Circuit B Fan #7 Hours
nnnnn
hours
hr_fanb7

19
Circuit B Fan #8 Hours
nnnnn
hours
hr_fanb8

20
Circuit B Fan #9 Hours
nnnnn
hours
hr_fanb9

21
Circuit B Fan #10 Hours
nnnnn
hours
hrfanb10

22
Circuit C Fan #1 Hours
nnnnn
hours
hr_fanc1

23
Circuit C Fan #2 Hours
nnnnn
hours
hr_fanc2

24
Circuit C Fan #3 Hours
nnnnn
hours
hr_fanc3

25
Circuit C Fan #4 Hours
nnnnn
hours
hr_fanc4

25
Circuit C Fan #5 Hours
nnnnn
hours
hr_fanc5

27
Circuit C Fan #6 Hours
nnnnn
hours
hr_fanc6

28
Circuit C Fan #7 Hours
nnnnn
hours
hr_fanc7

29
Circuit C Fan #8 Hours
nnnnn
hours
hr_fanc8

30
Circuit C Fan #9 Hours
nnnnn
hours
hr_fanc9

31
Circuit C Fan #10 Hours
nnnnn
hours
hrfanc10

Note: Table for display only.

CONFIGURATION SCREEN
TABLE NAME: USER      PIC TABLE TYPE : 10H, instance 2

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Circuit Loading Sequence
0/1/2
0
-
lead_cir

2
   0=Auto,      1=A Lead

3
   2=B Lead,  3 =C Lead

4
Staged Loading Sequence
No/Yes
No
-
seq_typ

5
Ramp Loading Select
No/Yes
No
-
ramp_sel

6
Unit Off to On Delay
1 to 15
1
min
off_on_d

7
Condenser Pumps Sequence
0/1/2/3/4
0
-
hpumpseq

8
Cooler Pumps Sequence
0/1/2/3/4
0
-
cpumpseq

9
    0 = No Pump

10 
    1 = One Pump Only

11
    2 = Two Pumps Auto

12
    3 = Pump#1 Manual

13
    4 = Pump#2 Manual

14
Pump Auto Rotation Delay
24 to 3000
48
hours
pump_del

15
Pump Sticking Protection
No/Yes
No
-
pump_per

16
Stop Pump During Standby
No/Yes
No
-
pump_sby

17
Flow Checked if CPump Off
No/Yes3
Yes
-
pump_loc

18
Auto Changeover Select
No/Yes
No
-
auto_sel

19
Cooling Reset Select
0 to 41
0
-
cr_sel

20
Heating Reset Select
0 to 31
0
-
hr_sel

21
   1 =OAT,    0=None 

22
   2=Delta T, 4=Space Temp

23
   3=4-20mA Control 

24
Demand Limit Type Select
0 to 22
0
-
lim_sel

25
    0 = None

26
    1 = Switch Control

27
    2 = 4-20mA Control

28
mA For 100% Demand Limit
 0 to 20
0
ma
lim_mx

29
mA For 0% Demand Limit
0 to 20
10
ma
lim_ze

30
Current Limit Select
No/Yes
No
-
curr_sel

31
Current Limit  at 100%
0 to 2000
2000
amps
curr_ful

32
Heating OAT Threshold
-4 to 32
5
°F
heat_th

33
Free Cooling OAT Limit
-4 to 37.4
32
°F
free_oat

34
Elec Stage OAT Threshold
23 to 70
41
°F
ehs_th

35
1 Elec Stage for Backup
No/Yes
No
-
ehs_back

36
Electrical Pulldown Time
0 to 60
0
minutes
ehs_pull

37
Quick EHS for Defrost
No/Yes
No
-
ehs_defr

38
Night Control

39
Start Hour
00:00 to 24:00
00:00
-
nh_start

40
End Hour
00:00 to 24:00
00:00
-
nh_end

41
Capacity Limit
0 to 100
100
%
nh_limit

42
Ice Mode Enable
No/Yes
No
-
ice_cnfg

43
Reverse Alarms Relay 
No/Yes4
no
-
al_rever

44
Pass For All User Config
No/Yes
No
-
all_pass

1.
If customer has selected the setpoint based on 4-20mA input signal through Comforlink , then 4-20 mA reset fuction shall be ignored. 

Configuration #3 (4-20mA Control) and #4 (Space Temp) shall require an Energy Management Module

2.
Configuration #2 (4-20mA Control) shall require an Energy Management Module.

Configuration #1 Switch Demand limit provides 3 step demand limit if an Energy Management Module is present. Otherwise, only one step is allowed.

3. This configuration is needed when customer commands the primary pump to prevent cooler from freezing in winter.  Customer pump will make cooler flow switch to closed while the controls stops the cooler pump. Then the controls may generate an alarm. If this decision is active, the cooler flow switch is not checked when the cooler pump is stopped.   

4.  This configuration when enable will de-energized the alarm & alert relay when alarms are present and energize its when no alarm is present.

CONFIGURATION SCREEN
TABLE NAME: MST_SLV          PIC TABLE TYPE : 10H, instance 3

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
MASTER/SLAVE CONTROL

2

3
Master/Slave Select:
0/1/2
0
-
ms_sel

4
   0 = Disable

5
   1 = Master

6
   2 = Slave

7
Master Control Type:
1/2/3
1
-
ms_ctrl

8
   1 = Local Control

9
   2 = Remote Control

10
   3 = CCN Control

11
Slave Address
1 to 236
2
-
slv_addr

12
Lag Start Timer
2 to 30
10
min
lstr_tim

13
Lead/Lag Balance
Yes/No
No
-
ll_bal

14
Lead/Lag Balance Delta
40 to 400
168
hours
ll_bal_d

15
Lag Unit Pump Control
0/1
0
-
lag_pump

16
   0 = Stop if Unit Stops

17
   1 = Run if Unit Stops

18
Lead Pulldown Time
0 to 60
0
minutes
lead_pul

19
Chiller in series 
Yes/No
No
-
ll_serie

CONFIGURATION SCREEN
TABLE NAME: DISPCONF    PIC TABLE TYPE : 10H, instance 5


DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Metric Display on STDU 
Yes/no 
No

DISPUNIT

2
Language Selection
0-4 
0

LANGUAGE
3
   0 = ENGLISH

4
   1 = ESPANOL

5  
   2 = FRANCAIS

6
   3 = PORTUGUES
7
   4 = ENGLISH2 1
1 The fifth language is originally  English and shall be tranlsated to the country language when needed through Montluel CCN Translator.  The text descriptions in this table can be translated through CCN translator. However it is recommended to not translate items from 3 to 6. 

MAINTENANCE SCREEN
TABLE NAME: LOADFACT         PIC TABLE TYPE : 12H, instance 1

DESCRIPTION
STATUS
UNITS 
POINT
1 
CAPACITY CONTROL

2 
Average Ctrl Water Temp
±nnn.n
°F
ctrl_avg

3 
Differential Water Temp
±nnn.n
°F
diff_wt

4 
Water Delta T
±nnn.n
^F
delta_t

5 
Control Point
±nnn.n
°F
CTRL_PNT

6 
Reset Amount
±nnn.n
^F
reset

7 
Controlled Temp Error
±nnn.n
^F
tp_error

8 
Actual Capacity
nnn
%
cap_t

9 
Actual Capacity Limit
nnn
%
cap_lim

10 
Actual Chiller Current
nnnn
amps
TOT_CURR

11 
Chiller Current Limit
nnnn
 amps
CURR_LIM

12 
Current At 30% Load  A
nnnn
amps
cur_30_a

13 
Current At 30% Load B
nnnn
amps
cur_30_b

14 
Current At 30% Load  C
nnnn
amps
cur_30_c

15 
Current At 100% Load  A
nnnn
amps
cur100_a

16 
Current At 100% Load  B
nnnn
amps
cur100_b

17 
Current At 100% Load  C
nnnn
amps
cur100_c

18 
Current Z Multiplier Val
±n.n
-
zm

19 
Load/Unload Factor
±nnn.n
-
smz

20 
Active Capacity Override
nn
-
over_cap

21
EHS CAPACITY CONTROL

22
EHS Ctrl Override
nn
-
over_ehs

23
Requested Electric Stage 
nn
-
eh_stage

24
Electrical Pulldown?
True/False
-
ehspulld

TABLE NAME: FANCTRL         PIC TABLE TYPE : 12H, instance 2

DESCRIPTION



STATUS


UNITS

POINT
1
Cir A SCT Control Point 
±nnn.n
°F
sct_sp_a

2
Cir A SCT Candidate
±nnn.n
°F
sct_fu_a

3
Cir A Fan Cycle Counter
±nnn.n

fancyc_a

4
Cir A Optimal Fan Count
±nnn.n

fancop_a

5
Cir B SCT Control Point 
±nnn.n
°F
sct_sp_b

6
Cir B SCT Candidate
±nnn.n
°F
sct_fu_b

7
Cir B Fan Cycle Counter
±nnn.n

fancyc_b

8
Cir B Optimal Fan Count
±nnn.n

fancop_b

9
Cir C SCT Control Point 
±nnn.n
°F
sct_sp_c

10
Cir C SCT Candidate
±nnn.n
°F
sct_fu_c

11
Cir C Fan Cycle Counter
±nnn.n

fancyc_c

12
Cir C Optimal Fan Count
±nnn.n

fancop_c

MAINTENANCE SCREEN
Note: Table for display only.

TABLE NAME: EXV_CTRL         PIC TABLE TYPE : 12H, instance 9

DESCRIPTION
STATUS
UNITS 
POINT
1

EXV CONTROL

2
EXV Position Circuit A
nnn.n
%
EXV_A

3
Discharge Superheat  A
nnn.n
%
DSH_A

4
Suction Superheat  A
nn.n
^F
SH_A

5
Suction SH Control Pt  A
nn.n
^F
sh_sp_a

6
Cooler Exchange DT Cir A
nn.n
^F
pinch_a

7
Cooler Pinch Ctl Point A
nn.n
^F
pinch_spa

8
EXV Override Circuit A
nn
-
ov_exv_a

9
EXV Position Circuit B
nnn.n
%
EXV_B

10
Discharge Superheat  B
nnn.n
%
DSH_B

11
Suction Superheat  B
nn.n
^F
SH_B

12
Suction SH Control Pt  B
nn.n
^F
sh_sp_b

13
Cooler Exchange DT Cir B
nn.n
^F
pinch_b

14
Cooler Pinch Ctl Point B
nn.n
^F
pinch_spb

15
EXV Override Circuit B
nn
-
ov_exv_b

16
EXV Position Circuit C
nnn.n
%
EXV_C

17
Discharge Superheat  C
nnn.n
%
DSH_C

18
Suction Superheat  C
nn.n
^F
SH_C

19
Suction SH Control Pt  C
nn.n
^F
sh_sp_c

20
Cooler Exchange DT Cir C
nn.n
^F
pinch_c

21
Cooler Pinch Ctl Point C
nn.n
^F
pinch_spc

22
EXV Override Circuit C
nn
-
ov_exv_c

23

24
ECONOMIZER CONTROL

25
Economizer Position A
nnn.n
%
EXV_EC_A

26
Economizer Superheat  A
nn.n
^F
eco_sha

27
Economizer SH Setpoint  A
nn.n
^F
ecsh_spa

28
EXV Override Circuit A
nn
-
ov_eco_a

29
Economizer Position B
nnn.n
%
EXV_EC_B

30
Economizer Superheat  B
nn.n
^F
eco_shb

31
Economizer SH Setpoint B
nn.n
^F
ecsh_spb

32
EXV Override Circuit B
nn
-
ov_eco_b

33
Economizer Position C
nnn.n
%
EXV_EC_C

34
Economizer Superheat  C
nn.n
^F
eco_shc

35
Economizer SH Setpoint  C
nn.n
^F
ecsh_spc

36
EXV Override Circuit C
nn
-
ov_eco_c

MAINTENANCE SCREEN
TABLE NAME: M_MSTSLV        PIC TABLE TYPE : 12H, instance 3

DESCRIPTION
STATUS
UNITS 
POINT
1 
MASTER/SLAVE CONTROL

2 
Unit is Master or Slave
Disable/Master/Slave
-
mstslv

3  
Master Control Type
Local/Remote/CCN3
-
ms_ctrl

4 
Master/Slave Ctrl Active
True/False
-
ms_activ

5   Lead Unit is the:
Master/Slave
-
lead_sel

6 
Slave Chiller State
0/1/2/3/4/51
-
slv_stat

7 
Slave Chiller Total Cap
0-100
%
slv_capt

8 
Lag Start Delay
1 to 302
minutes
l_strt_d

9 
Lead/Lag Hours Delta
±nnnnn3
hours
ll_hr_d

10 
Lead/Lag Changeover?
Yes/No4
-
ll_chang

11 
Lead Pulldown?
Yes/No4
-
ll_pull

12 
Master/Slave Error
nn
-
ms_error

13   Max Available Capacity ?
True/False5
-
cap_max

1: Slave chiller chilstat value

2: This decision is consistent for Master chiller only. It shall be set by default to 0 for the slave chiller.

3: Always CCN for the slave chiller.

4: This decision is consistent for Master chiller only. It shall be set by default to 'No' for the slave chiller.

5: This item is true when chiller has loaded its total unbroken capacity tonnage.

TABLE NAME: DEFROSTM         PIC TABLE TYPE : 12H, instance 4

DESCRIPTION



STATUS


UNITS      
POINT
 
CIR A DEFROST CONTROL


Exchanger Frost Factor


0-100


%


frost_a


Next Sequence Allowed in

nnn


minutes

def_se_a


Defrost Active?



True/False

-


mode[19]


Defrost Temperature


±nnn.n


°F


DEFRT_A


Defrost Duration



nnn


minutes

defr_dua

 
Fan Sequence Started?



n


-


def_fa_a

 
Override State



nn


-


over_d_a


Mean SST Calculation


±nnn.n


°F


sst_dm_a


Delta: OAT - Mean SST


±nnn.n


^F


delt_a


Reference Delta



±nnn.n


^F


delt_r_a


Delta - Reference Delta


±nnn.n


°F


del_v_a


Frost Integrator Gain


n.n


-


fr_int_a


Defrost Fan Start Cal A


0.00


psi


def_ca_a


Defrost Fan Offset Cal A


0.00


psi


def_of_a


CIR B DEFROST CONTROL


Exchanger Frost Factor


0-100


%


frost_b


Next Sequence Allowed in

nnn


minutes

def_se_b


Defrost Active?



True/False

-


mode[20]


Defrost Temperature


±nnn.n


°F


DEFRT_B


Defrost Duration



nnn


minutes

defr_dub

 
Fan Sequence Started?



n


-


def_fa_b


Override State



nn


-


over_d_b


Mean SST calculation


±nnn.n


°F


sst_dm_b


Delta: OAT - Mean SST


±nnn.n


^F


delt_b


Reference Delta



±nnn.n


^F


delt_r_b


Delta - Reference Delta


±nnn.n


^F


del_v_b


Frost Integrator Gain


n.n


-


fr_int_b


Defrost Fan Start Cal B


0.00


psi


def_ca_b


Defrost Fan Offset Cal B


0.00


psi


def_of_b

Note: Tables for display only. Forcing shall not be supported on this maintenance screen.

TABLE NAME: LAST_POR         PIC TABLE TYPE : 12H, instance 5



DESCRIPTION



STATUS


UNITS      
POINT
1

Power On 1:   day-mon-year

nnnnnn


ddmmyy

date_on1

2

Power On 1:   hour-minute

nnnn


hhmm

time_on1

3

PowerDown 1:day-mon-year

nnnnnn


ddmmyy

date_of1

4

PowerDown 1:hour-minute

nnnn


hhmm

time_of1

5

Power On 2:   day-mon-year

nnnnnn


ddmmyy

date_on2

6

Power On 2:   hour-minute

nnnn


hhmm

time_on2

7

PowerDown 2:day-mon-year

nnnnnn


ddmmyy

date_of2

8

PowerDown 2:hour-minute

nnnn


hhmm

time_of2

9

Power On 3:   day-mon-year

nnnnnn


ddmmyy

date_on3

10
Power On 3:   hour-minute

nnnn


hhmm

time_on3

11

PowerDown 3:day-mon-year

nnnnnn


ddmmyy

date_of3

12
PowerDown 3:hour-minute

nnnn


hhmm

ime_of3

13
Power On 4:   day-mon-year

nnnnnn


ddmmyy

date_on4

14
Power On 4:   hour-minute

nnnn


hhmm

time_on4

15
PowerDown 4:day-mon-year

nnnnnn


ddmmyy

date_of4

16
PowerDown 4:hour-minute

nnnn


hhmm

time_of4

17
Power On 5:   day-mon-year


nnnnnn


ddmmyy

date_on5

18
Power On 5:   hour-minute

nnnn


hhmm

time_on5

19
PowerDown 5:day-mon-year

nnnnnn


ddmmyy

date_of5

20
PowerDown 5:hour-minute

nnnn


hhmm

time_of5

TABLE NAME: PR_LIMIT         PIC TABLE TYPE : 12H, instance 6

DESCRIPTION



STATUS


UNITS


 POINT
Discharge A Temp Average
±nnn.n
°F
sdt_m_a

Discharge A Temp Rate
±nnn.n
^F
sdt_mr_a

Discharge A Gas Limit
±nnn.n
°F
sdtlim_a

Suction A Temp Average
±nnn.n
°F
sst_m_a

Discharge B Temp Average
±nnn.n
°F
sdt_m_b

Discharge B Temp Rate
±nnn.n
^F
sdt_mr_b

Discharge B Gas Limit
±nnn.n
°F
sdtlim_b

Suction B Temp Average
±nnn.n
°F
sst_m_b

Discharge C Temp Average
±nnn.n
°F
sdt_m_c

Discharge C Temp Rate
±nnn.n
^F
sdt_mr_c

Discharge C Gas Limit
±nnn.n
°F
sdtlim_c

Suction C Temp Average
±nnn.n
°F
sst_m_c

Note: Table for display only. Used for Cooling and Heat pump Compressor Envelope

TABLE NAME: BOARD_PN     PIC TABLE TYPE : 12H, instance 7

DESCRIPTION
STATUS
UNITS    
POINT
1
EXV Board  Circuit A  
XXXXXXXX
-
exv_brda

2
EXV Board  Circuit B  
XXXXXXXX
-
exv_brdb

3
EXV Board  Circuit C 
XXXXXXXX
-
exv_brdc

4
AUX Board #1 Part Number
XXXXXXXX
-
aux_brd1

5
AUX Board #2 Part Number
XXXXXXXX
-
aux_brd2

6
AUX Board #3 Part Number
XXXXXXXX
-
aux_brd3

7
AUX Board #4 Part Number
XXXXXXXX
-
aux_brd4

8
AUX Board #5 Part Number
XXXXXXXX
-
aux_brd5

9
EMM NRCP2 Board   
XXXXXXXX
-
emm_nrcp


10
Reclaim NRCP2 Board   
XXXXXXXX
-
rec_nrcp


11
TCPM  Board Comp A 
XXXXXXXX
-
cpa_vers

12
  Must Trip Amps
0 to 600 
amps
  cpa_mtam

13
     S1 Config Switch (8->1)
00000000
0
cpa_s1_m

14

15
TCPM  Board Comp A 
nnnn
-
cpb_vers

16
  Must Trip Amps
0 to 600 
amps
  cpb_mtam

17
     S1 Config Switch (8->1)
00000000
0
cpb_s1_m

18

19
TCPM  Board Comp A 
XXXXXXXX
-
cpc_vers

20
  Must Trip Amps
0 to 600 
amps
  cpc_mtam

21
     S1 Config Switch (8->1)
00000000
0
cpc_s1_m

TABLE NAME: SERMAINT        PIC TABLE TYPE : 12H, instance 8

DESCRIPTION
STATUS
UNITS 
POINT
FORCEABLE
1 
Reset Maintenance Alert
nn
-
S_RESET
Y

2 
  1 to 11: reset individually

3 
  11       : reset all

4 
OPERATION WARNINGS

5 
1 - Refrigerant Charge
Normal/Low
-
charge_m
N

6 
2 - Water Loop Size
Normal/Low
-
wloop_m
N

7 
GENERAL SERVICING DELAYS

8 
3–Cooler Pump 1 (days)
0 to 1000/Alert
-
cpump1_m
N

9 
4–Cooler Pump 2 (days)
0 to 1000/Alert
-
cpump2_m
N

10 
5–Condenser Pump 1(days)
0 to 1000/Alert
-
hpump1_m
N

11 
6–Condenser Pump 2(days)
0 to 1000/Alert
-
hpump2_m
N

12 
7–Water Filter (days)
0 to 1000/Alert
-
wfilte_m
N

13 
8–Cp A Oil Filter (days)
0 to 1000/Alert
-
oilfia_m
N

14 
9–Cp B Oil Filter (days)
0 to 1000/Alert
-
oilfilb_m
N

15 
10– C Oil Filter (days)
0 to 1000/Alert
-
oilfic_m
N

TABLE NAME: CUR_PHAS     PIC TABLE TYPE : 12H, instance 9

DESCRIPTION
STATUS
UNITS    
POINT
1
Current Phase 1 Comp A  
0 to 600 
amps
    cpa_cur1

2
Current Phase 2 Comp A  
0 to 600 
amps
    cpa_cur2

3
Current Phase 3 Comp A  
0 to 600 
amps
    cpa_cur3

4
Current Phase 1 Comp B  
0 to 600 
amps
    cpb_cur1

5
Current Phase 2 Comp B  
0 to 600 
amps
    cpb_cur2

6
Current Phase 3 Comp B  
0 to 600 
amps
    cpb_cur3

7
Current Phase 1 Comp C  
0 to 600 
amps
    cpc_cur1

8
Current Phase 2 Comp C  
0 to 600 
amps
    cpc_cur2

9
Current Phase 3 Comp C  
0 to 600 
amps
    cpc_cur3

SERVICE SCREEN
TABLE NAME: FACTORY1     PIC TABLE TYPE : 13H, instance 1

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Unit  Type (Heat Pump = 2)
1 t o 41
1
 -
unit_typ

2
Unit Capacity 
0 to 1800 6
0
 -
unitsize

3
Power Frequence 60HZ Sel
Yes/No 4
No
 -
freq_60H

4
Power Supply Voltage
200 to 660
Volt
 -
voltage

5
NB Fans on Varifan Cir A
0 to 10 2
0
 -
varfan_a

6
NB Fans on Varifan Cir B
0 to 10 2
0
 -
varfan_b

7
NB Fans on Varifan Cir C
0 to 10 2
0
 -
varfan_c

8
Soft Starter Select
Yes/No
No
 -
softstar

9
Wye Delta Start Select
Yes/No
No
 -
wye_delt

10
Air Cooled Reclaim Sel
Yes/No
No
 -
recl_opt

11
Free Cooling Select
Yes/No
No
 -
freecool

12
Cooler heater select
Yes/No
No
 -
heat_sel

13
Condenser Water Val Sel
Yes/No
No
 -
cond_val

14
Hot Gas Bypass Select
Yes/No
No
 -
hgbp_sel

15
MCHX Exchanger Select
Yes/No
No
 -
mchx_sel

16
Electrical Heat Stages
0 to 4
0
 -
ehs_sel

17
Energy Management Module 
Yes/No3
No
 -
emm_nrcp

18
High Tiers Display Selec
o/Yes5
Yes

highdisp

19
Factory Password
0 to 9999
113
 -
fac_pass

1.
1 = Air cooled
2 =Heat Pump
 3= Water Cooled 
4 =Heat Machine 

2.
Number of fans controlled directly by a variable speed fan actuator using 0-10Vdc signal.  This will let the controls determine the remained discrete fan staging outputs from the total fans on each circuit. 

3.
Used for customer extra functions with the purpose of  energy management  such as occupancy override switch, ice storage, setpoint reset,  demand limit  …


4. 
Used for compressor capacity and fans automatic determination (ref to section configuration description)

5.
No  = Use ComfortLlink display as user interface (factory installed) 


Yes = Use High Tiers Display  as user interface (factory installed)
6.
This items is used for compressors capacity and Must Trip Amps value determination based on the compressor fan arrangement (ref to section configuration description). 


0  =  Compressors and number of fans shall be entered  in FACTORY2 table


nnn = shall math the one in the compressor fan mapping array


150 (example for 30RG 150,  it is easier to remember and to configure the size of the unit  than to do for all


 the compressors). 


This items allows the controls to determine capacity of each compressor and the total number of fans on


 each circuit based on a compressor arrangement array (can be viewed in table FACTORY2 below).  It is


 no more necessary to enter compressor capacity and number of fans on circuit.  

TABLE NAME: FACTORY2      PIC TABLE TYPE : 13H, instance 2

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Compressor A Config
 




2
   Must Trip Amps
0 to 6001 
0

cpa_mtac

3
      S1 Config Switch (8->1)  
000000004 
00000000

cpa_s1_c

4
Compressor B Config
 




5
   Must Trip Amps
0 to 6001 
0

cpb_mtac

6
      S1 Config Switch (8->1)  
000000004 
00000000

cpb_s1_c

7
Compressor C Config
 




8
   Must Trip Amps
0 to 6001 
0

cpc_mtac

9
   S1 Config Switch (8->1) 
000000004 
00000000

cpc_s1_c

10



 -


11
Circuit A Total Fans NB
2 to 102
0
 -
nb_fan_a

12
Circuit B Total Fans NB
2 to 102
0
 -
nb_fan_b

13
Circuit C Total Fans NB
0 to 102
0
 -
nb_fan_c

14



 -


15
EXV A Maximum Steps Numb
0/150003
0
-
exva_max

16
EXV B Maximum Steps Numb
0/150003
0
 -
exvb_max

17
EXV C Maximum Steps Numb
0/150003
0
 -
exvc_max

18
Economizer A Steps Numb
0/150003
0
-
eco_cnfa

19
Economizer B Steps Numb
0/150003
0
 -
eco_cnfb

20
Economizer C Steps Numb
0/150003
0
 -
eco_cnfc

1
Compressor capacity will be automatically determined  if  unit size entered in FACTORY1 table matches


 the one from compressor /fan unit size arrangement table (ref to section configuration description).  

2
Total number of fans including fans controlled  by a variable speed fan.  This value  will be automatically


 determined  if  unit size entered in FACTORY1 table matches  the one from compressor /fan unit size


 arrangement table (ref to section configuration description).  


 If total fans number is higher than 8 then


 Aux board DO # 8 will support 2 fans,  fan #8 and fan #9


 Aux board DO # 7 will support 2 fans,  fan #7 and fan #10 if total fan number is 10

3.
0       = EXV not used 

4.
8 dip-switch configuration (8 7 6 5 4 3 2 1)

TABLE NAME: SERVICE1      PIC TABLE TYPE : 13H, instance 3

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Cooler Fluid Type
1/2/3
1
 -
flui_typ

2
Condenser Fluid Type
1/2
1
 -
cond_typ

3
Entering Fluid Control
Yes/No
No
-
ewt_opt

4
Prop PID Gain Varifan
-20.0 to 20.0
2.0
-
hd_pg

5
Int PID Gain Varifan
-5.0 to 5.0
0.2
-
hd_ig

6
Deri PID Gain Varifan
-20.0 to 20.0
0.4
-
hd_dg

7
EXV A Superheat Setpoint
15 to 44
34.2
^F
sh_sp_a

8
EXV B Superheat Setpoint
15 to 44
34.2
^F
sh_sp_b

9
EXV C Superheat Setpoint
15 to 44
34.2
^F
sh_sp_c

10
Pinch offset circuit A
-3.0 to 3.0
0
^F
pinoff_a

11
Pinch offset circuit B
-3.0 to 3.0
0
^F
pinoff_b

12
Pinch offset circuit C
-3.0 to 3.0
0
^F
pinoff_c

13
EXV MOP Setpoint
40 to 55
55
°F
mop_sp

14
High Pressure Threshold
200 to 264
260
psi
hp_th

15
Cooler Heater Delta Spt
1 to 6
2
^F
heatersp

16
Brine Freeze Setpoint
- 20 to 34
14
°F
lowestsp

17
Auto Start When SM Lost
Enable/Disable
Disable
-
auto_sm

18
Recl Valve Min Position
0 to 50
20
%-
min_3w

19
Recl Valve Max Position
20 to 100
100
%
max_3w

20
Economizer SH Setpoint A
5 to 15
7.2
^F
esh_sp_a

21
Economizer SH Setpoint B
5 to 15
7.2
^F
esh_sp_b

22
Economizer SH Setpoint C
5 to 15
7.2
^F
esh_sp_c

23
User Password
  to 150
  11
-
use_pass

Note: this table shall be downloadable at any time. However, modified value shall not be used by tasks until the unit is in off state . This shall not apply to the Varifan gains that shall be modified at any time and used immediately by the head pressure control tasks even if the unit is in operation.

SERVICE SCREEN
TABLE NAME: CP_UNABL      PIC TABLE TYPE : 13H, instance 4

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1 
TABLE USED FOR DISABLE

2
COMPRESSORS 

3


4

5
Compressor A Disable
No/Yes
No
un_cp_a

6
Compressor B Disable
No/Yes
No
un_cp_b

7
Compressor C Disable
No/Yes
No
un_cp_c

Table used to disabe compressors for maintenance purpose. The capacity control will consider that these compressors (once set to YES) are failed manually (no alarm will appear). 

All Data will be re-initialized to “NO”  at Power on reset on units using high tiers display. For Comforlink display, data shall be saved. 

SERVICE SCREEN
TABLE NAME: UPDTHOUR         PIC TABLE TYPE : 13H, instance 5

DESCRIPTION
STATUS
UNITS      
POINT
1 
TABLE TO BE USED FOR RUN

2
TIMES & STARTS UPDATE IN

3
CASE OF CONTROL RETROFIT

4

5
Machine Operating Hours
nnnnn
hours
hr_mach

6
Machine Starts
nnnnn
 -
st_mach

7
Compressor A Hours
nnnnn
hours
hr_cp_a

8
Compressor A Starts
nnnnn
-
st_cp_a

9
Compressor B Hours
nnnnn
hours
hr_cp_b

10
Compressor B Starts
nnnnn
-
st_cp_b

11
Compressor C Hours
nnnnn
hours
hr_cp_c

12
Compressor C Starts
nnnnn
-
st_cp_c

13
Circuit A Defrost Number
nnnnn
-
nb_def_a

14
Circuit B Defrost Number
nnnnn
-
nb_def_b

Note: this table shall be used for purposes of transplanting the devices on time or starts number in the event of a module hardware failure or software upgrade via downloading. It shall be usable only if all items are still nul. Afterwards, its access shall be denied.

SERVICE SCREEN
TABLE NAME: UPDHRFAN         PIC TABLE TYPE : 13H, instance 6

DESCRIPTION
STATUS
UNITS      
POINT
1 
TABLE TO BE USED FOR RUN

2
TIMES UPDATE IN CASE OF

3
CASE OF CONTROL RETROFIT

4
FAN Operating Hours

5
Circuit A Fan #1 Hours
nnnnn
hours
hr_fana1

6
Circuit A Fan #2 Hours
nnnnn
hours
hr_fana2

7
Circuit A Fan #3 Hours
nnnnn
hours
hr_fana3

8
Circuit A Fan #4 Hours
nnnnn
hours
hr_fana4

9
Circuit A Fan #5 Hours
nnnnn
hours
hr_fana5

10
Circuit A Fan #6 Hours
nnnnn
hours
hr_fana6

11
Circuit A Fan #7 Hours
nnnnn
hours
hr_fana7

12
Circuit A Fan #8 Hours
nnnnn
hours
hr_fana8

13
Circuit A Fan #9 Hours
nnnnn
hours
hr_fana9

14
Circuit A Fan #10 Hours
nnnnn
hours
hrfana10

15
Circuit B Fan #1 Hours
nnnnn
hours
hr_fanb1

16
Circuit B Fan #2 Hours
nnnnn
hours
hr_fanb2

17
Circuit B Fan #3 Hours
nnnnn
hours
hr_fanb3

18
Circuit B Fan #4 Hours
nnnnn
hours
hr_fanb4

19
Circuit B Fan #5 Hours
nnnnn
hours
hr_fanb5

20
Circuit B Fan #6 Hours
nnnnn
hours
hr_fanb6

21
Circuit B Fan #7 Hours
nnnnn
hours
hr_fanb7

22
Circuit B Fan #8 Hours
nnnnn
hours
hr_fanb8

23
Circuit B Fan #9 Hours
nnnnn
hours
hr_fanb9

24
Circuit B Fan #10 Hours
nnnnn
hours
hrfanb10

25
Circuit C Fan #1 Hours
nnnnn
hours
hr_fanc1

26
Circuit C Fan #2 Hours
nnnnn
hours
hr_fanc2

27
Circuit C Fan #3 Hours
nnnnn
hours
hr_fanc3

28
Circuit C Fan #4 Hours
nnnnn
hours
hr_fanc4

29
Circuit C Fan #5 Hours
nnnnn
hours
hr_fanc5

30
Circuit C Fan #6 Hours
nnnnn
hours
hr_fanc6

31
Circuit C Fan #7 Hours
nnnnn
hours
hr_fanc7

32
Circuit C Fan #8 Hours
nnnnn
hours
hr_fanc8

33
Circuit C Fan #9 Hours
nnnnn
hours
hr_fanc9

34
Circuit C Fan #10 Hours
nnnnn
hours
hrfanc10

35
Water Pump #1 Hours
nnnnn
hours
hr_cpum1

36
Water Pump #2 Hours
nnnnn
hours
hr_cpum2

37
Condenser Pump #1 Hours
nnnnn
hours
hr_hpum1

38
Condenser Pump #2 Hours
nnnnn
hours
hr_hpum2

Note: this table shall be used for purposes of transplanting the devices on time in the event of a module hardware failure or software upgrade via downloading. It shall be usable only if all items are still nul. Afterwards, its access shall be denied.

SERVICE SCREEN
TABLE NAME: MAINTCFG      PIC TABLE TYPE : 13H, instance 7

DESCRIPTION
STATUS
DEFAULT
UNITS 
POINT
1
MAINTENANCE CONFIG

2
Servicing Alert
Enable/Disable
Disable
 -
s_alert

3
Refrigerant Charge Ctrl
Enable/Disable
Disable
 -
charge_c

4
Water Loop Control
Enable/Disable
Disable
 -
wloop_c

5
CPump 1 Ctl Delay (days)
0 to 1000
0
 -
cpump1_c

6
CPump 2 Ctl Delay (days)
0 to 1000
0
 -
cpump2_c

7
HPump 1 Ctrl Delay (days) 
0 to 1000
0

hpump1_c

8
HPump 2 Ctrl Delay (days) 
0 to 1000
0

hpump2_c

9
Water Filter Ctrl  (days)
0 to 1000
0
 -
wfilte_c

10
Oil Filter A Ctrl  (days)
0 to 1000
0
 -
oilfia_c

11
Oil Filter B Ctrl  (days)
0 to 1000
0
 -
oilfib_c

12
Oil Filter C Ctrl  (days)
0 to 1000
0
 -
oilfic_c

CONFIGURATION SCREEN
TABLE NAME: BRODEFS      PIC TABLE TYPE : 14H, instance 1
 DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
Activate
0/1/2 1
2
-
ccnbroad

2

3
OAT Broadcast

4
Bus #
0 to 239
0
-
oatbusnm

5
Element #
0 to 239
0
-
oatlocad

6

7
DAYLIGHT SAVING SELECT
Disable/Enable
Disable
-
dayl_sel

8  
ENTERING

9
Month 
1 to 12
3
-
startmon

10
Day of week (1=Monday)
1 to 7
72
-
startdow

11
Week Number of Month 
1 to 5
53
-
startwom

12  
LEAVING

13
Month 
1 to 12
10
-
stopmon

14
Day of week (1=Monday)
1 to 7
72
-
stoptdow

15
Week Number of Month 
1 to 5
53
-
stopwom

1.
0 = Unused


1 = broadcast  time, date, holiday flag and OAT (as like existing pro_dialog control). 


2= For Stand alone chiller.  Day light saving time & holiday determination will be done without broadcasting thru 


the bus.

2.
Day of week where daylight saving time will occur in the morning (at 2:00 am). Usually, daylight saving time


occurs in the Sunday (7) morning.  1 hour shall be added in the clock when entering and 1 hour substracted when 


leaving.

3.
Date once selected (from 1) shall occur in the week number entered here.  

#1 :  if  day of  week select is 7 (Sunday). Therefor time change will occur in the first Sunday (week number 1) in the month

#5:  if  day of  week select is 7 (Sunday). Therefor time change will occur in the last Sunday in the month (some time 4th Sunday sometime the 5th).  

The daylight saving entering default configuration corresponds to European Nations and a lot of other nations (Last Sunday in March). USA uses First Sunday (week number 1) in April. 

The daylight saving leaving default configuration corresponds to USA, European Nations and a lot of other nations (Last Sunday in October). 

CONFIGURATION SCREEN
TABLE NAME: OCCDEFCS / OCCPC01S and OCCPC02S     PIC TABLE TYPE : 14H, instance 2

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT

Timed Override Hours
0-4
0
-
OVR_EXT


Period 1 DOW (MTWTFSSH)
0/1
11111111
-
DOW1


Occupied From
0:00-24:00
0:00
-
OCCTOD1


Occupied To
0:00-24:00
24:00
-
UNOCTOD1


Period 2 DOW (MTWTFSSH)
0/1
00000000
-
DOW2


Occupied From
0:00-24:00
0:00
-
OCCTOD2


Occupied To
0:00-24:00
00:00
-
UNOCTOD2


Period 3 DOW (MTWTFSSH)
0/1
00000000
-
DOW3


Occupied From
0:00-24:00
0:00
-
OCCTOD3


Occupied To
0:00-24:00
00:00
-
UNOCTOD3


Period 4 DOW (MTWTFSSH)
0/1
00000000
-
DOW4


Occupied From
0:00-24:00
0:00
-
OCCTOD4


Occupied To
0:00-24:00
00:00
-
UNOCTOD4


Period 5 DOW (MTWTFSSH)
0/1
00000000
-
DOW5


Occupied From
0:00-24:00
0:00
-
OCCTOD5


Occupied To
0:00-24:00
00:00
-
UNOCTOD5


Period 6 DOW (MTWTFSSH)
0/1
00000000
-
DOW6


Occupied From
0:00-24:00
0:00
-
OCCTOD6


Occupied To
0:00-24:00
00:00
-
UNOCTOD6


Period 7 DOW (MTWTFSSH)
0/1
00000000
-
DOW7


Occupied From
0:00-24:00
0:00
-
OCCTOD7


Occupied To
0:00-24:00
00:00
-
UNOCTOD7


Period 8 DOW (MTWTFSSH)
0/1
00000000
-
DOW8


Occupied From
0:00-24:00
0:00
-
OCCTOD8


Occupied To
0:00-24:00
00:00
-
UNOCTOD8

TABLE NAME: HOLIDAY / HOLDY01S to HOLDY16S      PIC TABLE TYPE : 14H, instance 3

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT

Holiday 
Start Month
0-12
0
-
HOL_MON


Start Day
0-31
0
-
HOL_DAY


Duration (days)
0-99
0
-
HOL_LEN

ALARM CONFIGURATION SCREEN
TABLE NAME: ALARMDEF           PIC TABLE TYPE : 14H, instance 4

DESCRIPTION
STATUS
DEFAULT       
POINT
1
Alarm Routing Control
0-11111111
00000000
ALRM_CNT

2
Alarm Equipment Priority
0 - 7
4
EQP_TYP

3
Comm Failure Retry Time
1 - 240 min
10
RETRY_TM

4
Realarm Time
1 - 255 min
30
RE_ALARM

5
Alarm System Name
8 chars
PRO_RBRQ
ALRM_NAM

TABLE NAME: OCCMAINT         PIC TABLE TYPE : 15,

DESCRIPTION
STATUS
UNITS      
POINT
1 
Current Mode (1=occup.)
0/1
-
MODE

2 
Current Occup Period #
1 to 8
-
PER_NO

3 
Timed -Override in Effect
Yes/No
-
OVERLAST

4 
Timed-Override Duration
0 to 4
hours
OVR_HRS

5 
Current Occupied Time
00:00 to 23:59
-
STRTTIME

6 
Current Unoccupied Time
00:00 to 23:59
-
ENDTIME

7 
Next Occupied Day
Mon to Sun
-
NXTOCDAY

8 
Next Occupied Time
00:00 to 23:59
-
NXTOCTIM

9 
Next Unocupied Day
Mon to Sun
-
NXTUNDAY

10 
Next Unoccupied Time
00:00 to 23:59
-
NXTUNTIM

11 
Prev Unocupied Day
Mon to Sun
-
PRVUNDAY

12 
Prev Unoccupied Time
00:00 to 23:59
-
PRVUNTIM

SETPOINT SCREEN
TABLE NAME: SETPOINT         PIC TABLE TYPE : 17H, instance 1

DESCRIPTION
STATUS
DEFAULT
UNITS    
POINT
1
COOLING

2
Cooling Setpoint 1
- 20 to 101
44.0
°F
csp1

3
Cooling Setpoint 2
- 20 to 101
44.0
°F
csp2

4
Cooling Ice Setpoinp
- 20 to 101
44.0
°F
ice_sp

5 
OAT No Reset Value
14 to 125
14.0
°F
oatcr_no

6
OAT Full Reset Value
14 to 125
14.0
°F
oatcr_fu

7
Delta T No Reset Value
0 to 25
0.0
^F
dt_cr_no

8
Delta T Full Reset Value
0 to 25
0.0
^F
dt_cr_fu

9
Current No Reset Value
0 to 20
0.0
ma
v_cr_no

10
Current Full Reset Value
0 to 20
0.0
ma
v_cr_fu

11 
Space T No Reset Value
14 to 125
14.0
°F
spacr_no

12
SpaceT Full Reset Value
14 to 125
14.0
°F
spacr_fu

13
Cooling Reset Deg. Value
-30 to 30
0.0
^F
cr_deg

14
Cooling Ramp Loading
0.2 to 2.0
1.0
^F
cramp_sp

15

16
HEATING

17
Heating Setpoint 1
80 to 153
100.0
°F
hsp1

18
Heating Setpoint 2
80 to 153
100.0
°F
hsp2

19
OAT No Reset Value
14 to 125
14.0
°F
oathr_no

20
OAT Full Reset Value
14 to 125
14.0
°F
oathr_fu

21
Delta T No Reset Value
0 to 25
0.0
^F
dt_hr_no

22
Delta T Full Reset Value
0 to 25
0.0
^F
dt_hr_fu

23
Current No Reset Value
0 to 20
0.0
ma
v_hr_no

24
Current Full Reset Value
0 to 20
0.0
ma
v_hr_fu

25
Heating Reset Deg. Value
-30 to 30
0.0
^F
hr_deg

26
Heating Ramp Loading
0.2 to 2.0
1.0
^F
hramp_sp

27

28
AUTO CHANGEOVER

29
Cool Changeover Setpt
39 to 122
75.0
°F
cauto_sp

30
Heat Changeover Setpt
32 to 115
64.0
°F
hauto_sp

31

32
MISCELLANEOUS

33
Switch Limit Setpoint 1
0 to 100
100
%
lim_sp1

34
Switch Limit Setpoint 2
0 to 100
100
%
lim_sp2

35
Switch Limit Setpoint 3
0 to 100
100
%
lim_sp3

36
Reclaim Setpoint
95 to 140
122.0
°F
rsp

37
Reclaim Deadband
5 to  27
9.0
^F
hr_deadb

38
Water Val Condensing Stp
80 to  120
86.0
°F
w_sct_sp

CONTROLLER IDENTIFICATION SCREEN
TABLE NAME: Ctrl_ID           PIC TABLE TYPE : 20H,
DESCRIPTION
STATUS
DEFAULT
Device Name
8 chars
PD5_RGWQ

Description
24 chars
PRO-DIALOG 5 30RG&30WQ

Location
24 chars

Software Part Number
16 chars
CSA-SR-20C4700NN
Model Number
20 chars


Serial Number
12 chars

Reference Number
24 chars

Note: The Model Number shall allow to verify the version compatibility between Flash and the Runtest Downloader. If this number doesn't fit the number registered in the Run Test Downloader  the download of any table shall not be allowed.

NN is software version

APPENDIX C — CCN ALARM DESCRIPTION

	alarm number


	alarm number viewed by CCN gateway (modbus …)


	High Tier  Display

alarm code


	Comforlink User Display

alarm code


	Alarm text description and ccn message

	
	
	Thermistor failure
	

	1
	1
	th-01
	th.01
	Cooler Entering Fluid Thermistor

	2
	2
	th-02
	th.02
	Cooler Leaving Fluid Thermistor

	3
	3
	th-03
	th.03
	Circuit A Defrost Thermistor

	4
	4
	th-04
	th.04
	Circuit B Defrost Thermistor

	5
	5
	th-06
	th.06
	Condenser Entering Fluid Thermistor

	6
	6
	th-07
	th.07
	Condenser Leaving Fluid Thermistor

	7
	7
	th-08
	th.08
	Reclaim Condenser Entering Thermistor

	8
	8
	th-09
	th.09
	Reclaim Condenser Leaving Thermistor

	9
	9
	th-10
	th.10
	OAT Thermistor                                                 

	10
	10
	th-11
	th.11
	MASTER/Slave Common Fluid Thermistor                           

	11
	11
	th-12
	th.12
	Circuit A Suction Gas Thermistor                               

	12
	12
	th-13
	th.13
	Circuit B Suction Gas Thermistor                               

	13
	13
	th-14
	th.14
	Circuit C Suction Gas Thermistor                               

	14
	14
	th-15
	th.15
	Circuit A Discharge Gas Thermistor                               

	15
	15
	th-16
	th.16
	Circuit B Discharge Gas Thermistor                               

	16
	16
	th-17
	th.17
	Circuit C Discharge Gas Thermistor                               

	17
	17
	th-18
	th.18
	Circuit A Condenser Subcooling Liquid Thermistor

	18
	18
	th-19
	th.19
	Circuit B Condenser  Subcooling Liquid Thermistor

	19
	19
	th-21
	th.21
	Space Temperature Thermistor                                    

	20
	20
	th-23
	th.23
	Cooler heater feedback thermistor                                    

	21
	21
	th-24
	th.24
	Circuit A Economizer Gas Thermistor                               

	22
	22
	th-25
	th.25
	Circuit B Economizer Gas Thermistor                               

	23
	23
	th-26
	th.26
	Circuit C Economizer Gas Thermistor                               

	
	
	Pressure Transducers
	

	24
	24
	Pr-01
	Pr.01
	Circuit A Discharge Transducer

	25
	25
	Pr-02
	Pr.02
	Circuit B Discharge Transducer                                 

	26
	26
	Pr-03
	Pr.03
	Circuit C Discharge Transducer                                 

	27
	27
	Pr-04
	Pr.04
	Circuit A Suction Transducer

	28
	28
	Pr-05
	Pr.05
	Circuit B Suction Transducer

	29
	29
	Pr-06
	Pr.06
	Circuit C Suction Transducer                                   

	30
	30
	Pr-07
	Pr.07
	Circuit A Reclaim Pumpdown Pressure Transducer                 

	31
	31
	Pr-08
	Pr.08
	Circuit B Reclaim Pumpdown Pressure Transducer                 

	32
	32
	Pr-10
	Pr.10
	Circuit A Oil Pressure Transducer          

	33
	33
	Pr-11
	Pr.11
	Circuit B Oil Pressure Transducer          

	34
	34
	Pr-12
	Pr.12
	Circuit C Oil Pressure Transducer          

	35
	35
	Pr-13
	Pr.13
	Circuit A Economizer Pressure Transducer          

	36
	36
	Pr-14
	Pr.14
	Circuit B Economizer Pressure Transducer          

	37
	37
	Pr-15
	Pr.15
	Circuit C Economizer Pressure Transducer          

	 
	 
	Communication with slave boards
	

	38
	38
	Co-a1
	Co.a1
	Loss of communication with Compressor Board A                

	39
	39
	Co-b1
	Co.b1
	Loss of communication with Compressor Board B                 

	40
	40
	Co-C1
	Co.C1
	Loss of communication with Compressor Board C                

	41
	41
	Co-E1
	Co.E1
	Loss of communication with EXV Board Number A                  

	42
	42
	Co-E2
	Co.E2
	Loss of communication with EXV Board Number B                  

	43
	43
	Co-E3
	Co.E3
	Loss of communication with EXV Board Number C                  

	44
	44
	Co-F1
	Co.F1
	Loss of communication with Fan Board Number 1

	45
	45
	Co-F2
	Co.F2
	Loss of communication with Fan Board Number 2                  

	46
	46
	Co-F3
	Co.F3
	Loss of communication with Fan Board Number 3

	47
	47
	Co-O1
	Co.O1
	Loss of communication with Free Cooling Board 1                   

	48
	48
	Co-O2
	Co.O2
	Loss of communication with Free Cooling Board  2

	49
	49
	Co-O3
	Co.O3
	Loss of communication with Energy Management NRCP2  Board  

	50
	50
	Co-O4
	Co.O4
	Loss of communication with Heat Reclaim  Board  

	51
	51
	Co-O5
	Co.O5
	Loss of communication with AUX Board 6

	 
	 
	Process  failure
	

	52
	52
	P-01
	P.01
	Cooler Freeze Protection                                       

	53
	53
	P-02
	P.02
	Circuit A Condenser Freeze Protection                                       

	54
	54
	P-03
	P.03
	Circuit B Condenser Freeze Protection                                       

	55
	55
	P-04
	P.04
	Circuit C Condenser Freeze Protection                                       

	56
	56
	P-05
	P.05
	Circuit A Low Suction Temperature                              

	57
	57
	P-06
	P.06
	Circuit B Low Suction Temperature                              

	58
	58
	P-07
	P.07
	Circuit C Low Suction Temperature

	59
	59
	P-08
	P.08
	Circuit A  High Superheat  

	60
	60
	P-09
	P.09
	Circuit B  High Superheat  

	61
	61
	P-10
	P.10
	Circuit C  High  Superheat  

	62
	62
	P-11
	P.11
	Circuit A Low Superheat

	63
	63
	P-12
	P.12
	Circuit B Low Superheat

	64
	64
	P-13
	P.13
	Circuit C Low Superheat

	65
	65
	P-14
	P.14
	Cooler Interlock Failure

	66
	66
	P-28
	P.28
	Electrical Box Thermostat or Power Reverse Phase Detection

	67
	67
	P-29
	P.29
	Loss of communication with System Manager

	68
	68
	P-30
	P.30
	Master/Slave communication Failure

	69
	69
	P-67
	P.67
	Circuit A Low Oil Pressure 

	70
	70
	P-68
	P.68
	Circuit B Low Oil Pressure 

	71
	71
	P-69
	P.69
	Circuit C Low Oil Pressure 

	72
	72
	P-70
	P.70
	Circuit A Max Oil Filter Differential Pressure 

	73
	73
	P-71
	P.71
	Circuit B Max Oil Filter Differential Pressure

	74
	74
	P-72
	P.72
	Circuit C Max Oil Filter Differential Pressure

	75
	75
	P-84
	P.84
	Circuit A High Oil Filter Drop Pressure 

	76
	76
	P-85
	P.85
	Circuit B High Oil Filter Drop Pressure

	77
	77
	P-86
	P.86
	Circuit C High Oil Filter Drop Pressure

	78
	78
	P-75
	P.75
	Circuit A Low Oil Level

	79
	79
	P-76
	P.76
	Circuit BLow Oil Level

	80
	80
	P-77
	P.77
	Circuit C Low Oil Level

	81
	81
	MC-nn
	MC.nn
	Master chiller configuration error   Number #1 to nn           

	82
	82
	FC-n0
	FC.n0
	No factory configuration

	83
	83
	FC-01
	FC.01
	Illegal factory configuration Number #1 to nn

	84
	84
	P-31
	P.31
	Unit is in CCN emergency stop     

	85
	85
	P-32
	P.32
	Cooler pump #1 default

	86
	86
	P-33
	P.33
	Cooler pump #2 default

	87
	87
	P-15
	P.15
	Condenser Flow Switch  Failure

	88
	88
	P-34
	P.34
	Circuit A Reclaim Operation Failure

	89
	89
	P-35
	P.35
	Circuit A Reclaim Operation Failure

	90
	90
	P-37
	P.37
	Circuit A - Repeated high discharge gas overrides 

	91
	91
	P-38
	P.38
	Circuit B – Repeated high discharge gas overrides

	92
	92
	P-39
	P.39
	Circuit C – Repeated high discharge gas overrides 

	93
	93
	P-40
	P.40
	Circuit A – Repeated low suction temp overrides

	94
	94
	P-41
	P.41
	Circuit B – Repeated low suction temp overrides 

	95
	95
	P-42
	P.42
	Circuit C – Repeated low suction temp overrides 

	96
	96
	P-43
	P.43
	Low entering water temperature in heating

	97
	97
	P-73
	P.73
	Condenser pump #1 default

	98
	98
	P-74
	P.74
	Condenser pump #2 default

	99
	99
	P-78
	P.78
	Circuit A High Discharge Temperature

	100
	100
	P-79
	P.79
	Circuit B High Discharge Temperature

	101
	101
	P-80
	P.80
	Circuit C High Discharge Temperature

	102
	102
	P-81
	P.81
	Circuit A Low Economizer Pressure 

	103
	103
	P-82
	P.82
	Circuit B Low Economizer Pressure 

	104
	104
	P-83
	P.83
	Circuit C Low Economizer Pressure 

	105
	105
	P-87
	P.87
	Circuit A Slide Valve Control Unverifiable 

	106
	106
	P-88
	P.88
	Circuit B Slide Valve Control Unverifiable 

	107
	107
	P-89
	P.89
	Circuit C Slide Valve Control Unverifiable 

	108
	108
	P-90
	P.90
	Cooler flow switch setpoint configuration failure 

	109
	109
	P-91
	P.91
	Cooler flow switch failure 

	 
	 
	
	
	

	
	
	Service failure
	

	110
	110
	Sr-nn
	Sr-nn
	Service maintenance alert Number # nn

	
	
	Compressor failure
	

	111-01
	111
	A1-01
	A1.01
	Compressor A Motor temperature too high                    

	111-02
	112
	A1-02
	A1.02
	Compressor A Motor temperature out of range                

	111-03
	113
	A1-03
	A1.03
	Compressor A High pressure switch protection               

	111-04
	114
	A1-04
	A1.04
	Compressor A Over current                                  

	111-05
	115
	A1-05
	A1.05
	Compressor A Locked rotor                                  

	111-06
	116
	A1-06
	A1.06
	Compressor A Phase loss L1                                 

	111-07
	117
	A1-07
	A1.07
	Compressor A Phase loss L2                                 

	111-08
	118
	A1-08
	A1.08
	Compressor A Phase loss L3                                 

	111-09
	119
	A1-09
	A1.09
	Compressor A Low current alarm                             

	111-10
	120
	A1-10
	A1.10
	Compressor A Y delta starter current increase failure alarm

	111-11
	121
	A1-11
	A1.11
	Compressor A Contactor failure                             

	111-12
	122
	A1-12
	A1.12
	Compressor A Unable to stop motor                          

	111-13
	123
	A1-13
	A1.13
	Compressor A Phase reversal                                

	111-14
	124
	A1-14
	A1.14
	Compressor A MTA configuration fault                       

	111-15
	125
	A1-15
	A1.15
	Compressor A Configuration switch mismatch                 

	111-16
	126
	A1-16
	A1.16
	Compressor A Unexpected switch setting change              

	111-17
	127
	A1-17
	A1.17
	Compressor A Power on reset                                

	111-18
	128
	A1-18
	A1.18
	Compressor A UL 1998 critical section software error       

	111-19
	129
	A1-19
	A1.19
	Compressor A UL 1998 current measure dual channel mismatch 

	112-01
	130
	B1-01
	B1.01
	Compressor B  Motor temperature too high                    

	112-02
	131
	B1-02
	B1.02
	Compressor B  Motor temperature out of range                

	112-03
	132
	B1-03
	B1.03
	Compressor B High pressure switch protection               

	112-04
	133
	B1-04
	B1.04
	Compressor B Over current                                  

	112-05
	134
	B1-05
	B1.05
	Compressor B Locked rotor                                  

	112-06
	135
	B1-06
	B1.06
	Compressor B Phase loss L1                                 

	112-07
	136
	B1-07
	B1.07
	Compressor B Phase loss L2                                 

	112-08
	137
	B1-08
	B1.08
	Compressor B Phase loss L3                                 

	112-09
	138
	B1-09
	B1.09
	Compressor B Low current alarm                             

	112-10
	139
	B1-10
	B1.10
	Compressor B Y delta starter current increase failure alarm

	112-11
	140
	B1-11
	B1.11
	Compressor B Contactor failure                             

	112-12
	141
	B1-12
	B1.12
	Compressor B Unable to stop motor                          

	112-13
	142
	B1-13
	B1.13
	Compressor B Phase reversal                                

	112-14
	143
	B1-14
	B1.14
	Compressor B  MTA configuration fault                       

	112-15
	144
	B1-15
	B1.15
	Compressor B Configuration switch mismatch                 

	112-16
	145
	B1-16
	B1.16
	Compressor B Unexpected switch setting change              

	112-17
	146
	B1-17
	B1.17
	Compressor B Power on reset                                

	112-18
	147
	B1-18
	B1.18
	Compressor B UL 1998 critical section software error       

	112-19
	148
	B1-19
	B1.19
	Compressor B UL 1998 current measure dual channel mismatch 

	113-01
	149
	C1-01
	C1.01
	Compressor C Motor temperature too high                    

	113-02
	150
	C1-02
	C1.02
	Compressor C Motor temperature out of range                

	113-03
	151
	C1-03
	C1.03
	Compressor C High pressure switch protection               

	113-04
	152
	C1-04
	C1.04
	Compressor C Over current                                  

	113-05
	153
	C1-05
	C1.05
	Compressor C Locked rotor                                  

	113-06
	154
	C1-06
	C1.06
	Compressor C Phase loss L1                                 

	113-07
	155
	C1-07
	C1.07
	Compressor C Phase loss L2                                 

	113-08
	156
	C1-08
	C1.08
	Compressor C Phase loss L3                                 

	113-09
	157
	C1-09
	C1.00
	Compressor C Low current alarm                             

	113-10
	158
	C1-10
	C1.10
	Compressor C Y delta starter current increase failure alarm

	113-11
	159
	C1-11
	C1.11
	Compressor C Contactor failure                             

	113-12
	160
	C1-12
	C1.12
	Compressor C Unable to stop motor                          

	113-13
	161
	C1-13
	C1.13
	Compressor C Phase reversal                                

	113-14
	162
	C1-14
	C1.14
	Compressor C MTA configuration fault                       

	113-15
	163
	C1-15
	C1.15
	Compressor C Configuration switch mismatch                 

	113-16
	164
	C1-16
	C1.16
	Compressor C Unexpected switch setting change              

	113-17
	165
	C1-17
	C1.17
	Compressor C Power on reset                                

	113-18
	166
	C1-18
	C1.18
	Compressor C UL 1998 critical section software error       

	113-19
	167
	C1-19
	C1.19
	Compressor C UL 1998 current measure dual channel mismatch 



Table 43 – Troubleshooting

	Symptom
	Possible Cause
	Possible Remedy

	Unit does not run
	Check for power to unit
	· Check Overcurrent Protection Device

· Check Non-Fused Disconnect (if equipped)

· Restore Power to unit

	
	Wrong/Incorrect unit configuration
	· Check Unit Configuration

	
	Active Alarm
	· Check Alarm status.  See separate Alarm and follow troubleshooting instructions

	
	Active Operating Mode
	· Check for Operating Modes.  See Operating Modes and follow troubleshooting instructions

	Unit operates too long or continuously
	Low refrigerant charge
	· Check for leak and add refrigerant.

	
	Compressor or control contacts welded
	· Replace contactor or relay.

	
	Air in Chilled Water Loop
	· Purge water loop

	
	Non-condensibles in Refrigerant circuit.
	· Remove refrigerant and recharge.

	
	Inoperative EXV
	· Check EXV, clean or replace.

· Check EXV Cable, replace if necessary.

· Check EXV Board for output signal.

	Circuit does not run
	Active Alarm
	· Check Alarm status.  See separate Alarm and follow troubleshooting instructions

	
	Active Operating Mode
	· Check for Operating Modes.  See Operating Modes and follow troubleshooting instructions

	Circuit does not load
	Active Alarm
	· Check Alarm status.  See separate Alarm and follow troubleshooting instructions

	
	Active Operating Mode
	· Check for Operating Modes.  See Operating Modes and follow troubleshooting instructions

	
	Low Saturated Suction Temperature
	· See Operating Modes 21, 22 and 23.

	
	High Circuit Suction Superheat
	· The circuit capacity is not allowed increase if circuit superheat is greater than 36 F (20 C).  See Alarms P.08, P.09 and P.10 for potential causes. 

	
	Low Suction Superheat
	· The circuit capacity is not allowed to increase if the circuit superheat is less than 5 F (2.8 C).  See Alarms P.11, P.12 and P.13 for potential causes.

	Compressor does not run
	Active Alarm
	· Check Alarm status.  See separate Alarm and follow troubleshooting instructions

	
	Active Operating Mode
	· Check for Operating Modes.  See Operating Modes and follow troubleshooting instructions

	
	Inoperative Compressor Contactor
	· Check control wiring

· Check Scroll Protection Module

· Check Contactor Operation, replace if necessary.

	Chilled Water Pump is ON, but the machine is OFF
	Cooler Freeze Protection
	· Chilled water loop temperature too low. Check cooler heater.










	
	

	
	
	

	



















	
	
	
	

	

	
	
	
	



	

	

	
	
	
	

	

	











	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	

	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


	
	
	
	
	
	
	

	
	
	
	
	

	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	































































































































































































































	

	
	

	
	

	
	

	
	

	
	









	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	














































































































































































































































	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	


















































































	

	


	

	


	

	























	




	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	















	

	
	
	
	
	

	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	

	
	
	

	
	
	
	
	
	
	

	
	
	



	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	





	
	
	
	
	

	

	
	


	
	
	

	
	









	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	



	
	
	

	
	


	
	
	

	
	
	
	
	

	
	


	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	




	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	



	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	



	
	
	
	
	
	

	
	
	

	
	
	

	
	
	


	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	




	
	
	

	
	
	


	
	
	

	
	
	
	
	
	



	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	



	
	
	
	
	
	

	


	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	





	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	



	
	
	
	
	

	



	
	

	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	



	
	
	
	
	

	
	
	
	
	

	



	
	
	
	

	



	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	


	
	
	
	

	
	
	
	
	



	
	
	
	
	

	
	
	
	
	

	





	
	
	
	



	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	



	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	




	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	



	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	




	
	
	
	
	

	



	
	
	
	

	


	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	




	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	




	
	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	





	
	
	
	

	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	




	
	
	
	

	


	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	




	
	
	
	
	

	


	
	
	
	
	

	
	
	
	
	


	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	
	
	
	
	

	
	
	
	
	




	
	
	
	
	
	

	
	
	
	


	
	

	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	


	
	

	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	


	
	



	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	















































































	
	
	

	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	

	
	
	

	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	











	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	






























































































	
	
	
	


	
	
	
	





	
	
	
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	





	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	



























































































































































































































































































Typical Economizer Assembly





Economizer Flow to Compressor





Main Flow to Cooler





Economizer EXVEXV





Main  EXV





Sightglass



































the Service Test mode. Press		to access TEST. Press�ENTER





to access T.REQ. Press		and the display�ENTER





will show OFF. Press		and OFF will flash. Enter the�ENTER





ENTER












_1162299307.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature (deg F)

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0





Sheet2

		





Sheet3

		






_1162309064.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



4-20 mA Reset

		4

		20



Reset

mA Signal

Degrees Reset (deg F)

4-20 mA Temperature Reset

0

5



Return Water Reset

		0

		2

		10



Entering - Leaving Water Temperature (deg F)

Degrees Reset (deg F)

Return Water Reset

5

5

0



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0

		Return Water Reset

		EWT-LWT		Reset

		0		5

		2		5

		10		0

		4-20 mA Reset

		mA		Reset

		4		0

		20		5





Sheet2

		





Sheet3

		






_1163922427.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



4-20 mA Reset

		4

		20



Reset

mA Signal

Degrees Reset (deg F)

4-20 mA Temperature Reset

0

5



Return Water Reset

		0

		2

		10



Entering - Leaving Water Temperature (deg F)

Degrees Reset (deg F)

Return Water Reset

5

5

0



Standard Control

		0		0

		100		100



EWT

LWT

Design
Rise

EWT

LWT

% Loading

Fluid Temperature (deg F)

Chilled Water Temperature Control

44

44

44

54



4-20 mA Demand Limit

		4

		20



Demand Limit

mA Demand Limit Signal

% Demand Limit

4-20 mA Demand Limit

100

0



4-20 mA Set Point

		4		0		0

		20		4.9		10.4

				15.4		15.4

				20		20



Equation

Medium Tempertaure Brine

Fresh Water

mA Signal

Set Point

4-20 mA Set Point Control

10

14

38

80

14

38

60

60

60

60



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0

		Return Water Reset

		EWT-LWT		Reset

		0		5

		2		5

		10		0

		4-20 mA Reset

		mA		Reset

		4		0

		20		5

		Building Load

		Load		EWT		LWT

		0		44		44

		100		44		54

		4-20 mA Demand Limit

		mA		Demand Limit

		4		100

		20		0

		4-20 mA Set Point

		4		10		0		14		0		38

		20		80		4.9		14		10.4		38

						15.4		60		15.4		60

						20		60		20		60





Sheet2

		





Sheet3

		






_1165125278.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



4-20 mA Reset

		4

		20



Reset

mA Signal

Degrees Reset (deg F)

4-20 mA Temperature Reset

0

5



Return Water Reset

		0

		2

		10



Entering - Leaving Water Temperature (deg F)

Degrees Reset (deg F)

Return Water Reset

5

5

0



Standard Control

		0		0

		100		100



EWT

LWT

Design
Rise

EWT

LWT

% Loading

Fluid Temperature (deg F)

Chilled Water Temperature Control

44

44

44

54



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0

		Return Water Reset

		EWT-LWT		Reset

		0		5

		2		5

		10		0

		4-20 mA Reset

		mA		Reset

		4		0

		20		5

		Building Load

		Load		EWT		LWT

		0		44		44

		100		44		54





Sheet2

		





Sheet3

		






_1187062468

_1163406423.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



4-20 mA Reset

		4

		20



Reset

mA Signal

Degrees Reset (deg F)

4-20 mA Temperature Reset

0

5



Return Water Reset

		0

		2

		10



Entering - Leaving Water Temperature (deg F)

Degrees Reset (deg F)

Return Water Reset

5

5

0



Standard Control

		0		0

		100		100



EWT

LWT

Design
Rise

EWT

LWT

% Loading

Fluid Temperature (deg F)

Chilled Water Temperature Control

44

44

44

54



4-20 mA Demand Limit

		4

		20



Demand Limit

mA Demand Limit Signal

% Demand Limit

4-20 mA Demand Limit

100

0



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0

		Return Water Reset

		EWT-LWT		Reset

		0		5

		2		5

		10		0

		4-20 mA Reset

		mA		Reset

		4		0

		20		5

		Building Load

		Load		EWT		LWT

		0		44		44

		100		44		54

		4-20 mA Demand Limit

		mA		Demand Limit

		4		100

		20		0





Sheet2

		





Sheet3

		






_1162300404.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0





Sheet2

		





Sheet3

		






_1162307675.xls
OAT Reset

		0

		55

		85

		125



Reset

Outdoor Temperature

Reset Amount (deg F)

OAT Temperature Reset

15

15

0

0



Space Temp Reset

		60

		68

		72

		80



Reset

Space Temperature (deg F)

Degrees Reset (deg F)

Space Temperature Reset

6

6

0

0



4-20 mA Reset

		4

		20



Reset

mA Signal

Degrees Reset (deg F)

4-20 mA Temperature Reset

0

5



Sheet1

		OAT Example

		OAT		Reset

		0		15

		55		15

		85		0

		125		0

		Space Temperature Reset

		SPT		Reset

		60		6

		68		6

		72		0

		80		0

		Return Watert Reset

		EWT-LWT		Reset

		4-20 mA Reset

		mA		Reset

		4		0

		20		5





Sheet2

		





Sheet3

		






_1125567940.vsd
�

�

Valve Builder�

�

�

�

text�

�

�

text�

�

�

�

text�

High Pressure Oil�

De-energized
FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

�

�

�

�

�

�

Drain to 
Low Pressure�

Bleed Line to Low Pressure Suction�

�

Compression Process�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

Unloaded Position�

�

�

�

�

�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

Energized
FLOW
Valve #1 (NC)�

�

Fill with High Pressure Oil�

�

Compression Process�

Bleed Line to Low Pressure Suction�

Loaded Position�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

�

�

�

�

�

�

Bleed Line to Low Pressure Suction�

Slide Valve�

Trapped Oil at High Pressure�

�

Discharge
Port�

Unloader Piston Chamber�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

Compression Process�

Part Load Position�


_1162041181.unknown

_1125567588.vsd
�

�

Valve Builder�

�

�

�

text�

�

�

text�

�

�

�

text�

High Pressure Oil�

De-energized
FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

�

�

�

�

�

�

Drain to 
Low Pressure�

Bleed Line to Low Pressure Suction�

�

Compression Process�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

Unloaded Position�

�

�

�

�

�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

Energized
FLOW
Valve #1 (NC)�

�

Fill with High Pressure Oil�

�

Compression Process�

Bleed Line to Low Pressure Suction�

Loaded Position�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

�

�

�

�

�

�

Bleed Line to Low Pressure Suction�

Slide Valve�

Trapped Oil at High Pressure�

�

Discharge
Port�

Unloader Piston Chamber�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

Compression Process�

Part Load Position�


_1109589553.vsd
�

�

Valve Builder�

�

�

�

text�

�

�

text�

�

�

�

text�

High Pressure Oil�

De-energized
FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

�

�

�

�

�

�

Drain to 
Low Pressure�

Bleed Line to Low Pressure Suction�

�

Compression Process�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

Unloaded Position�

�

�

�

�

�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

Energized
FLOW
Valve #1 (NC)�

�

Fill with High Pressure Oil�

�

Compression Process�

Bleed Line to Low Pressure Suction�

Loaded Position�

Slide Valve�

Discharge
Port�

Unloader Piston Chamber�

�

�

�

�

�

�

Bleed Line to Low Pressure Suction�

Slide Valve�

Trapped Oil at High Pressure�

�

Discharge
Port�

Unloader Piston Chamber�

High Pressure Oil�

Energized
NO FLOW
Valve #2 (NO) �

De-energized
NO FLOW
Valve #1 (NC)�

Compression Process�

Part Load Position�


