Loading 19DVFD Software into a CCN Module with CView
1. Make a file in C:\CVIEW\BESTPP and name it for the job site

2. Transfer the original Best++ files for the 19DVFD program to this file so you won’t make any changes to the original program

3. You will need to change the Dict1.fld file to point to the new folder you placed the 19DVFD files into.  In Explorer open the folder CView\BestPP\”the building you moved the files to”, open the Dict1.Fld file, it will open in notepad then you can change the files to point to the folder you made for this job.

4. Open CView and create a file for the building you are working on.  Once you have created the building and are creating the controller click on the import radio button, select browse and select the 19DVFD.CWX file in the BestPP building file.

5. Highlight the controller 19VFD controller for the building in CView, Click the Download Computer Arrow and download the 19DVFD file to the 6400

6. Check the 6400 Dip Switch settings per the controller wiring prints

7. Open Best ++ tab , “select comfort controller” heading, select the controller for the building you are working on
8. Under File select “open folder”, then select the building you are working on, CView/Best++/”Your Building File” and select the DICT1.FLD file

9. In the task bar in Best++ you should be able to see all the Best++ files for the 19DVFD software (10 files)
10. Select Best++, select compile all, check the file for any error indications

11. Select Dict1 in the Task Bar

12. Open Best++ tab and select Download All

13. Once the download is complete to the 6400 select the 19DVFD controller in CView, select / Maintenance/ DBSTATSM/ Updated/ and look that there are no errors indicated. No errors indicates the program should be good.

To Make Changes to the Programming Setpoints 

1. Open the Best++ Program in the CView folder

2. Open Best++ tab and “Select Comfort Controller” and select the controller for the 6400 you are working on
3. Under File select “open folder”, then select the building you are working on, CView/Best++/”Your Building File” and select the DICT1.FLD file

4. In the task bar in Best++ you should be able to see all the Best++ files for the 19DVFD software (10 files)

5. Select the file you want to change programming on, make the changes and save the Program

6. Compile the program you changed and then download it to the controller

7. check the controller to verify changes

8. When all changes are made do a file export on CView to the job file for future use
