Setting up a Data Collection III Module 

1. Load Data Collection Module into Comfort View 

2. Highlight Data Collection Module

3. Click on CCN tools

4. Click on CCN Options

5. Click on History

6. Each history i.e. HSTRM06S, 12S etc is a Master, each master will have 5 slaves under it.  Each slave will respond to its masters timing, start/stop parameters etc

7. Click on the HSTRM01-06S etc. to open the collection point

8. Set up HSTRM06S, 012S, 18S etc. the highest number in a group, this is the master and will setup the others in the group, set the start and stop times if needed.  The module will hold 192 collections per point.   If you don’t set a day or month it will execute daily.  If you don’t set a time it will start as soon as it is saved.  It will roll out the oldest collection and replace with the newest one.
9. Click on “controller name” and then push the F7 function key to open a dialogue box to select the controller and its point

10. Save the changes and download to the controller
11. You can modify the collection points in the  Config area of Comfort View under the Data Collection Module.

12. The master points can be checked or modified in the Hist-Mst file and the slave points can be modified in the Hist-Slv file.  Remember slave 1-5 go with master 6 and slave 7-11 go with master 12 etc.

To generate a report from the stored data

1. you must be connected to the module through Comfort View prior to trying to generate a report

2. open the reports file in the CCN folder
3. open the History file

4. create a new file for the building you are generating or open the building you are in

5. once in the building you can go to file and generate a report
