19XR ANNUAL TYPICAL PARTS 

QTY
PART NUMBER
DESCRIPTION

COST

COST/UNIT

1
02XB660004

INT. OIL FILTER KIT
$70.80
$70.80
OR
1
02XR05009501
SMALL DIA. INLINE FLTR
$225.60
$225.60
OR 

1
02XR05006201
LARGE DIA. INLINE FLTR
$202.40
$202.40 NOTE: SOME 19XR UNITS UTLIZE THE EXTERNAL INLINE FILTER 
The internal filters are used on all pre 2002 chillers and certain newer units, the external long filter is used on post 2002 size 3 compressors.

REFRIGERANT FILTER
FRAME 1-6


1
P5028415

5/8 FL. REF. DRIER 
$   36.44
$   36.44
FRAME 7&8
 19XR FRAME 7 &8 CHILLERS USE 7/8” LINE THAT WOULD BE BEST SERVICED WITH THE ADDITION OF A 7/8” 1 CORE DRIER SHELL(SUCH AS SPORLAN C-487G)AND FITTINGS DURING THE FIRST ANNUAL AND THEN ONLY THE DRIER CORE REPLACEMENT AFTER THE FIRST TIME.

1
SPOR 487G

SPOR SHELL+FTTGS.
$180.00
$180.00

1
OTHER ANNUALS
SPORLAN 4864 CORE
$  16.00
$  16.00
1
KH42ME060

OIL REC. FILTER 3/8 FL.
$38.64  
  $38.64
OIL (RECOMMEND ANALYSIS, ONLY REPLACE IF OIL IS BAD)

2
PP23BZ103 (SW68)POE OIL (5 GAL. CAN)
$ 268.80
$   537.60
4
PP23BZ103 (SW68) OIL 5 GAL (SZ 5 COMP)
$ 268.80
$ 1075.20
OR

10
SW68


POE OIL (1 GAL)

$   60.00
$      60.00
18
SW68


 OIL 1 GAL (SZ 5 COMP)
$   60.00
$  1080.00
NOTE: SIZE 5 COMPRESSORS REQUIRE 18 GALLONS OF OIL COST IS $1080.00! The additional labor cost of replacing 18 gallons of oil from 1 gallon cans instead of 5 gallon cans is not advised. Recommend buying 4-5 gallon cans if oil is to be changed.
1 
OIL SAMPLE AND SHIPPING




$80.00

PAINT (OPTIONAL) 

1
313 974-751

PAINT-CAN GREY


$7.75

$46.50**

PAINT IS SOLD THROUGH RCD IN STD. PKG. OF 6**
CONDENSER WATER BOX GASKETS (TYPICAL 150#)
DESCRIPTION



   
PART NUMBER
     COST/EA

	COND. W/B GSKT. NIH 150 PSI (FR#1)                 10XR15000201       $ 43.20

	COND. W/B GSKT. NIH 150 PSI (FR#2)                 09XB45001101       $ 26.08

	COND. W/B GSKT. NIH 150 PSI (FR#3)                 09XB45001101       $ 26.08

	COND. W/B GSKT. NIH 150 PSI (FR#4)                 09XR45000801       $ 38.88

	COND. HEAD GSKT. DISHED END (FR#4)           09XR05007001       $122.40

	COND. W/B GSKT. NIH 150 PSI (FR#5)                 09XR55000801       $ 70.00

	COND. HEAD GSKT. DISHED END (FR#5)            09XR05007002      $132.00

	COND. W/B GSKT. NIH 150 PSI (FR#6)                 09XR65000801       $ 95.20 
COND. HEAD GSKT. DISHED END (FR#6)            09XR05007003      $165.20


 COND. W/B GSKT. NIH 150 PSI (FR#7) 
      09XR75000901       $ 81.20
COND. HEAD GSKT. DISHED END (FR#7)
      09XR05007004      $184.80
COND. W/B GSKT. NIH 150 PSI (FR#8) 
      09XR85000901      $154.80
COND. HEAD GSKT. DISHED END (FR#8) 
      09XR05007005      $253.20
CONSIDER SHIPPING COSTS
SPECIAL PRODUCTS MAY REQUIRE RCD ASSISTANCE

DW 02/08
