30GX/HX ANNUAL ESTIMATES
30 SERIES CHILLERS UTILIZE 2-4 SMALLER HIGH SPEED SCREW COMPRESSORS. EACH CHILLER HAS 2 REFRIGERATION CIRCUITS THAT MAY CONTAIN 1 OR 2 COMPRESSORS DEPENDING ON THE SIZE OF THE UNIT. 30 GX UNITS ARE AIR COOLED. 30 HXA UNITS HAVE REMOTE CONDENSERS AND ARE RATHER UNCOMMON WHILE THE 30 HXC UNITS ARE WATER COOLED AND ARE QUITE COMMON.

CONFIRM THE INFORMATION CONTAINED IN THIS QUICK REFERENCE BY USING THE COMPLETE MODEL AND SERIAL NUMBER OF THE UNIT. THERE ARE A MANY UNIT VARIATIONS DUE TO THE NUMBER OF CHILLER SIZES AND SERIES NUMBERS. JOBSITE CONDITIONS CAN SIGNIFICANTLY AFFECT THE TIME REQUIRED TO PERFORM SERVICES. CONSULT SOMEONE FAMILIAR WITH THE JOBSITE AND PERFORMANCE OF SERVICES IF YOU ARE UNFAMILIAR WITH JOB VARIABLES.
 30 GX
ANNUALS TYPICALLY REQUIRE APPROXIMATELY 16 HOURS LABOR PER CHILLER.

 080-175= 2 COMPRESSORS

 204-264= 3 COMPRESSORS

 281-350= 4 COMPRESSORS

PARTS REQUIRED








COST

2-4
06NA660028

INTERNAL FILTER KIT (1 per compressor)

120.52 EA*

2
S-4004UA 

EXTERNAL FILTER (Change when specified)
  56.25 EA

30HXC

ANNUALS TYPICALLY REQUIRE APPROXIMATELY 12- 16 HOURS PER CHILLER.

076-186 = 2 COMPRESSORS

206-271 = 3 COMPRESSORS

PARTS REQUIRED








COST

2-3
06NA660028

INTERNAL FILTER KIT (1 per compressor)

 120.52 EA*

2 
30GX500403

EXTERNAL FILTER (for series 0, try other filter $$)
  217.81 EA
Or


2
4004TA

EXTERNAL FILTER (for series 3,4,5,6)

  155.26 EA
1
KK71JY180

COND. O-RING (size 76-146)


  101.20 EA

Or

1
KK71JY200

COND. O-RING (size 161-186)


    59.60 EA 

Or 

 1
KK71JY220

COND. O-RING (size 206-271)


    63.20 EA

*=Alternately 1-Parker filter (in shop) and 1- 8TB 0847 o-ring per compressor may be used for cost savings of over 100.00 per compressor (+/- $39.58 +12.40 per comp)




