Model:
 CARRIER 19EA/EB/EF/EX/FA CENTRIFUGAL CHILLER

              

Frequency:

Task and Actions

Year 1
 
 
 
 
 
ROUTINE OPERATING INSPECTION

3    
     
     
     
     
     


REPORT TO CUSTOMER UPON ARRIVAL

x    
     
     
     
     
     


LOG CHW/BRINE IN TEMPERATURE

x    
     
     
     
     
     


LOG CHW/BRINE OUT TEMPERATURE

x    
     
     
     
     
     


LOG CHW/BRINE FLOW DELTA P

x    
     
     
     
     
     


LOG CHW/BRINE PUMP DELTA P

x    
     
     
     
     
     


LOG COOLER REFRIGERANT TEMPERATURE

x    
     
     
     
     
     


LOG COOLER PRESSURE

x    
     
     
     
     
     


LOG COOLER LTD

x    
     
     
     
     
     


LOG CONDENSER WATER IN TEMPERATURE

x    
     
     
     
     
     


LOG CONDENSER WATER OUT TEMPERATURE

x    
     
     
     
     
     


LOG CONDENSER WATER FLOW DELTA P

x    
     
     
     
     
     


LOG CONDENSER WATER PUMP DELTA P

x    
     
     
     
     
     


LOG CONDENSER REFRIGERANT TEMP

x    
     
     
     
     
     


LOG CONDENSING PRESSURE

x    
     
     
     
     
     


LOG COND SUBCOOLER TEMPERATURE

x    
     
     
     
     
     


LOG CONDENSER LTD

x    
     
     
     
     
     


LOG VANE POSITION

x    
     
     
     
     
     


LOG MOTOR AMPERAGE 

x    
     
     
     
     
     


LOG OIL LEVEL

x    
     
     
     
     
     


LOG OIL SUMP TEMPERATURE

x    
     
     
     
     
     


LOG BEARING TEMPERATURE

x    
     
     
     
     
     


LOG OIL SUPPLY PRESSURE

x    
     
     
     
     
     


LOG LINE VOLTAGE

x    
     
     
     
     
     


LOG TRANSFER TIME

x    
     
     
     
     
     


LOG START COUNTS

x    
     
     
     
     
     


CHECK GENERAL OPERATING CONDITION

x    
     
     
     
     
     


CHECK LUBE SYSTEM, OIL LEVEL, COLOR, TEMP.
x    
     
     
     
     
     


CHECK GUIDE VANE SHAFT OILER

x    
     
     
     
     
     


CHECK APPROACHES THROUGH CALCULATION

x    
     
     
     
     
     


REVIEW AND EVALUATE LOG READINGS

x    
     
     
     
     
     


CLEAN UP WORK STATION

x    
     
     
     
     
     


REPORT TO CUST, ADVISE & OBTAIN SIGNATURE
x    
     
     
     
     
     

Model:
 CARRIER 19EA / EB CENTRIFUGAL CHILLER

                                      Frequency:

Task and Actions

Year 1
 
 
 
 
 
ANNUAL PREVENTIVE MAINTENANCE

1    
     
     
     
     
     


REPORT TO CUSTOMER UPON ARRIVAL

x    
     
     
     
     
     


DISCONNECT ALL CIRCUITS-(LOCKOUT & TAG)

x    
     
     
     
     
     


CHECK STARTER WIRING AND CONTACTS

x    
     
     
     
     
     


CLEAN STARTER

x    
     
     
     
     
     


MEG COMPRESSOR MOTOR <480V

x    
     
     
     
     
     


PULL OIL SAMPLE FOR ANALYSIS

x    
     
     
     
     
     


REPLACE OIL FILTER

x    
     
     
     
     
     


CALIBRATE SAFETY AND OPERATING CONTROLS
x    
     
     
     
     
     


CHECK GAUGES 

x    
     
     
     
     
     


CHECK INDICATOR LIGHTS

x    
     
     
     
     
     


TEST FOR LEAKS USING LEAK DETECTOR

x    
     
     
     
     
     


DRAIN WATER FROM CONDENSER WATER BOX

x    
     
     
     
     
     


REMOVE CONDENSER HEAD

x    
     
     
     
     
     


BRUSH CONDENSER TUBES

x    
     
     
     
     
     


RE-PLACE CONDENSER HEAD

x    
     
     
     
     
     


(RE)FILL CONDENSER WATERSIDE WITH WATER
x    
     
     
     
     
     


RESTORE POWER

x    
     
     
     
     
     


CLEAN UP WORK STATION

x    
     
     
     
     
     


REPORT TO CUST, ADVISE & OBTAIN SIGNATURE
x    
     
     
     
     
     

