
Model:
 CARRIER 19D, DA, DG, DH, DK, DM,DR – ALL SIZES




Frequency:

Task and Actions

Year 1
 
 
 
 
 
MULTI-YEAR PREVENTIVE MAINTENANCE

1    
     
     
     
     
     


REPORT TO CUSTOMER UPON ARRIVAL

x    
     
     
     
     
     


LOCKOUT AND TAG ALL CIRCUITS

x    
     
     
     
     
     


PRESSURIZE MACHINE (IF NECESSARY)

x    
     
     
     
     
     


CHECK FOR LEAKS USING LEAK DETECTOR

x    
     
     
     
     
     


CHECK STARTER WIRING AND CONTACTS

x    
     
     
     
     
     


INSPECT CONTACTORS

x    
     
     
     
     
     


TIGHTEN ELECTRICAL CONNECTIONS

x    
     
     
     
     
     


CLEAN STARTER

x    
     
     
     
     
     


MEGGER COMPRESSOR MOTOR AT STARTER <480 V 
x    
     
     
     
     
     


PULL OIL SAMPLE FOR ANALYSIS

x    
     
     
     
     
     


EVACUATE UNIT

x    
     
     
     
     
     


REMOVE INSPECTION COVER(S)

x    
     
     
     
     
     


CLEAN OIL COOLER SOLENOID STRAINER

x    
     
     
     
     
     


DISASSEMBLE OIL FILTER

x    
     
     
     
     
     


DISASSEMBLE COMPRESSOR @ DISCHARGE WALL
x    
     
     
     
     
     


DISASSEMBLE HI-SPEED ASSEMBLY

x    
     
     
     
     
     


INSPECT INLET GUIDE VANE ASSEMBLY

x    
     
     
     
     
     


INSPECT DIFFUSER

x    
     
     
     
     
     


INSPECT THRUST BEARING ASSEMBLY

x    
     
     
     
     
     


INSPECT SHAFT & SPLINE

x    
     
     
     
     
     


CHECK IMPELLER FRONT WALL CLEARANCE

x    
     
     
     
     
     


CHECK INTERNAL WIRING AND PIPING

x    
     
     
     
     
     


LOG IMPELLER FRONT WALL CLEARANCE

x    
     
     
     
     
     


CHECK THRUST CLEARANCE

x    
     
     
     
     
     


DISASSEMBLE END BELL

x    
     
     
     
     
     


DISASSEMBLE - REMOVE STATOR ASSEMBLY

x    
     
     
     
     
     


DISASSEMBLE TRANSMISSION & REMOVE MOTOR
x    
     
     
     
     
     


INSPECT TRANSMISSION

x    
     
     
     
     
     


INSPECT BULL & PINION GEARS

x    
     
     
     
     
     


INSPECT BEARINGS AND JOURNALS

x    
     
     
     
     
     


INSPECT ROTOR

x    
     
     
     
     
     


LOG COMPRESSOR MAIN BEARING CLEARNCE

x    
     
     
     
     
     


CLEAN OIL MAGNETIC PLUG

x    
     
     
     
     
     


REPLACE 0-RING

x    
     
     
     
     
     


REPLACE GASKETS

x    
     
     
     
     
     


REASSEMBLE TRANSMISSION & MOTOR

x    
     
     
     
     
     


REASSEMBLE STATOR

x    
     
     
     
     
     


REASSEMBLE END BELL

x    
     
     
     
     
     


REASSEMBLE HI-SPEED ASSEMBLY

x    
     
     
     
     
     


REASSEMBLE COMPRESSOR

x    
     
     
     
     
     


REPLACE OIL FILTER

x    
     
     
     
     
     


REPLACE VENTURI FILTER

x    
     
     
     
     
     


REPLACE REFRIGERANT FILTER

x    
     
     
     
     
     


DEHYDRATE UNIT

x    
     
     
     
     
     


DRAIN WATER FROM CONDENSER WATER BOX

x    
     
     
     
     
     


REMOVE CONDENSER HEAD

x    
     
     
     
     
     


BRUSH CONDENSER TUBES

x    
     
     
     
     
     


RE-PLACE CONDENSER HEAD

x    
     
     
     
     
     


(RE)FILL CONDENSER WATERSIDE WITH WATER
x    
     
     
     
     
     


CALIBRATE SAFETY AND OPERATING CONTROLS
x    
     
     
     
     
     


RESTORE POWER

x    
     
     
     
     
     


PERFORM CONTROLS TEST

x    
     
     
     
     
     


CLEAN UP WORK STATION

x    
     
     
     
     
     


REPORT TO CUST, ADVISE & OBTAIN SIGNATURE
x    
     
     
     
     
     

PAGE  
2

