19XL and 19XR ST-3 Thrust Bearing Inspection, Eddy Current Test, & PSIO Upgrade Package
(Not applicable for 19XR chillers with rolling element bearings)

SCOPE OF SERVICE: 

Isolate chiller.

Lockout and tag electrical.

Pump refrigerant over to storage vessel.

Break chiller with nitrogen.

Drain condenser and cooler.

Remove condenser head and cooler head.

Brush condenser and cooler tubes.

Perform Eddy Current Test on both the condenser and the cooler tube bundles.

Report findings and recommendations to customer.

Meggar compressor motor < 480 V

Disassemble front of compressor.

Check thrust bearing clearance and tolerance.

Inspect guide vane assembly.
Record findings and advise customer of findings and any recommendations.

Reassemble compressor using new gaskets and o-rings as required.

Leak check chiller using nitrogen and tracer gas per AQMD standards.

Evacuate chiller.

Charge chiller with stored, customer supplied refrigerant.

Upgrade PSIO module to the latest available version of the software.

Check configurations of PSIO and LID, change PSIO and LID battery (PIC 1) 
Start chiller and log operation.

Clean work station.

Provide written customer service reports and Annual Audit Form per rule 1415.

PAGE  
2

