19XL/XR/XRV OVERHAUL (ST-6)
19XL AND 19 XR(V) CHILLERS SHOULD HAVE PERIODIC OVERHAUL INSPECTIONS. THERE ARE A WIDE VARIETY OF OPERATING CONDITIONS BUT IT GENERALLY ACCEPTED THAT IT WOULD BE PRUDENT TO COMPLETELY DISASSMBLE AND INSPECT THE CHILLER AT APPROXIMATELY 20,000 – 30,000 HRS (POSSIBLY MORE IF THE UNIT CYCLES ON AND OFF FREQUENTLY)

THIS SHEET WILL PROVIDE AN ESTIMATE OF TYPICAL HOURS TO PERFORM THE OVERHAUL SERVICES FOR 19XL CHILLERS AND MOST SMALLER 19XR CHILLERS (UP TO MOST SIZE 4 COMPRESSORS) WITH ISOLATION VALVE THAT HOLD. THIS DOES NOT APPLY TO SIZE 5 19XR’s, UNITS WITH INSUFFICIENT SERVICE CLEARANCE, ACCESS ISSUES, ETC. (WHEN IN DOUBT CONSULT SOMEONE FAMILIAR WITH THE PROCEDURE AND LOCATION).
LABOR
OVERHAUL COMPRESSOR USING NEW GSKTS & ORINGS


 
140-180 hrs

EDDY CURRENT CLR AND COND.TUBES (INCL BRUSHING) COMP SIZE 2-3
                 8 –12 hrs

EDDY CURRENT CLR AND COND.TUBES (INCL BRUSHING) COMP SIZE 4 XR             12 –24 hrs

LINEAR FLOAT INSPECTION*






                      16 hrs

SOME EXTENDED LENGTH VESSELS DO NOT HAVE ISOLATION VALVES IN A LOCATION THAT ALLOWS FLOAT INSPECTION WITHOUT REMOVING THE UNIT CHARGE.

PARTS/ SERVICES

O-RINGS,GASKETS, ETC. “SOFT PARTS” (EXCLUDES BEARINGS, LABYS, ETC.)    
    $1100.00

OIL FOR 19XL USING R-22







    $  350.00

OIL FOR 19XL USING R- 134A OR 19XR (ALL ARE 134A) EXCEPT 19XR5

    $  573.00

GROWLER TEST AND BALANCE ROTOR





    $  500.00

MICROPROCESSOR UPGRADE ON PIC 1 UNITS (RELOAD EXISTING MODULE)
    $  300.00

EDDY CURRENT TEST







$450.00 – $1571.00**
**EDDY CURRENT TESTING 90 CENTS A TUBE OR $450 WHICHEVER IS GREATER

CONSULT TAB 6 TUBE COUNTS 19 XL’S HAVE AS FEW AS 419 TUBES AND AS MANY 

AS 929 TUBES. A SIZE 4 19XR COMPRESSOR IS ON SIZE 5, 6, OR 7 SHELLS, SIZE 7 SHELLS MAY HAVE AS MANY AS 1746 TUBES TOTAL.

DW 02/08

