May 4, 2001

Daniel Customer

ABC Maintenance Department

Processing and Distribution Facility

2901 Sunny Street

Oxnard, CA 93030-9310

805-988-XXXX (voice)

805-988-XXXX (fax)

RE: Chiller Repairs, Quote # 183XXXXXXX

Dan,

Carrier Corporation is presently performing the annual maintenance service on your 19DM chillers. 

While performing the work the service technicians have made the following observations and recommendations. It would be beneficial to have the work performed while Carrier Corporation is on site performing the annual service. 

Observations:

1. Condenser tubes are fouled. Recommendation: Perform acid cleaning.

2. Bubbles were observed on the crown sheet indicating a probable tube roll leak.

Recommendation: Remove refrigerant charge and store, pressurize to higher pressure, and check for source of bubbles, (suspect tube problems) advise and recommend repair.

3. Perform eddy current test on cooler and condenser.

4. Condenser crown sheet is corrodedand shows severe metal loss and possible tube roll problem. 

Carrier  recommends the following: Clean crown sheets, (condenser), sand blast as required, epoxy coat. 

Carrier Corporation will provide the above scope of services for $17,777.77 plus applicable taxes.

Exclusions: Overtime, Waste oil disposal, Asbestos, Oil, Refrigerant, Any additional parts or labor not included in the above scope of services.

If you have any questions or need any additional information I can be reached at 626-854-0133 or 626-926-68XX.

Carrier Corporation’s terms and conditions are outlined on side two of page one of this proposal.

Please sign at the appropriate areas and fax to Carrier Corporation at 626-435-3066.

Sincerely,

Your Name

Carrier Corporation

ACCEPTED BY: _____________________________________DATE: ____________________

