How to Use The 

ComfortLinkTM 

SmartLoader 
Software Download Program

Version 2.1

Manual Contents


1.0
About the SmartLoader Program


2.0
Hardware & Operating System Requirements


3.0
How to Install the SmartLoader

4.0 Getting Ready to Start the SmartLoader Program

5.0 Performing a Download 

6.0 Uninstalling SmartLoader

7.0 Technical Support 

8.0 Troubleshooting 

1.0 About the SmartLoader Program

SmartLoader is a Windows-based software tool that is used for downloading software to ComfortLink control boards.

SmartLoader provides for controlled software and command files stored on the hard disk or CD to be downloaded directly to the ComfortLink unit via LEN (Local Equipment Network) communications.

2.0 Hardware and Operating System Requirements 

SmartLoader requires the following hardware and operating system:

· 486 processor or better

· Minimum 640 x 480 screen resolution

· Microsoft Windows( 95, 98, 2000, XP

· RS-485 interface board, 2-wire half-duplex, 9600, 19.2K or 38.4K baud or, Serial port with RS-232/RS-485 converter, 2-wire half-duplex, 19.2K or 38.4K baud.
2.1 Cable Requirements & Connection Locations

A COMM port repeater & appropriate patch cable are needed to connect your computer to the ComfortLink unit or board. There are (2) two connection means to download unit software:

(1)  Via the “LEN” RJ11 connector on the unit’s “Comm Board” 

Or

(2) Via direct connection to the ComfortLink board
2.1.1 LEN Connectivity Requirements

LEN connectivity is accomplished through the “LEN” RJ11 on the unit’s “Comm Board” as shown in the figure below.

[image: image1.png]



Components for LEN RJ11 “Comm Board” download:

The cable/connector requirements for LEN connectivity are shown in the figure below. The components are:

· [image: image2.png]


B&B Line Powered Repeater, DB-9 to RJ11, B&B part number 485CARLP9A

Contact: B&B Electronics

707 Dayton Road

PO Box 1040

Ottawa, IL 61350

ph 815.433.5100

fx 815.433.5109

e-mail:  sales@bb-elec.com

www.bb-elec.com

· Patch Cable, six-conductor, male-to-male RJ11, straight through pin out, OR four-conductor modular extension, male-to-male RJ11, straight through pin out.

2.1.2 ComfortLink Board Connectivity Requirements

ComfortLink board communication & power connectivity is accomplished through direct connection to the J1 power & J3 communication terminals as shown in the figure below.

[image: image3.png]



Components for direct download to ComfortLink board:

Communication Components:

· B&B Line Powered Repeater, DB-9 to RJ11, B&B part number 485CARLP9A.

[image: image4.wmf]Contact: B&B Electronics

707 Dayton Road

[image: image5.wmf]PO Box 1040

Ottawa, IL 61350

ph 815.433.5100

fx 815.433.5109

[image: image6.png]J3

ODE mr

-} DL~

- CD‘)r‘ GHp=

G}»— RED

Phone Cable RJ11

1 LEN+
2 LENcomm
3 LEN-
4 (Not Used)

Yellow

Green

Black
(Not Used)



e-mail:  sales@bb-elec.com

www.bb-elec.com

· Patch Cable: Part Number 30GX680004 is available from RCD. 
· This cable can also be made from a phone cable, four-conductor modular extension, male-to-male RJ11, straight through pin out.
· The patch cable wiring diagram is based on looking at the end of the RJ11 connector, with the locking tab facing up and reading left to right. Cut the RJ11 connector off of the opposite end.
· Strip the appropriate leads and crimp on the Trifurcon terminal, qty 3, Carrier HY57MP008, (same as Molex 08-50-0189). Terminals are to be crimped and soldered to the yellow, green, and black cable wires as shown below. 
Note: Molex crimping tool required to assemble Trifurcon terminal & Molex housing. Available from Paladin Tool, part number 1631.

· Connect with 4-Pin Molex connector housing HY07MP504, (same as Molex part number 09-50-8041).
[image: image7.png]= 9 » 9 5 B P

My Computer Recycle Bin Word 97 Excel 97 Access'97  Powerfully  Mess Up You

L SmartLoader (Carier Proprietary) PSS REEEi
L s e
(& =35

LY = R
& 5 b
MSDOS  Outiook

ce_mail Visio 4.0 VisSim3.06  Designer 4.

sodotelt Apact
S Bobe
| B
ResPlar  EPIC

DEVENG  PENGR DEVENG  RightFAX DEC Cress TWT+ 1M
HPSMCOLOR  HPLIII HpSSl Printer




J3 pin identification is silk screened on each ComfortLink board.

[image: image8.png]



· A Navigator can be connected to the MBB by using a HY84HA096 Comm Board and a 30GT680001 wiring harness to verify configurations.  This will also allow connection of Service Tool or ComfortView.

Power Components:

· 24VAC Power Supply: Part Number 30GX680005 available from RCD. Plug type cube, 115/24VAC transformer, 450mA rated output. 

· A field supplied 24VAC transformer can also be used. Strip the leads and crimp on the Trifurcon terminal, qty 2, Carrier HY57MP008, (same as Molex 08-50-0189).

· Wire terminals as follows: Pin 1: 24 VAC, Pin 2: Ground, Pin 3: Not Used.

· Connect with 3-Pin Molex connector housing HY07MP503, (same as Molex part number 09-50-8031).
2.2 Interaction with Network Service Tool IV, Building Supervisor IV, and ComfortVIEW

SmartLoader can be installed on a computer along with Carrier's Network Service Tool IV, Building Supervisor IV, and ComfortVIEW software. These software products cannot, however, run simultaneously with SmartLoader. You can shut down Network Service Tool IV and Building Supervisor IV and launch SmartLoader without re-booting the computer. Smartloader 2.0 will automatically shutdown ComfortVIEW Services and return them to their previous state after you exit SmartLoader.

Note:
You must install SmartLoader after installation of the aforementioned software products. If, for any reason, you install any of these products after SmartLoader has been installed, you must re-install SmartLoader.

2.3 Comm Port Setup 

The LEN Bus serial port must be set to an unused serial comm port to avoid hardware conflicts. Although the baud rate is selectable in SmartLoader, all ComfortLink units are set to 38.4K baud at the factory. The baud rate selection feature can apply to future SmartLoader products with variable rates.

3.0 How to Install SmartLoader 

Note:
You must install SmartLoader after installation of Carrier's Building Supervisor IV, Network Service Tool IV, and ComfortVIEW products. If, for any reason, you install any of these products after SmartLoader has been installed, you must re-install SmartLoader.

[image: image9.png]


Before installing SmartLoader, all applications running under Windows must be closed. If you are using Windows 2000 or XP you must be logged on as an Administrator.

To install SmartLoader, place the SmartLoader CD into your computer’s CD-ROM drive. If your computer is set up for CD autoplay, the SmartLoader install program will start automatically. 

· If the CD autoplay feature is active, SmartLoader will attempt to install every time you place the SmartLoader CD into your CD drive. 

· Press the SHIFT key when you insert the CD into the CD-ROM drive to deactivate the autoplay feature.

To install SmartLoader with the autoplay feature deactivated, open the Start menu, select Run…, and type d:setup, where d is the drive letter assigned to your CD drive. 

[image: image10.png]Hardware Installation

A The sofwate you ae instling fr this hrcare

CCN Levell Commurications Part

s ot passed Windows Logo testing o veiy s compatibiy

withWindows <P. (Tell me why i tesing s mpartant

Continuing your installation of this software may impair
o destabilize the correct operation of your system
either immediately or in the future. Microsoit strongly
recommends that you stop this installation now and
contact the hardware vendor for software that has
passed Windows Logo testing.

o)





The SmartLoader welcome screen will appear followed by the Setup acknowledgement of the InstallShield Wizard as shown to the right.

3.1 Installation Welcome Screen

Once the password was been entered, the installation will proceed as shown below.

· Click “Next” to continue.

[image: image11.png]Carier model rumber:
(Complets 16-digh number equied, . 30GXN1254:660-)
[S0GTNO70E 820KA

el number:

(Complete serial number required, .. wwexyyyyy)
F19F 12346

I~File selection methad:
& Automatic
© Manual

Source diector:

R — )
Setup. Cantinue >> | Close

Foar 0200 [pasiae 00 |





3.2 User Information

[image: image12.png][SmartLoader Manual Download Browser:
Product
3061/60 040420, AL Crlers =

Revision:

[Version 4.1

ess < oK

[Version 4.1

Comfortink 30 Seies Dual Recip Chiler Software.





· Enter your name & company name.

· Click “Next” to continue.

3.3 Registration Confirmation

Your personal registration will be confirmed as shown below.

[image: image13.png]Carrier

R United Tchrcioges Company

MODEL

30GTNO70-E-620KA

SERIAL

NNNNF 12346




If acceptable:

· Click “Yes” to proceed.

3.4 Destination Drive Selection

You will be allowed to copy SmartLoader to any drive. Installation to your primary hard drive C: is suggested.

[image: image14.png][Select Database Folder
Dive [Br
TR =

Aquasniap.
Assries

recip_le
recip_2c

Souce foder
WM _image

Cancel




If you would like to install SmartLoader to a drive other than C: 

· Click the “Browse” button.

· Choose the drive & folder for the SmartLoader installation as shown below.

Note: Network installation is not recommended since the SmartLoader is intended for field download applications.

[image: image15.png]Select Database Folder
Dive: [ 3 [System - win2k]
(dh <

Program Files
{3y SmartLoader

Centuon
En_Screw

‘Souce foder:
[FFrogram Fies\martL oaderh_Image

Cancel





3.5 Operation from CD-ROM Drive

It is recommended to copy all support & unit software to your hard drive.

· Click “Yes” to copy support & unit software to your hard drive.

All SmartLoader drivers, executable & unit software files will be loaded to your hard drive.

Some users may prefer to minimize the amount of unit software on their hard drive. SmartLoader allows you to download unit software from either your hard drive or the SmartLoader CD.

If you would like to run SmartLoader from the CD-ROM drive:

· Click “No”.

· The installation will proceed to copy only the SmartLoader drivers & necessary executable files to your hard drive. Unit software will only reside on the SmartLoader CD.

· Note: the SmartLoader CD must be loaded in the CD-ROM drive for downloads to occur.

[image: image16.png]Welcome to the InstallShield Wizard for
SmartLoader

The InstalShield® Wizard il nstal SmarLoader on your
computer. To continue, cick Nex.

eiws ] _ Cancel





Appropriate files will now be copied to the destination drive as determined above. A status bar will appear as files are copies to the hard drive. 

[image: image17.png]=18
| 6o & vow Faes Ik teb |

| neck - = - (21| Quserch | Gyroiers Py | 05 B X 0|
| acress [ recp_2c =l 0w

l-"ﬁ;‘:'l_'l

01990199 01991301 DI99ZS03  DISIZS9S  DISIR603 01994139

Fokers
=01 smationdr
=00 i e
O Aaussnap recip_2c
33 hsees

20 En_screw

See ko 01995099 02040204 02041704  Productixt
1 Documerts
] 01390199 Uy Network Places
{23 01991301 My Computer ABB42935
20 01992503
20 01992599
20 01992603
20 01994199
20 01995099
{21 02040204
20 02041704
2 screw
{2 sTaGEGAS
Q:z

] Temp

10 cbject() (Dik fee space: 5.04 GB) a3 bytes

My Computer





3.6 Windows XP( Installation
[image: image18.wmf]The communications driver used by SmartLoader is not digitally signed.  By default, Microsoft Windows XP ( prevents unsigned device drivers from being installed without confirmation from the person performing the installation.  As a result, when SmartLoader is installed, the operating system displays the following warning:

In order to proceed, select Continue Anyway.  On systems containing one integrated serial port, this message will appear once.  On systems containing two integrated serial ports, this message will appear twice.  If STOP Installation is selected, a subsequent full reinstallation of SmartLoader will be required.

The level of protection provided by the operating system against unsigned device drivers is configurable.  With the strictest setting, the driver will not be installed, and there will be no option for the user to remedy this during installation.  With the least strict setting, the operating system will unconditionally allow the installation of all unsigned device drivers (no warning will be issued during installation).  With the default setting, the warning identified above is displayed, and the user is allowed to confirm the installation and proceed.

3.7 Setup Complete
Once the appropriate files have been copied to the hard drive, a SmartLoader program group will appear. This confirms that SmartLoader has been installed.

Notice: the Readme.doc file contains any last minute software notes that may be important to the operation of the program. Please read the Readme.doc file for any last minute & important program information.

See “SmartLoader 2.1 User Manual.doc” or “SmartLoader 2.1 User Manual.pdf” located on the SmartLoader CD for a copy of this manual.

Once the installation has been competed, you should restart your computer to ensure the drives & program configuration settings are established.

· Ensure  “Yes, I want to restart my computer now.” has been chosen.

· Click “Finish”.

[image: image19.png][SmartLoader Communications Setup

Commurication pott [ Baudrale

& oM 9600 baud
 tomMz

e € 19K baud
© coMg

& 34K baud

PC bus rumber (0:233):

PC element number (1-240]

Wﬁ o

Cancel





3.8 Installation Validation

Access to SmartLoader software is restricted to Carrier authorized service personnel only. This is to ensure that the proper unit software is downloaded to the equipment. Installation of the incorrect software may result in damage to the equipment and may be considered abuse. A registered password will be required before the software will proceed. The password will have to be entered only once for each PC or laptop installation.

In order to use SmartLoader, you must register your copy of the software with CSS Service Engineering support. To accomplish this:

1. Copy the Installation Serial Number that appears on the Installation Validation dialog box the first time you run Smartloader.

2. Telephone or e-mail the Installation Serial Number to CSS Service Engineering:

	Contact
	Phone 
	e-mail 

	Steve Bayes
	315-432-6067
	stephen.bayes@carrier.utc.com

	Lewis Clark
	315-432-3788
	lewis.clark@carrier.utc.com

	Chris Jones
	315-433-4751
	chris.jones@carrier.utc.com


3. Provide the following information:

· Installation Serial Number

· Your full name 

· Company name (Only Carrier distributors, CCS & Carrier Export Companies will be authorized)

· Distributor mailing address

· Your e-mail address 

4. CSS Service Engineering support will in turn give you a password.

5. Enter the password into the Installation Verification dialog box.

6. Then you will be able to use SmartLoader without the need to enter a password again.

7. You will be required to acknowledge copyright protection on the SmartLoader software.

4.0 Getting Ready to Start the SmartLoader Program

You are almost ready to use the SmartLoader. Just a few more steps:

· Ensure control power to the ComfortLink unit is ON. Unit power is not necessary unless the unit relies on a control voltage transformer to provide unit control power.

Note: All 30 Series Chillers must have the Remote/Off/Enable switch in the Off position.

· Ensure your RS-232 line powered repeater is connected to your computer’s COM port.

· Ensure an appropriate four-conductor cable with RJ11 connector is connected to the repeater.

· Connect the other end of the cable to:

· Either an appropriate ComfortLink board J3 terminal

· Or LEN RJ11 connection on the ComfortLink unit “Communication Board”

[image: image20.png]—[ofx]
File Edt View Took Help
&S00 0L ~1 ml bl g lesl@l vl Xl o
! I
:
:
SmartlLoader e A
Version 1.0 1438 B.
= 5KB D
1KB D.
S T Vet e o
1 object(s) selected 58.5K8 100 %

g start| Z Ditle..| ELotus . |[Ewpl.. B Mitos..| [lMicws..| [ QR & S H SRELL 320





[image: image21.png]SmartLoader

Version 2.1

Copytight Carrier Corporation, 2004
AlRights Reserved





[image: image22.png]



[image: image23.png]


[image: image24.wmf]

4.1 Starting SmartLoader

To start the SmartLoader program:

· Click on the SmartLoader icon from the SmartLoader program group

Or

· [image: image25.jpg]


Click the Windows( Start button & choose SmartLoader from the program list 

The following introduction screen will appear.

· Click “OK” to proceed.

· Locate the unit Model & Serial numbers.

· [image: image26.png]Choose Folder

Please chaose the instalaton foder.

Palh

Ditectories:

[ OoukCowasn 4]

{22 QuickTime.

{2 Real

{3 Rosio

=423 SmartLoader —
{2 M1_Imags

_ILIJ—I




[image: image27.png]Folder: frecip_zc.




[image: image28.png]Part Number

30GTN Controller 4.1 (MBB) 30GT515165
30GTN EXV Controller 1.2 30GT515217
Extra Unloader Board 1.2 (CXB) 30GT515219
Energy Management Module 1.1 30GT515218
Scroling Marquee Display 1.4 HKB0AA031

Model Number




The 30GTN chiller nameplate is located on the unit corner post.  

· A secondary identification label is located on the inside of the control box as show below.

[image: image29.png]uestion [
y defeut, Setup i copy the SrtLoader suppertand dta s
tothe selcte targetlocation on your ard

These fles wil consume appraximately 93450 KB M of free disk space.
I you do ot wish to copy the support and data files to your hard dsk,
you can choose to keep your StrtLoader distribution edia n s drive
in order for the SmartLoader program to access the.

0 you wish to copy the support and dat il to your arget drive?.

T




[image: image30.png]SmartLoader 2.1

number of file




[image: image31.png]SmartLoader

= Version 2.1 @

This software s licensed to

Carrier Corporation
Carrier Corporation

No watay, it expresse ot gl s given with espect o the

acouracy orhe slfcency of the lomaton rovided hereby. nd

the user mst assume al tisks and tesponsibiity in comnecton with
the use thereat

Copyight, Carier Corporaton, 2004, All ights reserved.

This program s protected by US and Inemnalional copyigh laws.




[image: image32.png]



[image: image33.png]30GTN/GUN/HK/HL SCP

Select Appropiate Mode o

Select1 o> Dovrioad Softuare ]

Select 2o - Restore factory default corfiguratons.
without dowrloading new soltware.





[image: image34.png]O Microsoft PowerPoint - [Presentationl] SEIES

/&1 Ele Edt viow Insert Farmat Tools Side Show Window tHelp JREDY
D&y e v oo & ®ilE =508 || mestewromn =

Cartier model number: (Complete 16-digit number required)
[FoGTNG70-501K,

| Searching for Target Device

T e =]

Setup. | Cantinue >> Close. |

[Poots028 [sowsiae 30

TN

=Kl | L2
|| tewsice.. sideLavout... ApplyDesion
I Side2of 4 I Dsfauk Desgn =l

Start| 5 Distler s (2] Exloing - | B Micosot .| ) smartoa.. | [@iMicisott..|[SmartLonder | |06 @, 5 [ S RE 553





· Enter the complete Model & Serial number in the fields provided. 

· Use the full model & serial numbers from the unit nameplate or secondary identification label to ensure the appropriate software is downloaded.

Note: SmartLoader will not recognize units with SPECIAL ORDER model numbers. Only base unit model number will be accepted. SPECIAL ORDER model numbers can be identified by numeric values in the 12th through 16th digits as follows:

Unrecognized SPECIAL ORDER Model Number Example

	3
	0
	G
	T
	N
	0
	7
	0
	-
	E
	-
	7
	2
	2
	9
	1

	1
	2
	3
	4
	5
	6
	7
	8
	9
	10
	11
	12
	13
	14
	15
	16


[image: image35.png][=1 % 1 < 98 2

= L7 % 2 2 2

wy Computsr  Recycle Bn W'y Beels7  Acces 7 Powertily MessUp Yo
T SmartLoader (Carrier Proprietary) X RS Ey (el

o Y e = 23
MSDOS Outiook ARNING: data

VisSim 300 Designer 4.

e

Basics Explare The new program willuse the curent configurations i possibl, or willset all configuratons
st L
feapae EIC

¢ ¢ ¢ € H H L

DEVENG  PENGR DEVENG  RightFAX DEC Cress TWT+ 1M
food  HPSMCOLOR  HPLTI HpSSl Printer





[image: image36.png]J3

ODE mr

-} DL~

- CD‘)r‘ GHp=

G}»— RED

Phone Cable RJ11

1 LEN+
2 LENcomm
3 LEN-
4 (Not Used)

Yellow

Green

Black
(Not Used)




[image: image37.png]Installshield wizard

Customer Information
Flease enter yourinformation.

Please enter yout name and the name of the companyfor whom you wark.

User Nae:

Company Neme:

[Computer Sciences Corparation

InsalSHeld

<Back Next> Cancel





[image: image38.png]Yo have provided the following regstaton iformator:
Name: Windows 2000 User

Company: Computer Sciences Corparation

Is this registaton informaton corect?




[image: image39.png]g

iy Computer

big
s
we00s

(‘)

Bookshelf
Basics

=

RealPlayer

Te=t
Netwark
‘hood

e

Recycke Bin

o

Outiaak

Aspect
Explare

L

EPIC

¢

DEVENG
HPSM COLOR

ce_mail

Field Failure
Reports

Netscape

9 ¥y g B B

Word 97 Excel 97 Access'97  Powerfully  Mess Up You
Pointiess 97 Project 4.0

I =

Visi40  Vissim3.00 Designer 4.

el rum g uied, e, weF i)
B 5061 /Hw rev 1.0 SCP. ] ﬂ*
Factory
Downloater

DEVENG  RIghtFAX DEC Cress TWT+
HpSSl Printer



[image: image40.png]Installshield wizard

Choose Destination Lacation
Selectfolder where Setup villinstal fes.

Setup wil nstall Smartoader n the foloving folder.

To nstall 1o tis folder, lick Newt. To instal to adifeent folder, cick Browse and select
anather folder.

C:\Program FlestSmatLoader Browse.

InsalSHeld

"Deshnahan Folder

<ok [[THes | Concel





[image: image41.png]Installshield wizard

)

InstaliShield Wizard Complete

The InstalShield Wizard has suscessfuly installed
SmartLoader. Before you can use the program, you st
festatt your computer

@ a5 Twant 1o estar my compie: now!
€ No,l willstatt my computer lter.

Remove any disks from thei dives, and then click Firish to
complete setup.

Fiish




[image: image42.png]Part Number

V/ [80GTN Controller 4.1 (MBE)

seloct

:

30GT515165
30GTN EXV Controller 1.2 30GT515217
Extra Unloader Board 1.2 (CXB) 30GT515219
Energy Management Module 1.1 30GT515218
Scroling Marquee Display 1.4 HKB0AA031

Model Number
[Svtinoro-E-ore n cance





OR

[image: image43.png]30GTN/GUN/HK/HL SCP

° Target: 30T Controller 4.1 (M6B)

The program being downlaaded ncludes configuration setting. The settings currently inthe targe board can be:
used by the program being downlosded.

Press YES to keep the current configurations
Press NO to set all configurations o theirdefault valuss,

Keep current configurations ?




[image: image44.png]30GTN/GUN/HK/HL SCP

The target board for
"30GTH Contraller 4.1 (MEE)"
is currently runming a diferent application.

0 you want to proceed with the downioad?





[image: image45.png]30GTN/GUN/HK/HL SCP

The target board for *30GTH Cortrolr 2.2 (MEE)"
Is running a more recent versin of the application

you have selected to download.

0 you really want to downlosd the older version?





4.2 Choose File Selection Method

There are two modes possible for file selection, Automatic and Manual. 

When running in the Automatic mode, SmartLoader searches the “M1_Image” database for download files corresponding to the model number and serial number entered by the user. The latest compatible revision of download files for a board set is used. 

[image: image46.png][Download to dey

Downloading MBB_0401 HEX

e at address 0, 1

Bytes downloaded: 60032 More>>




Manual mode allows a user to select download files from a Product folder, as well as a Revision level. While not typically used, Manual file selection allows an experienced user to revert back to older versions of download files if necessary.

The Automatic file selection method is recommended to ensure the latest unit software is selected & downloaded. 
If you would like SmartLoader to automatically locate the appropriate unit software:

· [image: image47.png][Download to device at address 0, 1

Device download complete

Bytes downloaded: 372411

Dowrload log
VARIABLE HSP_B SET T0 113
WAIT DELAY: 0

[Reseting Systern
DESTINATION ADDRESS SETTO 0,1
VARIABLE RESETDEY SETTO 1
WAIT DELAY: 0
SUCCESSFUL DOWNLOAD




Click on Automatic file selection method.

The Manual file selection method is convenient if you desire to download a previous version of the software from your hard drive or from the SmartLoader CD. 

· [image: image48.png]COULDN'T LOCATE the 30GTN Controller 4.1
(MBB)

Press 'CANCEL' to abort the download
Press 'ERASE BOARD INFO.' to re-initialize the
board. Keep in mind

the current board configurations WILL BE
LOST.

ERASE BOARD
CANCEL INFO




Click on Manual and then “Continue>>” to direct SmartLoader to the desired software revision. The revision can be selected by clicking on the “Revision” drop down list.

· Click on the “More >>” button to see any related notes regarding the software release as shown to the right.

· Click on “Less <<” to hide these notes.

· Click on “OK” once the desired software package has been selected.

4.3 Select Database Folder

SmartLoader can be directed to find the unit software database on your hard drive or SmartLoader CD. 

· Click on “…” to select the source directory.


If you elected to run SmartLoader from the CD-ROM, you will have to choose the CD-ROM drive from the “Select Database Folder” menu. 


However, if you installed the unit software database files to your hard drive, you will have to select the database folder from that drive. An example for a C: installation is shown to the right.

4.4 File Directory Structure

The SmartLoader assumes that a CD or hard disk is used to store controlled versions of downloadable code files and command files.  The file structure consists of a database folder that in turn consists of product folders that contain dated subdirectories, or dated folders.  These dated folders are of the format AABBXXYY where AABB determines the compatible date (AA=week of year, BB=year) and XXYY determines the effective date (XX=week of year, YY=year).  Each dated folder contains the downloadable code files and command files for the unit.  The serial number of the unit determines which version will be downloaded to the unit (which dated subdirectory will be used).

An example of the M1_Image folder directory structure is shown below.  


4.5 Communications Setup

SmartLoader can be directed to configure the computer’s communication hardware. Click on the “Setup…” button from the SmartLoader screen to launch the Communications Setup screen. The host LEN network address is also configured here. You only have to run the setup once. These settings are stored for future use when SmartLoader is closed. 

By using radio buttons, the PC serial port can be selected. Choose from Com1, Com2, Com3, and Com4. 

Note: 
If the wrong serial port is selected, or if there is a hardware conflict with another PC device, an error message will result.

4.6 Baud Rate

The baud rate may be selected by clicking the appropriate radio button.  The baud rate selections are 9600, 19200, and 38400 baud.

Note: 
For M1 boards, the configuration program that SmartLoader executes prior to a download automatically resets the baud rate to 38400 baud, regardless of the user’s selection. The baud rate selection feature is provided for thefuture expandability of SmartLoader.

4.7 Set PC Address

PC element number and bus number may be set with the spin buttons or typed into the text box.  The allowable entries for the PC element number are 0-240 and the allowable entries for bus number are 0-239. PC element number 240 is recommended.

4.8 Continue to Download

Once the above configuration choices have been entered, 

· Click the “Continue >>” button to allow SmartLoader to search for the specific unit software database.

· Once the specific unit database has been located, SmartLoader will allow you the option to download the software or restore the configuration parameters to the factory defaults.

· After you make your selection SmartLoader will proceed to the SmartLoader board selection screen as described in Section 5.0.



5.0 Performing a Download

You are now ready to choose the specific board to download. 
SmartLoader will show you the ComfortLink boards associated with the model number & serial number unit entered in the previous menu.

An example of a 30GTN070 using a version 4.1 controller (MBB) & all related ComfortLink boards are shown to the right. 

5.1 Select Board to Download

You will now choose the ComfortLink boards to download. 

· Click on the “select” button to choose the board(s) to download.

· If you want to download all boards, click all “select” buttons. Note: All boards listed may not be present in the unit. Verify that boards selected are actually in the unit.

Notice a ( mark will appear next to the board selected as shown to the right.

· You may deselect any board by clicking on the “select” button again.

· Click on the “OK” button to allow SmartLoader to download to the selected boards.

5.2 Download in Process

SmartLoader will now search for the board(s). These are referred to as “Target Devices” as shown below. 


SmartLoader will tell you its progress as it searches for the appropriate unit software. If this warning is displayed Smartloader cannot communicate with the Comfortlink board. Check all connections. Verify operation of RS485 converter. Selecting ERASE BOARD INFO. will completely erase the application software and make the unit inoperable.    

5.3 Existing Software Configuration Confirmation

SmartLoader will attempt to preserve the unit’s existing software configuration to minimize reconfiguration during unit startup. Once the existing configuration is determined, SmartLoader will establish the best way to preserve the configurations. There are three (3) potential configuration confirmations:
1. All existing configurations can be saved.

2. SmartLoader can not verify configuration status.

3. SmartLoader can not save existing configurations.

5.3.1 All Existing Configurations Can Be Saved

If SmartLoader can save all existing configurations, the following message will be displayed: 

· Pressing the “Cancel” button will abort the download and return to the SmartLoader data entry screen for any of the following messages.

5.3.2 Configurations Can Not Be Verified

If the new unit software contains new configuration settings, SmartLoader will not be able to determine if the existing configurations can be saved. The following will be displayed if this scenario exists. 

5.3.3 Configurations Can Not Be Saved

The new unit software may contain entirely new configuration setting requirements. As a result, SmartLoader will not be able to preserve any of the existing configuration settings. This scenario will reset all configurations to the default values.

5.4 Potential Download Errors
SmartLoader will recognize errors that could be encountered during the download. All are intended to prevent accidental download of inappropriate software into a unit or download when the machine has not been adequately shut down.

An example of the most likely error message is shown below.  This error message indicates the target board is running an application different that what you attempted to download. Make sure you have entered the correct Model and Serial number.


This error message indicates that you are about to download an older version of software then currently resides in the board. Verify that you have selected the correct software version.

5.5 Download Continuation

SmartLoader will advise you of its progress as the unit software is downloaded.


· Click on the “More >>” button to view details of the download event. 
An example of this information is shown to the right.

Notice: A download log is presented to show the status of the download event.

At this point the download is complete!

· Click “OK” to return to the SmartLoader input screen to download another unit or ComfortLink board.
6.0 Uninstalling Smartloader

SmartLoader can be removed from your PC if necessary.

Note:
If, in error, you installed ComfortVIEW, Building Supervisor IV, or Network Service Tool IV after installing SmartLoader, the removal of SmartLoader will adversely affect the operation of these other Carrier products. In this case, after you uninstall SmartLoader, you must re-install the Carrier product(s) you wish to retain.

6.1 To Uninstall SmartLoader

1. Open the Start menu.

2. Choose Settings.

3. Choose Control Panel.

4. Double click on Add/Remove Programs.

5. Click the top tab that says Install/Uninstall.

6. Select SmartLoader.

7. Click the Add/Remove button.

8. Click Yes to confirm that you want to delete SmartLoader.

9. If a dialog box entitled Remove Shared File? is displayed, click No to All.

10. You may receive a message indicating that some elements could not be removed. Clicks on Details to identify which folders remain. You can delete your SmartLoader folder manually via Windows Explorer. DO NOT remove anything in a Carrier Shared directory.

11. Click OK to exit from the Remove Programs From Your Computer dialog box and you are done.

7.0 Technical Support

SmartLoader Installation & Operation Support:

Installation and Startup questions and the ability to communicate to the equipment from the SmartLoader, please contact, CSS Support, at:

TEL: 860-674-3067 or 800-277-9852

ComfortLink Unit or Control Support:

For problems relating to ComfortLink software, problems downloading to ComfortLink products or other product service inquiries, please contact CSS Service Engineering at: 

TEL: 315-432-6067 or 315-432-3788

8.0 Troubleshooting 

Further assistance is available by contacting CSS at the Technical Support numbers shown above.







Patch Cable, Male-to-male RJ11





B&B Line Powered Repeater





� EMBED Unknown  ���





� EMBED MSPhotoEd.3  ���

















30GTN Secondary Identification Label





“Comm Board” LEN RJ11 connection point





� EMBED Unknown  ���





J3 for communication. Main Base Board (MBB) shown. 





� EMBED Word.Document.8 \s ���





� EMBED Word.Document.8 \s ���





CAUTION: Do not connect into the CCN RJ11 on the ComfortLink unit or any non-ComfortLink RJ11 connector. Only ComfortLink units or ComfortLink boards can be downloaded with SmartLoader.  30GTN chiller connection location example is shown below.





To RJ11 connector





Download through LEN connection ONLY!





Patch Cable,  30GX680004











30GTN Nameplate Example

































































J1 for 24VAC power. Wire as follows:


Pin 1: 24VAC


Pin 2: Ground


Pin 3: Not Used














Power Supply, 30GX680005





Patch Cable Wiring








� EMBED MSPhotoEd.3  ���








B&B Line Powered Repeater














ComfortLink Communication Board











16
How to Use the SmartLoader

February 2005

15
How to Use the SmartLoader

February 2005


_1003738901

_1004519599.bin

_1005570077.bin

_1003578509.doc
[image: image1.png]. Carrier 30GTNO70-E~620KA
‘A United Technologies Company NNNNF 12346 ®

MODEL 30GTNO70-E-620KA ]SERIAL NNNNF 12346 ’ FACTORY CHARGED
ary]  voursac  [pH| Hz RLA LRA BEFRIC/ RS 22
compP| 1 460 3 |60 65. 4 345 70 1Bs 3.8 g
COMP| 1 460 3 |60 65. 4 345 69 Les 31.3 g
coMP
DESIGN / TESTPRESSURE GAGE[ HIGH [PSI 450 |WPa 3102]LOW[PSI 278 [kPa 1917
FAN MOTORS[aTY] VOLTS AC PH] HZ FLA HP kW ouT
OUTDOOR |4 460 3 [60 3.3 2.0 s
OUTDOOR |2 460 3 [60 2.8 Nz 1.2
OTHER
HEATERS TOTAL PRLTSUITABLE FOR OUTDOOR USE
) 50 o] 3 pu] B0 o] CRCUT Aurs| o
G T 506 MAX 414 mIN[1 166.C o
BONERSuppLy 115 VOLTST 1 PHIEG HZ PO AMPS| 2 e

MADE INUSA. TLF (CHARGE SYSTEM PER INSTALLATION INSTRUCTIONS 99NA504514 E @








_1003579068.doc
[image: image1.png]. Carrier 30GTNO70-E~620KA
‘A United Technologies Company NNNNF 12346 ®

MODEL 30GTNO70-E-620KA ]SERIAL NNNNF 12346 ’ FACTORY CHARGED
ary]  voursac  [pH| Hz RLA LRA BEFRIC/ RS 22
compP| 1 460 3 |60 65. 4 345 70 1Bs 3.8 g
COMP| 1 460 3 |60 65. 4 345 69 Les 31.3 g
coMP
DESIGN / TESTPRESSURE GAGE[ HIGH [PSI 450 |WPa 3102]LOW[PSI 278 [kPa 1917
FAN MOTORS[aTY] VOLTS AC PH] HZ FLA HP kW ouT
OUTDOOR |4 460 3 [60 3.3 2.0 s
OUTDOOR |2 460 3 [60 2.8 Nz 1.2
OTHER
HEATERS TOTAL PRLTSUITABLE FOR OUTDOOR USE
) 50 o] 3 pu] B0 o] CRCUT Aurs| o
G T 506 MAX 414 mIN[1 166.C o
BONERSuppLy 115 VOLTST 1 PHIEG HZ PO AMPS| 2 e

MADE INUSA. TLF (CHARGE SYSTEM PER INSTALLATION INSTRUCTIONS 99NA504514 E @








_1003337079

