COMPRESSOR/COMPONENT WEIGHTS                                           Revision Date 03/21/01
Unit

Type
Unit/

Comp 

Size

60HZ
Unit/

Comp 

Size

50HZ
Econo

Mizer

(Std. Less free cooling)
Suction Elbow
1st Stage Inlet 

Vane
1st 

Stage

Suction Cover
Impellers

All

Stages
2nd
Stage

Alum. Vane Plate
2nd
Stage 

Casing
3rd
Stage

Alum.

Vane

Plate
2nd or 3rd
Stage

Inlet Vanes &

Plate
3rd
Stage

Casing
Steel   Volute Diffuser

Plate
Discharge 

Volute
Complete

Compressor

Including

Motor

CVHE
016-020


016-020
300 lbs.
203 lbs.
200 lbs.
715 lbs.
37 lbs.
90 lbs.
820 lbs.
90 lbs.
70 lbs.
768 lbs.
162 lbs.
800 lbs.
5665 lbs.

CVHE
023-032

230-320
023-032

190-270
385 lbs.
266 lbs.
240 lbs.
1008 lbs.
42 lbs.
115 lbs.
719 lbs.
115 lbs.
76 lbs.
742 lbs.
162 lbs.
793 lbs.
 6880 lbs.

CVHE
036-050

360-500
036-050

300-420
700 lbs.
310 lbs.
270 lbs.
1050 lbs.
42 lbs.
130 lbs.
875 lbs.
130 lbs.
82 lbs.
775 lbs.
162 lbs.
910 lbs.
7300 lbs.

CVHE
056-080

560-800
056-080

470-660
840 lbs.
494 lbs.
300 lbs.
1145 lbs.
47 lbs.
140 lbs.
1132 lbs.
140 lbs.
88 lbs.
880 lbs.
232 lbs.
1110 lbs.
9175 lbs.

CVHE
089-125

890-1250
089-125

740-1040
1280 lbs
706 lbs. 
350 lbs.
1285 lbs.
47 lbs.
150 lbs.
1257 lbs.
150 lbs.
93 lbs.
1200 lbs.
346 lbs.
1608 lbs.
11125 lbs.


















CVHG
N/A
480-565
930 lbs.
494 lbs.
311 lbs.
1740 lbs.
64 lbs.
190 lbs.
1840 lbs.
190 lbs.
82 lbs.
1840 lbs.


356 lbs.
1418 lbs.


9360 lbs.

CVHG


N/A
670-780
1365 lbs.
688 lbs.
408 lbs.


1690 lbs.           
68 lbs.
190 lbs.
1990 lbs.
190 lbs.
88 lbs.
1920 lbs.


309 lbs.
1430 lbs.


10360 lbs.

CVHG


N/A
920-1067
1365 lbs.
688 lbs.
425 lbs.
1718 lbs.
72 lbs.
190 lbs.
2010 lbs.


190 lbs.
93 lbs.
1920 lbs.


309 lbs.
1820 lbs.


11160 lbs.


















CVHF
350-485
N/A
700 lbs.
494 lbs.
295 lbs.
1400 lbs.
64 lbs.
190 lbs.


1400 lbs.


N/A
82 lbs.
N/A
289 lbs.
1336 lbs.


7610 lbs.

CVHF


555-640
N/A
700 lbs.
494 lbs.
311 lbs.


1740 lbs.


64 lbs.
190 lbs.


1840 lbs.


N/A
88 lbs.
N/A
356 lbs.
1418 lbs.


8230 lbs.

CVHF


650-910 
N/A
836 lbs.
688 lbs.
408 lbs.


1690 lbs.
70 lbs.
190 lbs.


1990 lbs.


N/A
88 lbs.
N/A
309 lbs.
1430 lbs.


9200 lbs.

CVHF


1060-1280
N/A
836 lbs.
688 lbs.
425 lbs.
1718 lbs.


70 lbs.
190 lbs.


2010 lbs.


N/A
93 lbs.
N/A
309 lbs.
1820 lbs.


9800 lbs.

CVHF ext. cap.
1470-1720
N/A
836 lbs.
1000 lbs.
750 lbs.


2133 lbs.


100 lbs. 


290 lbs.


2210 lbs.


N/A
300 lbs.
N/A
712 lbs. 
2250 lbs.


13120 lbs.



CDHF*
1500
N/A
836 lbs.
688 lbs.
Size CVHF 770 See Compressor

See Compressor Size CVHF 910

See Compressor Size CVHF 1060

See Compressor Size CVHF 1280

CDHF *
2000
N/A
836 lbs.
688 lbs.


CDHF*
2100
N/A
836 lbs.
688 lbs.


CDHF*
2500
N/A
836 lbs.
688 lbs.




CDHG*
N/A
1250
1365 lbs.
1078 lbs.
See Compressor Size CVHG  670

See Compressor Size CVHG 780

See Compressor Size CVHG 1067

CDHG*
N/A
1750
1365 lbs.
1078 lbs.


CDHG*
N/A
2150
1365 lbs.
1343 lbs.


· Duplex Units. Suction elbow weight  for each compressor. 

