
Frick Compressor Control Panel 


Operators Manual
- 2 -

     [image: image1.jpg]ud YORK Process Systems

A JOHNSON CONTROLS COMPANY




REFRIGERATION CONTROL PANEL

OPERATING PROCEDURES
[image: image2.png]



FRICK COMPANY

100 CV AVENUE P.O. BOX 997

WAYNESBORO, PA 17268-0997

PHONE (717-762-2121)

1. TABLE OF CONTENTS

21.
TABLE OF CONTENTS

2.
CONTROL PANEL OVERVIEW
4
Introduction and Purpose
4
Equipment Settings Grid
4
Recommended Spare Parts List
4
Common Control Panel Equipment
5
Bently Nevada Vibration Monitoring System
5
SPA2 Module
7
HOA Switches
7
Indicator Lights
7
Pushbuttons
7
PLC Rack
7
3.
GETTING STARTED
9
Navigating the Operator Interface
9
JCI Operator Interface Menu System
9
Standard Screen Layout and Contents
10
I/P-PID Control Menu Button
10
Status Screens Menu Button
10
Alarms / Setpoints Menu Button
10
I/O Status Menu Button
10
System Trending Menu Button
11
System Setup Menu Button
11
Login / Security Menu Button
11
Current User Indicator
11
Alarm Status Indicator
11
Screen Name Display
12
Common Colors
12
Common Terms
12
Setpoint Entry Boxes
12
Value Display Boxes
13
User Action Buttons
13
Setpoint Security System
13
Logging In and Logging Out
13
Changing User Passwords
14
User Level Security
14
4.
STATUS SCREENS
15
System Overview Screens
15
I/O Status Display
16
Compressor Status
16
Comp / Gear Aux Oil Pump Status
16
Modulating Valves
17
Transmitter Indicator
17
SyncFault (Suction Pressure)
18
Digital Indicators
18
Quick Link Buttons
19
Motor Indicators & Alarms
19
System Status Indicator
19
PRV Overrides Indicator
20
Start Permissives (Compressor Summary Screen)
20
Phase 1 Start Sequence Permissives
20
Phase 2 Compressor Start Initiate
20
Phase 3 Oil Pressure Interlocks
21
Phase 4 Compressor Motor Start
21
Electric Motor Inhibits and Runtimes
21
Motor Current Setpoints
21
Motor Runtimes
22
2 Minute Delay
22
Hot Start Delay
22
Cold Start Delay (24 Hour Inhibit)
22
Start Times in Last 24 Hours
22
Actual Motor Amps
22
FLA Setpoint
22
Actual FLA %
22
Stop Load
22
Force Unload
22
Number of Starts
22
Runtimes
22
Date and Time of Compressor Start
22
5.
PID SCREENS
23
PID Setpoints
23
List of PID Loops
23
PID Loop Setpoints
23
Actual PV
23
Setpoint SP
23
Gain
23
Reset TI
24
Range
24
Output CV
24
Manual / Auto Valve Control
24
Mode Change Bumpless Transition Operation
24
Valve Modes Of Operation
24
Command Position
25
PRV Capacity Control
25
PRV Overrides Indicator
25
Startup Setpoint
26
Discharge Pressure Override
26
Override Comparator
26
Sync Fault
26
6.
I/O Status Screens
27
Digital Inputs and Digital Outputs
27
Analog Inputs
28
Scale Min and Scale Max
28
RTD Inputs
29
Analog Outputs
30
7.
ALARM SCREENS
31
Alarm Setpoint Entry Screens
31
Alarm Navigation Box
32
Alarm Silence and Alarm Reset Buttons
33
New Alarm Banner
33
Active Alarms
34
Alarms History
35
First Out / Freeze
36
Freeze Screens
36
8.
TRENDING SCREENS
37
Purpose of Trending
37
Trending Screen
37
Pen Color Assignment Chart
37
Pen Scale Increase / Decrease Buttons
37
Trend Control Buttons
37
9.
SETUP SCREENS - Commissioning
38
HMI Display Setup
38
Screen Protector
38
PLC Date and Time Setup
38
PanelView Plus Panel Configuration
38
AOP Setpoints
39
Overview of AOP control
39
Compressor AOP Setpoints
39
Gear AOP Setpoints
40
Setup Page 1
41
PRV Constants Setup
41
Surge Control Setup
42
Misc. Control Setup
42
Setup Page 2
43
Rate of Change Filters
43
Slow Suction Pulldown
43
Setup Page 3
44
Sump Temp Permissive
44
Bently Trip Multiplier
44
Alarm / Shutdown Warning
44
Suction Pressure ATL or Soft Start
45
Setup Page 4
46
Action
46
Direction
46
Rate of Change Filters
46
Operating Minimum
46
Mtr Current Unload Bias
46
HGVF Output Disable
47
Setup Page 5
47
Suction
47
Stage 2 & 3
47
Surge Bias
47
10.
MODBUS DCS ADDRESSING
48
Modbus Port Settings and Connection
48


2. CONTROL PANEL OVERVIEW
Introduction and Purpose
The compressor is controlled by an Allen-Bradley processor, hereafter referred to as the controller or PLC.  The controller continuously monitors compressor and system conditions and operation.  This manual explains how the controller is used to control the refrigeration system.
Operator interface is through a PanelView-Plus 1000 or 1250 Color, Touch Screen Operator Interface located on the front of the control panel.  The interface is used for system monitoring, history, manual PID loop control, trending, and setpoint entry.
Equipment Settings Grid

Appendix A of this manual contains a list of supplied equipment settings including modbus protocols
Recommended Spare Parts List

Recommended Spare Parts lists are provided on request.  Typical recommended spare parts would include:

· Circuit Breakers

· Fuses

· SPA2 Module

· Analog Input Module

· Analog Output Module

· RTD Input Module

· Discrete Input Module

· Discrete Output Module

· Power Supply

· Relay and Base

Please contact your Johnson Controls or York Process Systems Sales Representative to request a recommended spare parts list.  Contact information can be found on the internet at www.jci.com or by calling Frick at (800)-ITSCOLD.
Common Control Panel Equipment
NOTE:  The following equipment descriptions are for most refrigeration control panels.  Projects with special requirements may or may not include the equipment listed.

Bently Nevada Vibration Monitoring System

· Display – The HMI has custom screens for monitoring the Bently.  The Bently display content is automatically generated from the rack configuration and setpoints entered using the Bently Nevada Rack Configuration software.  The display communicates to the Bently Nevada Rack with Modbus through the Prosoft card in slot 2 of the AB rack.
[image: image3.png]Bently Nevada 1~ CEERE [Fo 7] o
Wils set in Bertly
Reading Alert Danger

S @ shatindvibrationx | 002 Mils [ 200 240 mis
e @ hatndvibrationy | 002 Mils [ 200 240 mis
ameesor Sump Ena viragon | 002 Mils [ 200 [ 240 wils
T SumpEnd vibrationy | 002 Mils [ 200 240 i
e N3 002 Mis | 1.00 150 | mils
Ty 002 mis [ 1.00 150 | mils
T e ST 002 mis [ 1.00 150 | mils
e 002 mis [ 1.00 150 | mils
KA dvirationx | 002 Wil [ 250 400 Mils
ARG adiatvirationy | 003 Wils [ 250 400  Miis
AN radiovirationx| 002 Mils [ 250 400  Miis

d End Radial Vibration Y 0.03  Mils 250 400  Mils

d End Radial Vibration X 0.02  Mils 250 400  Mils

d End Radial Vibration Y 0.03  Mils 250 400  Mils
AR radiatvirationx | 002 Mils [ 250 400  Miis
Gem e £t End Racil vibratony | 0021 2.50

Alarms & 0 Trending System

Setpoints Status and Bently Setup




[image: image4.png]Fcte: Al GURRENT USER:
et n ety
0 2 4 6 8 tgs
S S A S — Reading Alert
Xe2tas0 . .
Gear LS Shatt Acceterometer | 001 |95 EOORNE
"E‘I“DS Reading
50 &0 YEA231APO Display Only) [tz 12
100 100 Compressor Axal Thrust -15.13 | Mils
Xe1231AP1 528 i
-150 150 Compressor Axial Thrust -15.26 | Mils
200 200 Danger  Alert Alet  Danger
Lo Lo HI HI
250 250 -20.00 -17.00  Mils 5.00 10.00  Mils
ete
PR ——
Xe1231AK1
0.00  RPM |Upper RPM Limit

Compressor Keyphasor Prabe e oL 4
erty
ete

, e {Tweshotttype - o
Gear L3 ShttKeyphasr Probe 0,00 RPH (s e L 1500

i Setup is done in

ertly

1P - PID s

Control Screens

Alarms &

Trending System

Setpoints and Bently Setup





[image: image5.png]Fcte: Al
| Bently Nevada 3 o | Ve

0 60 120 180 240  300°F set inBently
Reading Alert Danger

000 o (68589 ¢ [22500 23909 [
Bl 000 i (6599 ¢ [22500 2399 [

B . .
d-End Bearing RTD 6599 °F 225.00 239.99 °F
B

== . )
I — SR — o5se r | 22500 || 23889 °F

e : -
Bl e cwmenmonm | 6800 7 [ 19939 [ 22000 'F

T . )
Bl e cneom| 6900 ¢ [ 19999 [ 22000 |'F

TEAZ31AZIA g
Hl 0000 ] e eeasemen 6500 °F [ 20300 [ 21200 °F
| I [ e 699 |'F [ 20300 [ 21200 F
nc-End Bearing RTD 5 X _

TEARstAZSD . .
[ Motor ShaftEnd Bearing RTD 6300 °F | 20300 | 21200 °F
[ | Mot Bl End Bearing KTD 6599 °F [ 20300 |[ 21200 °F

Alarms & 0 Trending System

Setpoints Status and Bently Setup




· Rack Interface Module – This module is used for uploading / downloading / monitoring of the Bently Nevada system using the Bently Nevada Configuration Software.  A laptop running the Rack Configuration software can communicate to the Rack using a standard RS232 cable (Null Modem).  
· Relay Module – This module is used to control the PLC interlocking signals.
· Proximotor Module – Monitors the vibration transducers mounted on the compressor or motor.  
· Keyphasor Module – Monitors the keyphasors.
· RTD Module – Monitors compressor, gear, and motor mounted RTD’s.
· Communication Gateway Module – Transfers Bently Nevada equipment status to the PLC using Modbus protocol.
SPA2 Module

The SPA or Site Programmable Alarm module is used for safety backup of transmitter data.  The SPA2 module monitors a 4-20mA signal.  When the signal falls above or below an alarm threshold, then a contact opens inside the SPA module which will cause the compressor to go into a shutdown condition.
SPA2 modules are commonly used to monitor Discharge High Pressure and Compressor Journal Bearing Inlet Low Differential Pressure.  SPA modules can also be used to retransmit a 4-20mA signal. SPA2 series module setpoints can be monitored and changed through a RS232 interface on the front of the module with the Moore Industries (www.miinet.com) SPA2 Configuration Software.
HOA Switches

The following are a list of standard HOA switches located on the electrical control panel:
· Compressor Aux Oil Pump (Auto / Manual) – When in the Auto position, the PLC controls the oil pump.  When in the Manual position, the pump will turn on immediately and run until the selector switch is returned to the auto position.

· Gear Aux Oil Pump (Auto / Manual) – When in the Auto position, the PLC controls the oil pump.  When in the Manual position, the pump will turn on immediately and run until the selector switch is returned to the auto position.
Indicator Lights
The following are a list of standard indicator lights that are located on the electrical control panel:
· Compressor AOP Running – The compressor AOP running light is an indicator of the status of the auxiliary input for the motor.  The indicator is illuminated when the auxiliary input to the controller is energized.
· Gear AOP Running – The compressor AOP running light is an indicator of the status of the auxiliary input for the motor.  The indicator is illuminated when the auxiliary input to the controller is energized.

· Compressor Running – The compressor running light is an indicator of the status of the auxiliary input for the motor.  The indicator is illuminated when the auxiliary input to the controller is energized.

Pushbuttons

The following pushbuttons are located on the control cabinet door.

· Compressor Start – Press to locally start the compressor.  Please refer to the System Startup Procedures before pressing this button.
· Compressor Stop - Press to locally stop the compressor.  Please refer to the System Shutdown Procedures before pressing this button.
· Emergency Stop – Pull to immediately shutdown the compressor.  Push to unlatch and allow the operator to restart the compressor.
PLC Rack

The following are a list of modules that can be found mounted in the PLC rack.

· Power Supply – The power supply is used to supply power to the PLC backplane for use by the PLC cards.
· Processor – The PLC processor is the “decision making unit” and is generally referred to as the controller. This system utilizes the 1756-L61 CPU. The PLC program is loaded into the processor via RS232 or Ethernet interface.  The processor scans the status of the I/O cards and sends command signals to the outputs.
· Analog Input Card – Analog input cards monitor the 4-20mA signals supplied from transmitter devices.  The transmitter devices, typically Rosemount or similar, can be compressor mounted, package mounted, or from customer supplied equipment panels.  Examples of typical 4-20mA analog inputs would be pressures, levels, motor current, and in some cases temperatures.
· Analog Output Card – Analog output cards supply a variable 4-20mA control signal to modulating valves (typically Fisher or Hanson style) and variable frequency drives.  Example of typical 4-20mA analog outputs would be PRV position control, pressure control valves, level control valves, and temperature control valves.
· Discrete Input – Discrete input cards monitor the 120VAC or 24VDC signal supplied from a discrete switch or contact.  Discrete devices are those that have an on or off state.  Example of discrete input devices would be a level switches, pressure switches, thermostats, and auxiliary contacts.
· Discrete Output – Discrete output cards are used to control 24VDC or 120VAC devices.  Examples of discrete output devices would be solenoids and relays. 
· RTD Module – RTD input cards monitor the temperature of an RTD (resistive temperature device).
· Ethernet Module – The Ethernet card is used for downloading a PLC program into the PLC processor, monitoring the PLC status via laptop, monitoring the system status via PanelView plus, and for DCS communications.  A category 5 (Cat-5) cable connects the Ethernet card to a switch for interface with all Ethernet compatible devices on the system.    
· ProSoft Modbus Module – A ProSoft Modbus Card ( 1756-MNETR) is used to connect modbus capable devices to the PLC.  The ProSoft configuration is handled by the PLC program & the Prosoft Configuration Builder Program (www.prosoft-technology.com).  The ProSoft Modbus module is used to monitor Bently Nevada vibration information and can also be used for DCS communications.
3. GETTING STARTED

Navigating the Operator Interface

[image: image6.jpg]



Figure 1 PanelView Plus 1250 Operator Interface (HMI)
All navigation is performed using the touch sensitive screen.
JCI Operator Interface Menu System

The JCI Operator Menu Interface is laid out so the operator can easily navigate from one screen to another without getting lost or having to navigate through a series of menus.  The main menu is mapped across the bottom of the screen.  Touching a menu button will bring up a list of screens within that submenu.  To close a submenu popup screen simply click on the “Close Menu” button.  

The Main Menu consists of the following submenu popup screens:
· System Overview

· I/P-PID Control

· Status Screens

· Alarms & Setpoints

· I/O Status

· System Trending & Bently
· System Setup

· Login / Language

The following section provides a detailed description of the submenu screens.
Standard Screen Layout and Contents
[image: image7.png]Alarms History CURRENT USER:

DEFAULT

Alarm time.

11/16/2009 10:45:35 PM  PDT-1231A7 Stage 2 Strainer Dff Pressure - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  PDT-123148 Stage 1 Suction Strainer Diff Pressure - Transmitter Out of Range Alaim
11/16/2009 10:45:35 PM  HIT-1231A16 Comp Discharge Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A10 Stage 1 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A12 Stage 3 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A15 Stage 3 Upstream Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A11 Stage 2 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A14 Stage 2 Upstream Block Valve Position - Transrmitter Out of Range Alarm

11/16/2009 10:45:35 PM  HZT-1231A13 Stage 1 Block Valve Position - Transrmitter Out of Range Alarm

First Out/
Freeze Menu

System P .PID s Alarms & 0 Trending System

Overview Control Screens  Setpoints Status and Bently Setup




Figure 2 Topbar for the Alarms History Screen

[image: image8.png]Alarms History CURRENT USER:

DEFAULT

Alarm time.

11/16/2009 10:45:35 PM  PDT-1231A7 Stage 2 Strainer Dff Pressure - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  PDT-123148 Stage 1 Suction Strainer Diff Pressure - Transmitter Out of Range Alaim
11/16/2009 10:45:35 PM  HIT-1231A16 Comp Discharge Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A10 Stage 1 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A12 Stage 3 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A15 Stage 3 Upstream Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A11 Stage 2 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A14 Stage 2 Upstream Block Valve Position - Transrmitter Out of Range Alarm

11/16/2009 10:45:35 PM  HZT-1231A13 Stage 1 Block Valve Position - Transrmitter Out of Range Alarm

First Out/
Freeze Menu

System P .PID s Alarms & 0 Trending System

Overview Control Screens  Setpoints Status and Bently Setup




Figure 3 Menu Buttons Typical for all screens
I/P-PID Control Menu Button

This menu provides access to all PID setpoints used for setting up the current to pneumatic (I/P) valves.  The operator can manually control the selected valve by placing the valve in Manual Mode or allow the controller to automatically adjust the valve when selected for Auto Mode.  
Status Screens Menu Button
This menu provides access to the Electric Motor Start / Inhibits and Runtimes screen.  On applicable projects, customized status screens are also placed under this menu.  From these screens, the operator can perform the following actions:
· View compressor AOP, Gear AOP, and compressor Motor run times.

· View Motor Start Inhibit status.

· View all start times within the last 24 hours

· Set Motor Full Load Amps.

· Set PRV Stop Load and Force Unload setpoints.

· View time and date of last compressor start.
Alarms / Setpoints Menu Button

This menu provides access to all of the Alarm Setpoint Entry screens and Alarm Status / Alarm History Screens.  From these screens, the operator can perform the following actions:

· Edit analog input and RTD input alarm and shutdown setpoints and delays.
· View Active Alarms.
· View Alarm History.
· Reset Alarms.

· Silence Alarms.

· Clear Alarm History.

· View System Shutdown First Out Indicator.
· View System Shutdown Freeze Screens.
I/O Status Menu Button

This menu provides access to the current operating condition of all of the PLC analog and digital I/O cards.  The screens are organized by card location.  From these screens, the operator can perform the following actions:

· View status of all analog inputs including levels, pressures, and temperatures.

· View status of all discrete inputs including pushbuttons, level switches, motor auxiliaries, and estop buttons .
System Trending Menu Button

This menu provides access to the historical trending feature of the HMI.  From these screens, the operator can perform the following actions:
· View historical data for all analog input and RTD input cards.
· View historical data for compressor Capacity Control equipment including suction, discharge, and PRV status.
System Setup Menu Button

This menu provides access to the system commissioning screens and equipment control setpoints.  From these screens, the operator can perform the following actions:

· Access PanelView Plus panel configuration

· Set PLC date and Time

· Set compressor AOP and Gear AOP setpoints.

· Set PRV constants and view Pressure Ratio.

· Set Surge Control and Hot Gas Valve setpoints.

· Set Rate of Change Filter setpoints.

· Set Suction Pressure Pulldown setpoints.

· Set Sump Vent Valve timer setpoints (when controlled).

· Set Condenser Control setpoints (when controlled)
Login / Security Menu Button
This menu provides access to the user login / logout feature and, if specified, language switching capability.  From these screens, the operator can perform the following actions:

· Login
· Logout
· Change text display language

· Change password
Current User Indicator
[image: image9.png]- Setup Condenser Control CURRENTLISER

Condenser Control Setpoints.

Fast Start Pressure | 20000 | PSIG [][]D .
FastStartDelay | 15 | Sec.
CRRERRS
Slow Start Pressure | 19000 | PSIG
Slow Start Delay | 30 | Sec. I‘
Slow Stop Pressure 180.00 |PSIG [ ][ ][ ]1
L
SlowStop Delay || 45 ||Sec. SESEE -
Fast Stop Pressure | 17000 | PSIG SO
SRR 3
Fast Stop Delay 20 Sec. SO O Ol

Condenser Control Pressure [_15.09 | PSIG

View /Change
Current Step |0 Condenser Sequence

System  IP-PID Status  Alarms & w0
Overview  Comtrol  Screens  Sefpoints  Status





Figure 4 Current User Indicator
The Current User indicator is displayed in the upper left hand side of all screens.  The indicator uses the format of “CURRENT USER:” with the username of the current user below.  “Default” is displayed when no user is logged in.

Refer to the section “User Level Security” for more information on the Current User indicator.
Alarm Status Indicator

[image: image10.png]e Compressor Shutdown First Out R

7/19/2006 6:05:27 PM  TE-512 Mator Stator Temp - High Reading Shutdown
7/19/2006 6:05:23 PM TE-514 Mator Stator Temp - High Reading Shutdown
7/19/2006 B:05:09 PM  TE-512 Mator Stator Temp - High Reading Shutdown
7/19/2006 6:04:44 PM  PDIT-402 Comp Journal Brg Diff Pressure - High Reading Shutdown
7/19/2006 5:59:38 M PIT-155 Suction Pressure Shutdown - High Reading Shutdown

Compressor Shutdown Data Freeze Screens

RIDInput  RTD Input Analogin  Analog Out
Slot415  Slot6!7 Slot8 Siot 10
Digitalin  Digitalln _ Digitalin Digitalin Digtalin  Digitalin _DigitalIn

Rack 2Siot1 Rack2Slot2 Rack2Slotd Rack2Siotd Rack2SlotS Rack2Slot Rack 2Siot7

Digital Ot Digital Out__Digital Out _Digital Out
Rack 2Siot 9 Rack 2 Siot 10 Rack 2 Slot 11 Rack 2 Slot 12

System  IP-PID Status  Alarms & [ System  System EENVYTWEN
Overview  Control  Screens  Setpoints  Status  Trending  Setup





Figure 5 Alarm Status Indicator
The Alarm Status indicator is located in the upper right hand corner of all screens. The background color of the indicator is red for shutdowns and Yellow for alarms. The following are the status conditions that can be displayed:

· No Alarms or Shutdowns – No active alarms or shutdowns exist in the controller.
· New Alarm Exists (Blinking Yellow) – Displayed when an unacknowledged alarm exists in the controller.

· New Shutdown Exists (Blinking Red) – Displayed when an unacknowledged shutdown exists in the controller.
· Alarm Exists – Displayed when an acknowledged alarm exists in the controller.
· Shutdown Exists – Displayed when an acknowledged shutdown exists in the controller.
Screen Name Display

The Screen Name is displayed in the top center of all screens.  This display is useful for keeping track of what screen the operator is currently viewing.
Common Colors
The following are common colors that are used throughout the HMI:

· Yellow – Alarm condition, or warning indication.

· Red – Shutdown condition or high alert indication.

· Green – On or Active.  On setpoint entry boxes, green indicates that the user has the necessary security level to change the setpoint.

· Grey – Off

· Blue – Touch sensitive box

· Orange – Used on setpoint entry boxes to indicate that the user does not have the necessary security level to change the setpoint.
Common Terms
· ALARM - An alarm setpoint has been reached or exceeded and the compressor will continue to run. 

· AOP - Auxiliary oil pump (also referred to as Lube Oil Pump). 

· AUTO (Automatic) - The device is being controlled from the Allen-Bradley Processor.

· I/P – Current (milliamps DC) / Pneumatic (PSIA)

· MAN (Manual) - The device is being controlled from the PanelView 1000 .

· PID – (Proportional, Integral, Derivative) – This references the loops used to control the current to pneumatic (I/P) valves.

· PLC – Refers to the Allen Bradley SLC or ControlLogix processor that is installed in the control panel.

· Recycle Delay - this message indicates that the compressor has started and has shut down within the delay time that has been set to prevent the compressor from starting again.  Recycle delay is intended to prevent damage to the compressor motor from successive restarts.

· SHUTDOWN - A critical safety limit has been reached or exceeded and the compressor has been shutdown.

Setpoint Entry Boxes

[image: image11.png]- Setup Condenser Control CURRENTLISER

Condenser Control Setpoints.

Fast Start Pressure | 20000 | PSIG [][]D .
FastStartDelay | 15 | Sec.
CRRERRS
Slow Start Pressure | 19000 | PSIG
Slow Start Delay | 30 | Sec. I‘
Slow Stop Pressure 180.00 |PSIG [ ][ ][ ]1
L
SlowStop Delay || 45 ||Sec. SESEE -
Fast Stop Pressure | 17000 | PSIG SO
SRR 3
Fast Stop Delay 20 Sec. SO O Ol

Condenser Control Pressure [_15.09 | PSIG

View /Change
Current Step |0 Condenser Sequence

System  IP-PID Status  Alarms & w0
Overview  Comtrol  Screens  Sefpoints  Status




          
Figure 6 Setpoint Entry Box.  The highlighted color reflects the user’s security level.  Green = access allowed, Orange = access denied.
Setpoint entry boxes are used by the operator to enter setpoints that are used by the controller to define parameters such as alarm delays, shutdown delays, PID gains and setpoints, control setpoints, etc.  Setpoint Entry boxes have a “raised” border style, and are characterized by either a bright orange (access denied), or bright green (access allowed) outline.  A user must be logged in with the correct security level to change setpoints.  
Value Display Boxes

[image: image12.png]- Setup Condenser Control CURRENTLISER

Condenser Control Setpoints.

Fast Start Pressure | 20000 | PSIG [][]D .
FastStartDelay | 15 | Sec.
CRRERRS
Slow Start Pressure | 19000 | PSIG
Slow Start Delay | 30 | Sec. I‘
Slow Stop Pressure 180.00 |PSIG [ ][ ][ ]1
L
SlowStop Delay || 45 ||Sec. SESEE -
Fast Stop Pressure | 17000 | PSIG SO
SRR 3
Fast Stop Delay 20 Sec. SO O Ol

Condenser Control Pressure [_15.09 | PSIG

View /Change
Current Step |0 Condenser Sequence

System  IP-PID Status  Alarms & w0
Overview  Comtrol  Screens  Sefpoints  Status





Figure 7 Value Display Box
Value Display boxes show controller values such as temperatures, pressures, valve positions, and I/O status.  Value Display boxes have an “inset” border style.
User Action Buttons

[image: image13.png]- Setup Condenser Control CURRENTLISER

Condenser Control Setpoints.

Fast Start Pressure | 20000 | PSIG [][]D .
FastStartDelay | 15 | Sec.
CRRERRS
Slow Start Pressure | 19000 | PSIG
Slow Start Delay | 30 | Sec. I‘
Slow Stop Pressure 180.00 |PSIG [ ][ ][ ]1
L
SlowStop Delay || 45 ||Sec. SESEE -
Fast Stop Pressure | 17000 | PSIG SO
SRR 3
Fast Stop Delay 20 Sec. SO O Ol

Condenser Control Pressure [_15.09 | PSIG

View /Change
Current Step |0 Condenser Sequence

System  IP-PID Status  Alarms & w0
Overview  Comtrol  Screens  Sefpoints  Status





Figure 8 User Action Button (No highlight indicates that all user levels can access this button)
User Action Buttons are used by the operator to reset alarms, go to screens, and change system modes.  User Action boxes are blue and, when applicable, have either a bright orange (access denied), or bright green (access allowed) outline.  A user must be logged in with the correct security level to change setpoints.  
Setpoint Security System
[image: image14.png]- Setup Condenser Control CURRENTLISER

Fast Start Pressure 200.00 |PSIG BBB 2
R
L —

Slow Stop Pre Login

Fast Start Delay 15 | Sec.
Slow Start Pressure | 190.00 | PSIG

Slow Start Delay 30 | sec.

QLK

Slow Stop

Fast Stop Pre

Fast Stop
Condenser Control Pressure |_15.09 | PSIG
a0 | View | Change
Current Step |__0 Condenser Sequence

System  IP-PID Status  Alarms & 2 System  System EEYTWEN
Overview  Control  Screens  Setpoints  Status  Trending  Setup |l | |





Figure 9 User Login Screen
User security is used to prevent unauthorized users from changing setpoints or controller modes.  The user security system is similar in setup to the Frick Quantum LX controller.

Logging In and Logging Out

The Login / Logout function is performed through the Login / Language button on the bottom right hand corner of all screens.  Use the following procedure to login to the HMI:

· Press the “Login / Language” button
· Press the green “Login” button.

· Press the “User (F2) button.

· Enter the required user level (OPER, ENG, or ADMIN)
· Press the Enter key at the bottom right had corner when finished.

· Press the “Password (F3)” button.

· Enter the password for the required user level.

· Press the Enter key at the bottom right hand corner when finished.

· Press the Enter button again (above the ESC button on the touch screen).

Users are automatically logged out after 30 minutes of no activity.  Users can logout by pressing the red “Logout” button from the “Login / Language” submenu.
Changing User Passwords

Password can be changed from the blue “Password” button.  The level 3 and York passwords can not be changed through the operator interface.

Use the following procedure to login to the HMI:

· Press the “Login / Language” button

· Press the blue “Password” button.

· Press the “Old Password (F2) button.

· Enter the Old Password.

· Press the Enter key at the bottom right had corner when finished.

· Press the “New Password (F3)” button.

· Enter the new password for the required user level.

· Press the Enter key at the bottom right hand corner when finished.

· Press the “Confirm Password (F4)” button.

· Re-enter the new password for the required user level.

· Press the Enter key at the bottom right hand corner when finished.

· Press the Enter button again (above the ESC button on the touch screen).
User Level Security
User security is setup at the factory with the operators of 1, 2, 3, and York.

· OPER - Lowest level of access.  Can change capacity control setpoints and acknowledge alarms.

· ENG – Can change most setpoints except those located under the System Setup menu.

· ADMIN – Can change all setpoints including setup

· York – Same access as “3”.  Included for technicians familiar with legacy PanelView setpoints
4. STATUS SCREENS
System Overview Screens
[image: image15.png]Sy stem Overview 1 comsamuser:

54 OK] 96.0 MIN 119 PSIA, CN
EF T EAPE
O _s60 <t Tgeiere] pv
TS [on] o] 25l Lt |
DRIVEL GAFEIS Lantigpsia | [or] 4 | [on] s
RS TVAZINAS
— T
- -
Il 3 e RPN Pl oiscrnrce —
FTATAS o] g5 | [0] 90 | | HEADER TS
¥ Fvantes REZAT 1
> > P4
OK_ 2.5 psiD OK 25 P 0K ] 25,0 OK] 99.0
TOTAZ31A6 . A4 POTAZ3TAG FY-T231AT RIT-T231ATT
P
o s i Ui Refig P T
AT oo n19psia | [or] sy |[o] 80 o oo+
psia TR | & A AT AT Tz
> 7
‘Ist Stage Suction Header
0K ] 25,0 OK] 99.0
o250 GEFE T AT v
[ oK 506 e
~[oxrsw0 o P4 PEAZS
Compressor Status A <'|
FT-123142 O] 250 OK] 99.0 60 PSIA
Stage 1 Downstream Block Valve AT FETTZIATS 310 Stage Suction Header
Closed nhibit
PRV Override Status ||_: S
—_ 0K 39T.0 10 ﬂ PEAZEs 0 poin
No PRV Overrides Exist FT-1231A1 O] 250 OK] 99.0
FVA2IIAT FETI231ATE 2nd Stage Suction Header

1P - PID Status Alarms & 0 Trending System

Control Screens  Setpoints Status and Bently Setup




[image: image16.png]_ Sysgem Compressor Status || PRV Override Status | cursent user:

DEFAULT
: tage 1 Downstream Block Valve
Overview 2 P No PRV Overrides Exist

Compressor oK 00T
czm T
oK 00w
(EFET OK_oo.
GEAR TEZIATIA
CG-1231 4 [oszsiate

Compressor 01 Cocler

[ox o0 ]
T CM-1231  TEAZSIATIA

oK 130 rn

PZaATE

Exr
Y TEA23TAT08

oK 1210 T LsL123180
TZAAz A

oK 1200 T
Tz AR

oK 609 T
I

——— OK_ 11016
\raswsm‘ PTAZINATE [ox sea - |
TETRNATEE
ook Heaeror |

A

RV-123185 (===l

=77 LB F134A]
L From 1968 |
Receher, 13 PSiA

0 |

P Sucton
Fos ]

R
= POT-1231AT4

e 08 Cookr

00
51ae

1P - PID Status Alarms & Trending System

Control Screens  Setpoints and Bently Setup




[image: image17.png]Compressor Status || PRV Override Status | current user:
BMCENNN  System :

stage 1 DownstreamBlock Vave || o pry Overrides Exist

Overview 3 Closed inhibit
Bentyy
Vibration
o 350 x| [ox s v
P RicErs
oluids Fos-zait o sn0 ] [oK 550 v
HV-1231AT | Ok 200 TT-1231A2 PT-123140
o550 e T
PYA23143 | pTraatas —
OK 1360 F L[ oK 150
TT-A23143 TT1231A0
— @ @ U
o 1200 v
TTA231815 —] —_
! I’l
ERrE
A\ I
PITATAT
,* ,* ,* ,* ,* ,* LSH-123143
EEETESS
POT-1231AT0 Ok 110 s ot
POTZATT ey 1
prazaz] @
ocwe v ] & v - et
TS o sz +  starcsear
J TTAZ31A1E —_— Recovery
- [EEEETY) Systom
[overiew <

P .PID Status Alarms & 0 Trending System
Status and Bently Setup

Control Screens  Setpoints




Figure 10 System Overview Screens
The System Overview screen 1 is the default HMI startup display. This screen is an overview of the entire system based on the P&I Diagram (659D2149). It consists of a general diagram of the critical components of the refrigeration system as well as motor status, analog inputs, RTD inputs, modulating valve positions, and information displays.
System Overview 2 (659D2147) supplies a more detailed view of the gearbox & motor. Finally Stem Overview 3 (659D2146) supplies a more detailed look of the Compressor. 

I/O Status Display
System critical temperatures, pressures, levels, and modulating valve positions are shown in their respective locations per the P&I Diagram. 
Compressor Status

The compressor status is shown with respect to the running status of the compressor:
· ON = Green

· OFF = Grey
Comp / Gear Aux Oil Pump Status 

The AOP status is shown with respect to the running status of the compressor and gear AOP: 
· ON   =  [image: image18.png][o] Stat PRV O de Statt
_ System ompressor Status verride Status | curven user

: Compressor Discharge Block
Overview 2 e e e No PRV Overrides Exist

Lue 08 compressar - T
1231 ently TE-1231AT0A
alG Vibration 7
o 03 e
- — 123140 OK_66.
GEAR TR
¥ Fos-1zatte —
Compressor il Cooler Cc.1231 4 OK_ 651
CM-1231 " TEA231AT2A
i CurentPha
o 01 ro
FETZHATS . Curent round T

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup




· OFF =  [image: image19.png]_ System Compressor Status || PRV Override Status | current user:

DEFAULT

. Compressor Discharge Block || o pRY Overrides Exist
Overview 2 Valve Closed Infibit
T
Lukbe O Compressor Bent OK_ 667 F
c123 ontly TE-1231A10A
alG Vibration 7
o 03 e
- — T-1231A0 OK_66.
GEAR TEATA

CG-1231 4 [osziess

Compressor 01 Cocler

oK 654

CM-1231 “TE-I231A128
i, Curent P

o7

PT123TATS Y . Current ind Trip

(o s <]
T s
m

= o 20

A4 N 2 e
S S
1 ! e |
KV-123126 L Vessel |

7 TN T 1 e
FrT ﬁ_ummm‘ » S o0 rn
R e

b

Alarms & ! Trending Syste

Setpoints Status and Bently Setup




Modulating Valves 
[image: image20.png]_ System Compressor Status || PRV Override Status | current user:

DEFAULT

. Compressor Discharge Block || o pRY Overrides Exist
Overview 2 Valve Closed Infibit
T
Lukbe O Compressor Bent OK_ 667 F
c123 ontly TE-1231A10A
alG Vibration 7
o 03 e
- — T-1231A0 OK_66.
GEAR TEATA

CG-1231 4 [osziess

Compressor 01 Cocler

[ox esa |
CM-1231_ TEAZIATIA
i, Cument Pha:

oK 07 s

PTA231ATS . Curent Ground Tip

oK 654t
TEZIATE

oK 640 T
REFEe]

oK 663 T
I

—»—— o 72 o
\raswsm‘ PTTZTATE [ox es1 -]
TETRNATEE
ook Heaeror |

A

RV-125185 (===l

=77 LB F134A]
L From 1968 |
Receher, 13 PSiA

it |

P Sucton
Fos ]

o 00w
> POT-1231AT4

e 08 Cookr

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



     [image: image21.png]_ o [ = Fe e e 1System Overview 1 currenmuser
3 Lo BB [ a0 | L 119psia DEFAULT
HITAZs1a10 | TVAIZ31AS  RVAZIAZ
v = —
) < Figh Prossure] g —
T [0] 0.0 260 | Ceust et > 1
™ —DRIVELINE BOUNDARY R Lini11gPsia 250 260
ll cwioncost | WY WAETD
- ;1o
T I o1 oiscinnce n
FT-123183 250 | 0] 250 [HERTE B TTAZ31A5
Yy Pvazias AZSIATE Y
=== -
»- »-
25 o0 25 o0 260 260
FOTAZIAE | POTAZIEG FVAZ31AT FET-123111
wﬁ@i = —
i Ui e P o
EEFER Ao hani 13 pia e & 500t
psin T | A Y S-12s1ad  TVAZS18 TS
] o > v
‘st Stage Suction Header
260 260
25 10 Fv-123142 FET-1231812 v
POTAZITAT _ YRy
Compressor Status 4998 "| — 60 PSIA
GEFEr™ 260 260 )
Emergency Stop F-A251AZ  RE-1231A15 31d Stage Suction Header
Pressed
500 ron
PRV Override Status — w ST
2499
i ' 28PSIA
No PRV Overrides Exist FrAzAT 250 S| -

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

System P . PID Status Alarms & ! Trending System Login

Overview Control Screens  Setpoints Status and Bently Setup Security



    [image: image22.png]_ o [ = Fe e e 1System Overview 1 currenmuser
3 Lo BB [ a0 | L 119psia DEFAULT
HITAZs1a10 | TVAIZ31AS  RVAZIAZ
v = —
) < Figh Prossure] g —
T [0] 0.0 260 | Ceust et > 1
™ —DRIVELINE BOUNDARY R Lini11gPsia 250 260
ll cwioncost | WY WAETD
- ;1o
T I o1 oiscinnce n
FT-123183 250 | 0] 250 [HERTE B TTAZ31A5
Yy Pvazias AZSIATE Y
=== -
»- »-
25 o0 25 o0 260 260
FOTAZIAE | POTAZIEG FVAZ31AT FET-123111
wﬁ@i = —
i Ui e P o
EEFER Ao hani 13 pia e & 500t
psin T | A Y S-12s1ad  TVAZS18 TS
] o > v
‘st Stage Suction Header
260 260
25 10 Fv-123142 FET-1231812 v
POTAZITAT _ YRy
Compressor Status 4998 "| — 60 PSIA
GEFEr™ 260 260 )
Emergency Stop F-A251AZ  RE-1231A15 31d Stage Suction Header
Pressed
500 ron
PRV Override Status — w ST
2499
i ' 28PSIA
No PRV Overrides Exist FrAzAT 250 S| -

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

System P . PID Status Alarms & ! Trending System Login

Overview Control Screens  Setpoints Status and Bently Setup Security



    
 Figure 11 Represents the 3 styles of Valves
The modulating valve position is shown to the lower center of the valve box. Some limited function valve indicators will have a BV (Block Valve) or HV (Hand Valve) in the top left of the valve box. Block valve body and handle will turn green when the solenoid is energized. Hand valves have no solenoid so the image has no handle but the body turns green when the valve position is above 95%.   Listed below are the different states of the valve indicator:
· [image: image23.png]_ System Compressor Status || PRV Override Status | current user:

DEFAULT

. Compressor Discharge Block || o pRY Overrides Exist
Overview 2 Valve Closed Infibit
T
Lukbe O Compressor Bent OK_ 667 F
c123 ontly TE-1231A10A
alG Vibration 7
o 03 e
- — T-1231A0 OK_66.
GEAR TEATA

CG-1231 4 [osziess

Compressor 01 Cocler

[ox esa |
CM-1231_ TEAZIATIA
i, Cument Pha:

oK 07 s

PTA231ATS . Curent Ground Tip

oK 654t
TEZIATE

oK 640 T
REFEe]

oK 663 T
I

—»—— o 72 o
\raswsm‘ PTTZTATE [ox es1 -]
TETRNATEE
ook Heaeror |

A

RV-125185 (===l

=77 LB F134A]
L From 1968 |
Receher, 13 PSiA

it |

P Sucton
Fos ]

o 00w
> POT-1231AT4

e 08 Cookr

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



 This example is of a normal off / closed state

· [image: image24.png]_ System Compressor Status || PRV Override Status | current user:

DEFAULT

. Compressor Discharge Block || o pRY Overrides Exist
Overview 2 Valve Closed Infibit
T
Lukbe O Compressor Bent OK_ 667 F
c123 ontly TE-1231A10A
alG Vibration 7
o 03 e
- — T-1231A0 OK_66.
GEAR TEATA

CG-1231 4 [osziess

Compressor 01 Cocler

oK 654

CM-1231 “TE-I231A128
i, Curent P

o7

PT123TATS Y . Current ind Trip

Y OK_ 654 F
4 FrarTa ez
T s
TTEAZIIANE
= o 20 i
A4 wy o 2 e
S S
1 o] il e |
KV-123146 L Vessel |
7 TN T 1 e
FrT ﬁ_ummm‘ » S o0 rn
R e
b

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



 The green handle indicates the solenoid for the valve is energized
· [image: image25.png]_ System Compressor Status || PRV Override Status | current user:

DEFAULT

. Compressor Discharge Block || o pRY Overrides Exist
Overview 2 Valve Closed Infibit
T
Lukbe O Compressor Bent OK_ 667 F
c123 ontly TE-1231A10A
alG Vibration 7
o 03 e
- — T-1231A0 OK_66.
GEAR TEATA

CG-1231 4 [osziess

Compressor 01 Cocler

oK 654

CM-1231 “TE-I231A128
i, Curent P

o7

PT123TATS Y . Current ind Trip

(o s <]
T s
m

= o 20

A4 N 2 e
S S
1 ! e |
KV-123126 L Vessel |

7 TN T 1 e
FrT ﬁ_ummm‘ » S o0 rn
R e

b

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



 The green valve body indicates the valve is more than 95% open (adjustable 95 to 100%) 
· [image: image26.png]W Hioh Pressure] i
_ 4 i Remg‘System Overview 1 cormmmuser
3 [ bR @] [ 113psia|
HITa231a10 Y TV-1231A0  RV-1231A2
el —
S0 < FighPressure] g
TR 250 50 Lt 1
DRIVELINE BOUNDARY _ | Fv-123143 LMni119psia 260 260
cmazn  cotant SOzHAs TAsAS
=i
9996 oo |- T ¥ biscrnree —
GEFErS 250 Sslon| | HEADER A
¥y Pvazias AZ23ATE Y
T — »- »
25 10 260 260
ROTIS | 4 TOTIiS FVAZ31AT FET-123111
mﬁsmL
i Ui e P o
EEFER o hani 13 pia 2 & 500t
wesn Sy 4 v SAzatAG  TAZINA Y TS
v
Ist Stage Suction Header »-
260 260
25 10 Fv-123142 FET-1231812 v
POTAZITAT YRy
or 4598 e GEFErS
Compressor Status A "|
GEFEr™ 260 250 . S0PSA_ 1o
Compressor Discharge Block F-A251AZ  RE-1231A15 3rd Stage Suction Header
Valve Closed Inhibit
PRV Override Status T ST Jpsin
No PRV Overrides Exist FrAzAT 250 260 [ﬂ_l—

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

1P - PID Status Alarms & 110 Trending System

Control Screens  Setpoints Status and Bently Setup



 The pink box & IOF indicate an out of range condition
Transmitter Indicator
[image: image27.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lue 08 compressar - T
1231 ently TE-1231AT0A
alG Vibration 7
o 03 e
- — 123140 OK_66.
GEAR TR
¥ Fos-1zatte —
Compressor il Cooler Cc.1231 4 OK_ 651
CM-1231 " TEA231AT2A
i CurentPha
o 01 ro
FETZHATS . Curent round T

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



             

 Figure 12 Multipurpose Transmitter Indicator

The Transmitter indicator can be used for Temperature, Flow, Current, Pressure, & Differential Pressure.
· [image: image28.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lube O Compressor Bent OK 667 F
1231 i :""y TE-1231AT0A
ARG ibration j
r_ o _w.
GEAR A
¥ Posazatate —
Compressor il Cooler 61231 4 OK_ 651
CM-1231 “TE-I231A128
i, Curent P
o7
PTAZIETS . Curent oround 11

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



  This example is of a normal reading transmitter

· [image: image29.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lube O Compressor Bent OK 667 F
1231 i :""y TE-1231AT0A
ARG ibration j
r_ o _w.
GEAR A
¥ Posazatate —
Compressor il Cooler 61231 4 OK_ 651
CM-1231 “TE-I231A128
i, Curent P
o7
PTAZIETS . Curent oround 11

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



  This example is of  transmitter in Alarm (H or L)

· [image: image30.png]NEW

System Compressor Status || PRV Override Status | curren user:
DEFAULT
Overview 3 EmErgennyEn No PRV Overrides Exist
Pressed
Bently
Vibration
Ok 134 o] Ok 144 rem
- GEEER) TPTTAz
Foszoa T
O 641t Tz
HH 144 AT v
= = T
Ok 64T | [0 ws =
MEEELS] A
= d ol ol 1l U
24 0
\ i ok 21
PITAZITAD
.* .* .* .* .*.* LsH-123143
} ATl | e —
——7 FOT-1231A11 S A
Ok 36T . [EEEr
AT oK 639 = [ seresea
AT — Recovery

Status

Alarms & !
Setpoints Status

Trending
and Bently

Syste
Setup



 This example is of  transmitter in shutdown (HH or LL)
· [image: image31.png]_ o [ = Fe e e 1System Overview 1 currenmuser
3 Lo BB [ a0 | L 119psia DEFAULT
HITAZs1a10 | TVAIZ31AS  RVAZIAZ
v = —
) < Figh Prossure] g —
T [0] 0.0 260 | Ceust et > 1
™ —DRIVELINE BOUNDARY R Lini11gPsia 250 260
ll cwioncost | WY WAETD
- ;1o
T I o1 oiscinnce n
FT-123183 250 | 0] 250 [HERTE B TTAZ31A5
Yy Pvazias AZSIATE Y
=== -
»- »-
25 o0 25 o0 260 260
FOTAZIAE | POTAZIEG FVAZ31AT FET-123111
wﬁ@i = —
i Ui e P o
EEFER Ao hani 13 pia e & 500t
psin T | A Y S-12s1ad  TVAZS18 TS
] o > v
‘st Stage Suction Header
260 260
25 10 Fv-123142 FET-1231812 v
POTAZITAT _ YRy
Compressor Status 4998 "| — 60 PSIA
GEFEr™ 260 260 )
Emergency Stop F-A251AZ  RE-1231A15 31d Stage Suction Header
Pressed
500 ron
PRV Override Status — w ST
2499
i ' 28PSIA
No PRV Overrides Exist FrAzAT 250 S| -

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

System P . PID Status Alarms & ! Trending System Login

Overview Control Screens  Setpoints Status and Bently Setup Security



 The pink box & IOF indicate an out of range condition
SyncFault (Suction Pressure)
[image: image32.png]NEW

ol BV | i Prassure]

s System Overview 1 cumenmuser

Lol [] a0 | fwnrrspsie DEFALLT
HITA231410 Y TV-1231A4  RV-1231A2
v = —
500 <+ Figh Prossure] g —
TS 0] 00 50 Lt 1
" _DRIVELINE BOUNDARY | V125143 LM 119pSia 250 260
[ cmrncoron Az TS
| - - ;1o
| i 9996 " »- P DiscHareE —
23S el | [0] 250 | | HEADER S
I Y Pvimig AELsiATS 1
=== =
»- »-
25 10 25 10 250 260
[SyncFaut PomEET: 4, [T FVA231AT FZT-1231A11
wﬁ@i = —
o o - ]
e hani 13 pia o 250 500t
y7psia Mz | Y 123184 TV-125188 T2
] i > v
‘st Stage Suction Header
260 260
25 10 Fv-123142 FET-1231812 v
POTAZITAT _ YRy
Compressor Status 998 "| —— 60 PSIA
a2 260 250 ]
Emergency Stop F-A251AZ  RE-1231A15 3rd Stage Suction Header
Pressed
500 ron
PRV Override Status b
— 2099 b ﬂ P o
No PRV Overrides Exist FrAzAT 250 S| -

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

System P . PID Status Alarms & ! Trending System Login

Overview Control Screens  Setpoints Status and Bently Setup Security



             

 Figure 13 Above PT-1231A9 the SyncFault is active otherwise this space is empty
Comparator Compares Local (PT-1231A0) & Common Header Suction Pressure (PT-1231A9). The Comparator uses the Common Header Suction pressure unless the Delta PSI differs by more than the Setpoint default of 2 (0-10 adjustable) then it uses the Local Pressure.
Digital Indicators
[image: image33.png]NEW

System Compressor Status || PRV Override Status | curren user:
DEFAULT
Overview 3 EmErgennyEn No PRV Overrides Exist
Pressed
Bently
Vibration
Ok 134 o] Ok 144 rem
- GEEER) TPTTAz
Foszoa T
O 641t Tz
HH 144 AT v
= = T
Ok 64T | [0 ws =
MEEELS] A
= d ol ol 1l U
24 0
\ i ok 21
PITAZITAD
.* .* .* .* .*.* LsH-123143
} ATl | e —
——7 FOT-1231A11 S A
Ok 36T . [EEEr
AT oK 639 = [ seresea
AT — Recovery

Status

Alarms & !
Setpoints Status

Trending
and Bently

Syste
Setup




 Figure 14 Above is an examples of digital alarm indicators
The digital alarm indicator are used for level swithces and SPA2 module alarm conditions. 

· [image: image34.png]NEW

System Compressor Status || PRV Override Status | curren user:
DEFAULT
Overview 3 EmErgennyEn No PRV Overrides Exist
Pressed
Bently
Vibration
Ok 134 o] Ok 144 rem
- GEEER) TPTTAz
Foszoa T
O 641t Tz
HH 144 AT v
= = T
Ok 64T | [0 ws =
MEEELS] A
= d ol ol 1l U
24 0
\ i ok 21
PITAZITAD
.* .* .* .* .*.* LsH-123143
} ATl | e —
——7 FOT-1231A11 S A
Ok 36T . [EEEr
AT oK 639 = [ seresea
AT — Recovery

Status

Alarms & !
Setpoints Status

Trending
and Bently

Syste
Setup



 Normal State

· [image: image35.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lube O Compressor Bent OK 667 F
1231 i :""y TE-1231AT0A
ARG ibration j
r_ o _w.
GEAR A
¥ Posazatate —
Compressor il Cooler 61231 4 OK_ 651
CM-1231 “TE-I231A128
i, Curent P
o7
PTAZIETS . Curent oround 11

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup



 Level switch in alarm

· [image: image36.png]NEW

System Compressor Status || PRV Override Status | curren user:
DEFAULT
Overview 3 EmErgennyEn No PRV Overrides Exist
Pressed
Bently
Vibration
Ok 134 o] Ok 144 rem
- GEEER) TPTTAz
Foszoa T
O 641t Tz
HH 144 AT v
= = T
Ok 64T | [0 ws =
MEEELS] A
= d ol ol 1l U
24 0
\ i ok 21
PITAZITAD
.* .* .* .* .*.* LsH-123143
} ATl | e —
——7 FOT-1231A11 S A
Ok 36T . [EEEr
AT oK 639 = [ seresea
AT — Recovery

Status

Alarms & !
Setpoints Status

Trending
and Bently

Syste
Setup



   SPA2 signal in shutdown (Same for Level Switch)

Quick Link Buttons
[image: image37.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lube O Compressor Bent OK 667 F
1231 i :""y TE-1231AT0A
ARG ibration j
r_ o _w.
GEAR A
¥ Posazatate —
Compressor il Cooler 61231 4 OK_ 651
CM-1231 “TE-I231A128
i, Curent P
o7
PTAZIETS . Curent oround 11

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup




 Figure 15 Above is an examples of two Quick Link Buttons

The blue Quick Link Buttons are on each of the Overview Screens to aid in moving between frequently used screens.
Motor Indicators & Alarms
[image: image38.png]NEW

System Compressor Status || PRV Override Status | current user:

; Emergency Stop DEFAULT
Overview 2 Pressed

No PRV Overrides Exist

Lube O Compressor Bent OK 667 F
1231 i :""y TE-1231AT0A
ARG ibration j
r_ o _w.
GEAR A
¥ Posazatate —
Compressor il Cooler 61231 4 OK_ 651
CM-1231 “TE-I231A128
i, Curent P
o7
PTAZIETS . Curent oround 11

oK 654t

T TETTATE
T T
e

== o 22 rm

- N FETTS o
= esiaE
1 Sl k|
KV-123146 L Vessel 1

577 LA FA34R] =
o O o ﬁ_mmmm‘ - o 00
Receiver, 113 PSIA. ‘ FOT-T23TAT

i

Alarms & ! Trending Syste

Setpoints Status and Bently Setup




 Figure 16 Motor indiactors
The motor will indicate running when the motor aux contact is made. The alarm states are tripped from the GE Multilin MIF II Digital Feeder Relay. The following are the trip states:

· Differential Current Phase Trip

· Differential Current Ground Trip

System Status Indicator

The System Status Indicator is an information display used to alert the operator of the current functioning status of the compressor system.  The following states can be displayed:
· Compressor Ready To Start
· Electric Motor Anti Recycle Inhibit On (Recycle Delay)
· Compressor Running

· Compressor Running In Alarm 

· System Shutdown

· System Starting - Starting Oil Pumps
· Starting Compressor

· Emergency Stop is Pressed

· Local Stop Button Pressed
· Remote Stop Pressed / Enabled
· Low Compressor Oil Sump Level Start Inhibit

· Low Gear Oil Sump Level Start Inhibit
· Low Comp Oil Sump Temp Start Inhibit
· DCS Permissive Start Inhibit
· MCC Permissive Start Inhibit
· Compressor Stage Drain High Level Inhibit
· Stage 1 Block Valve Closed Inhibit
· Stage 2 Upstream Block Valve Closed Inhibit
· Stage 2 Downstream Block Valve Closed Inhibit
· Stage 3 Upstream Block Valve Closed Inhibit
· Stage 3 Downstream Block Valve Closed Inhibit
· Stage 1 Downstream Block Valve Closed Inhibit
· Compressor Discharge Block Valve Closed Inhibit
PRV Overrides Indicator

The PRV Overrides Indicator is an information display used to alert the operator of any active conditions that will stop load or force unload the motor.  The following states can be displayed:
· No PRV overrides exist

· Discharge Pressure Override

· Motor Current Stop Load

· Motor Current Force Unload

· PRV in slow Pulldown startup
Start Permissives (Compressor Summary Screen)
[image: image39.png]NEw COMPRESSOR START SUMMARY

Phase 1 START SEQUENCE PERMISSIVES

@ Sump Oil Temperature > Saturated Suction +30°F

ompressor Oil Sump Temp. 120.0 °F
Saurated Suction + Offset 755 °F
Sump Temp Start Permissive ~ 75.0 °F

@ Active Shutdown Alarm

@ Electric Motor Anti Recycle P
@ Compressor Oil Sump Level Low

@ Gear il Sump Level Low

@ NICC Permissive Start Signal

@ DCS Process Permissive Start Signal

@ Compressor Stage Drain High Level

@ Open Stage 1Block Valve

@ Open Stage 2 Upstream Block Valve

@ Open Stage 2 Downstream Block Valve
@ Open Stage 3 Upstream Block Valve

@ Open Stage 3 Downstream Block Valve
© Open Stage 1 Downstream Block Valve
@ Open Compressor Discharge Block Valve
© COMPRESSOR READY TO START

issive

Phase 2 Compressor Start Intlate
© Press Compressor Start Button or Send Through DCS.

1P - PID Status

Screens

Alarms &

Control

CURRENT USER:
DEFAULT
Phase 3 Oll Pressure Interlocks
© Compressor AP Pressure
mp Oil Supply DP 330 PSIA
mp Oil Supply SP 200 PSIA
mp Oil Pump Status. OFF
@ Gear AOP Pressure
GEAR Oil Supply Press. 17.0  PSIA
GEAR Oil Supply SP 100 PSIA

Gear Oil Pump Status. OFF
@ Compressor Start Delay Timer > 30 sec

Phase 4 Com pressor Motor Start
@ Soft Start Request To Motor Switchgear
or
@ ATL Start Request To Motor Switchgear
o
0 AMPS

Compressor Status

Stage 1 Downstream Block Valve
Closed Inhibit

PRV Override Status
No PRV Overrides Exist

0 Trending System

Setpoints

Status and Bently Setup




Figure 17 Compressor Start Summary Screen

The Compressor Start Summary Screen displays information regarding the Startup sequence and anything inhibiting the compressor from starting.

 Phase 1 Start Sequence Permissives

The Phase 1 Start Sequence displays all of the permissives that must be met to receive the Compressor Ready To Start signal. The Compressor Ready To Start indicator will be Red until all permissives are met and then turn Green. The round indicators in front of each permissive will be grey until met and then turn green to show it is OK.
 Phase 2 Compressor Start Initiate
The Phase 2 Compressor Start Initiate is only waiting for the start button or DCS start signal to be sent.

 Phase 3 Oil Pressure Interlocks

The Phase 3 Oil Pressure Interlocks showing that Compressor & Gearbox oil pressure is ok along with a 30 sec delay must be met for the automatic sequence to continue. 

 Phase 4 Compressor Motor Start

The Phase 4 Compressor Motor Start waits for either a soft start or ATL (Across The Line) signal. Then once the Compressor motor AUX contacts close the Compressor Status will display Compressor Running Status.
Note: For further detail see the Logic Diagram 669D0127 sheet 2 of 11.
Electric Motor Inhibits and Runtimes
[image: image40.png]_ Electric Motor Start Inhibits / Runtimes CURKENT USER:

11/19/2009 1:16:20 AM

Motor Start Inhibit Motor Runtimes:
Start Times in Last
24H PR
fn 24 Hour Inhibit Compressor RunTime | 11 Hours
L g Compressor Starts 59
7 28: 0
3 19 2 Inhibit Delay| 0 Min. Comp AOP RunTime| 1 Hours
4 ds 6 2 Minute Delay] 0  Sec. Comp AOP Starts | 1623
5 22 44 ——
Cold Start Enable[ 1 Min. PR
6 22 : 47 Gear AOP RunTime| 3  Hours
Motor Current Setpoints——— Gear AOP Starts | 1630
Motor Current [ 0 Amps 0 %FLA
Last Compressor Start
Full Load Amps (100%)=  496.0 | Amps P
PRV Stop Load ~ 100.0 | % 11119 | 2009
PRV Force Unload ~ 103.0 |

Alarms & 0 Trending System

Setpoints Status and Bently Setup




Figure 18 Typical Electric Motor Inhibits and Runtimes Screen
The Electric Motor Inhibits and Runtimes screen displays information regarding motor protection and motor runtimes.  When anti-Recycle is active the compressor is prevented from starting.  Anti-recycle is used to prevent excessive starting of the compressor to avoid damage to the motor.  
 Motor Current Setpoints

The “Motor Current Setpoints” section of the screen is used to set the parameters defining the FLA%, PRV stop load, and PRV force unload.
 Motor Runtimes

The “Motor Runtimes” section displays run time information and number of start counts for the compressor motor and auxiliary oil pump motors. The last compressor start is logged on this display with the date and time being displayed
2 Minute Delay
Indicates two minute start inhibit delay time.  Compressor startup will be permitted when this value is zero
Hot Start Delay
The Hot Start Delay is the amount of time between the stop and restart of the compressor.  A hot start will be permitted when this value is zero. 
Cold Start Delay (24 Hour Inhibit)
Indicates the maximum number of starts for the past 24 hours has been reached.  The times of the last six starts are recorded under TIME OF LAST 6 STARTS.  Compressor startup will be inhibited until 24 hours have elapsed since the first start. This will allow two consecutive starts with only a two minute inhibit between them.
Start Times in Last 24 Hours
The time of the six most recent compressor starts within a 24 hour period.
Actual Motor Amps
Displays the current Motor Amps transmitted from the C/T sensor.
FLA Setpoint
Enter the motor AMP Setpoint to be used as the 100% load value.
Actual FLA %
The current Motor Amps usage as a percentage of Full Load Amp draws.

Stop Load
When the motor FLA reaches or exceeds this setpoint, the pre-rotation vanes are prohibited from opening any further. 

Range (0 – 110%)
Force Unload
When the motor FLA reaches or exceeds this setpoint, the pre-rotation vanes are ramped closed at a rate of 10% per second. The ramp time is adjustable and can be changed via the “Motor Current Force Unload” setpoint in the System Setup page accessed via the System Setup Menu.
Range (0 – 103%) 
Number of Starts

The total number of starts for each motor.

Runtimes

The total running hours for each motor. 

Date and Time of Compressor Start
The date and time of the last compressor start.
5. PID SCREENS

PID Setpoints

[image: image41.png]System
Overview

wP-PID
Control

PID 4 Setup - Evaporator LCV
Evaporator Level Control
(PV) LIT-103A 3280 [in.
(cv) LIc103 [100.00 |%

(SP) Setpoint | 40.00 |PSIG

Upper  Lower

Gain 40 40
Reset | 05 05

Range 100

PID Manual Mode Control

Command | 1000 |%
Valve In Auto Mode v
Press for Manual Mode

Status  Alarms & 0 System
Screens  Sefpoints  Status  Trending

(CURRENT USER:
3





Figure 19 Represents a Typical PID Loop Screen
List of PID Loops

A detailed list of PID loop control can be found in both the Logic Diagrams (669D0127) and Pneumatic Electric Diagrams (669D0124) provided with the project
PID Loop Setpoints

Actual PV

The analog input (or process variable) is displayed along with its unit of measure.   The PID loop will equalize this variable around the loop setpoint based on the gain and reset values.

NOTE:  Rate (not adjustable on the display). 
Setpoint SP 

Enter the setpoint of the desired temperature, pressure, level, or flow to be maintained.  The PID loop will equalize the process variable around this setpoint based on the gain, reset, and rate (not adjustable on the display). (See explanations of each below)
Gain 

This is the Proportional Gain, ranging from .001 to 20. Gain acts directly on the change in error since the last scan (error is the setpoint (SP) minus the control variable (CV) value). Therefore, in the case of steady-state error, gain alone has no effect on the output. For this reason, gain cannot be used alone. 
Gain is also used as a multiplier on the integral and derivative. A rule of thumb is to set this gain to one half the value needed to cause the output to oscillate when the reset is set to zero.  Too much gain results in output oscillation (overshooting). Too little gain results in very slow performance
· UPPER Gain - This setpoint will be used when the process variable is above the loop setpoint. 
· LOWER Gain - This setpoint will be used when the process variable is below the loop setpoint.
· Adjusting Gain Values – Increasing gain causes a FASTER response (valve ramps in larger increments).  Decreasing gain causes a SLOWER response (valve ramps in smaller increments)

Reset TI 

Reset is the Integral gain, adjustable from 0.001 to 20. This term acts only on the current error. It is used to reduce the current error to zero. Note that during steady-state conditions, integral multiplied by current error multiplied by gain is the only thing affecting the output.  A rule of thumb is to set the reset as low as needed to prevent over-shooting.
· UPPER Reset - This setpoint will be used when the process variable is above the loop setpoint
· LOWER Reset - This setpoint will be used when the process variable is below the loop setpoint
· Adjusting Reset Values - Increasing reset causes a SLOWER response.  Decreasing reset causes a FASTER response.
Range
The range is used to set minimum and maximum control values for the modulating valve.  An example would be a minimum value of 20% for a pressure control valve that should never close to less than 20%.
Output CV

This displays the current control output in % open.  NOTE: When the valve is in manual mode, this value will represent the PID Loop control position if the valve were still in auto mode, and not the physical position of the valve.  
Manual / Auto Valve Control

Mode Change Bumpless Transition Operation

The control system utilizes a “bumpless” transition when switching from manual to auto control.  Bumpless refers to the ramping of the valve in a smooth transition, as opposed to non-bumpless which would “slam” the valve from the manual position to the auto position.
Valve Modes Of Operation
The operator must be logged in with a minimum of level 2 to use the manual control feature.  The following are the 2 states of the valve:

· Auto Mode – When the valve is in auto mode the control button will say “Valve in Auto Mode Press for Manual Mode”.  Pressing the button will change the valve to manual mode.

· Manual Mode – When the valve is in Manual Mode, the control button will show “Valve in Manual Mode Press for Auto Mode”.  Pressing the button will change the valve to auto mode.  The indicator will blink red when the modulating valve is placed in manual mode control.
Command Position
The Command Position represents the percentage location of the valve.  0% represents fully closed, 100% represents fully open.  When the valve is in manual mode in can be ramped open and close using 2 different methods, by touching on the “Command” box and entering a command value, or by touching the blue ramp up or ramp down arrows.

NOTE: If a valve is left in manual mode, and the current user logs out, the valve mode status will show “Valve in Manual Mode Login to Change”.
PRV Capacity Control

[image: image42.png]PID Setup - PRV Controller U TR

3

—Suction Pressure Control PIC 1231A0— Discharge Pressure Override PIC-1231A3
(PV) PT-1231A0 1430  PSIAsyncFault (PV)PT-1231A3 | 1444 PSIA
(CV) PY-1231A0 500 % (CV) PIC-1231A3 [ 0.00
startup Setpoint | 17.00 PSIA
(SP) Setpoint  17.00 | PSIA (7)) et
Upper Lower Upper Lower

Discharge Pressure

Override
PID Manual Mode Control u

o Motor Current
Command 5.0 % Stop Load

Valve In Auto Mode
Press for Manual Mode Motor Current

Force Unload
Suction Pulldown Disabled Press To Enable

Status Alarms & 0 Trending System Log

Screens  Setpoints s and Bently Setup




Figure 20 Typical PRV Capacity Control Screen with Discharge Pressure Override
PRV Overrides Indicator

The PRV Overrides Indicator is an information display used to alert the operator of any active conditions that will stop load or force unload the motor.  The following states can be displayed:

· No PRV overrides exist

· Discharge Pressure Override

· Motor Current Stop Load

· Motor Current Force Unload

· PRV in slow Pulldown startup
Startup Setpoint

Default conditions will allow for the compressor to do a slow loading of the Pre Rotation Vanes according to setup parameters entered in the setup display section.  This slow loading can be bypassed at any time of the startup procedure by pushing the Suction Slow Pulldown Enabled Press to Disable button.  If the Slow Pulldown is disabled the pushbutton will display Suction Pulldown Disabled Press to Enable, this will disable all Slow Pulldown setpoints on startup.    
Discharge Pressure Override

This override is designed to ramp the PRV’s closed during high discharge pressure conditions.  If the process variable (discharge pressure) exceeds the loop setpoint, the PID Loop will begin ramping down.  When the output of the discharge loop is less than the output of the suction loop, the suction loop will begin ramping down at the same rate as the discharge loop in order to close the PRV’s due to high discharge pressure
· Upper Gain & Reset Setpoints - The gain and reset setpoints are set for a faster response during high discharge pressure conditions.  This allows the PRV’s to close sooner in order to reduce the discharge pressure.

· Lower Gain & Reset Setpoints - The gain and reset setpoints are set for a slower response after the discharge pressure falls below the setpoint.  This allows the PRV’s to open slowly in order to prevent the discharge pressure from rising to quickly.
Override Comparator

The Override Comparator is located in the lower right portion of the screen (box with “ < “ symbol). The lines to & from the comparator to the PRV PID will normally be black. When Discharge Override, Motor Current Stop / Force Unload are active the lines will turn green as in figure 20.

Sync Fault

Figure 20 shows PT-1231A0 with SyncFault active otherwise this space is empty

A comparator compares Local (PT-1231A0) & Common Header Suction Pressure (PT-1231A9). The comparator uses the Common Header Suction pressure unless the Delta PSI differs by more than the Setpoint default of 2 (0-10 adjustable) then it uses the Local Pressure.
6. I/O Status Screens
Digital Inputs and Digital Outputs
[image: image43.png]Discrete Input Card Slot 14 GURRENT USER:
OEFALLT

:xx/00 NI Local Emergency Stop

:xx/01 ]Il Remote Emergency Shutdown

1:Xx/02 Compressor Start

1:xx/03 [JENH compressor Stop

I:xx/04 [JENH Compressor AOP Selected to Auto

1:xx/05 [JEII Gear AOP Selected to Auto

I:xx/06 [N Enclosure Purge Alarm

1:xx/07 [JENH Switch Fault Alarm

I:xx/08 [JEEH Compressor High Discharge Pressure Shutdown SPA
1:xx/09 Compressor Oil Supply High Differential Pressure Shutdown SPA
1:xx10 [JERH Bently ok

:xx/11 [JENI Bently Common Vibration Alarm

I:xx/12 [JEEHH Bently Common Vibration Shutdown

I:xx/13 [JEEHI Bently Common Thrust / Temperature Alarm
:xx/14 [N Bently Common Thrust / Temperature Shutdown

I:xx/15 Spare

1P - PID Alarms & 0 Trending System

Control Setpoints Status and Bently Setup




Figure 21 Typical Digital Input Status Screen
The Digital Inputs and Digital Outputs screen displays the actual states of all digital inputs wired to the controller.  The inputs and outputs are listed in order as wired to the digital input card.
Analog Inputs

[image: image44.png]PT-1231A3

PT-1231A0
PT-1231A9
PT-1231A1
PT-1231A4
PT-1231A2
PT-1231A5
FT-1231A3
FT-1231A1
FT-1231A2
TT-1231A0
TT-1231A3
TT-1231A4
TT-1231A5
TT-1231A6
PT-1231A15

[1a63
[1a47
[ 4096
[1a52
[ 4008
[1a51
[ 4097
[ 9995
[ 2409
[ 4008
[6761
[ 6645
[ 4099
[ 5000
[ 4099
[ 060

1P - PID

PSIA
PSIA
PSIA
PSIA
PSIA
PSIA
PSIA
FT"3Min
FT"3Min
FT"3Min

Analog Input Card Slot 6 ‘GURRENT USER:

DEFAULT

Compressor Discharge Pressure
Compressor Stage 1 Suction Pressure
Common Stage 1 Suction Pressure

Stage 2 Downstream Pressure

Stage 2 Upstream Recycle Liquid Pressure
Stage 3 Downstream Pressure

Stage 3 Upstream Recycle Liquid Pressure
Discharge Line Flow Transmitter

Stage 2 Flow Transmitter

Stage 3 Flow Transmitter

Compressor Stage 1 Suction Temp.
Compressor Discharge Temp

Stage 1 Recycle Gas Liquid Temp

Stage 2 Recycle Gas Liquid Temp

Stage 3 Recycle Gas Liquid Temp

Gear AOP Start/ Stop Pressure

Alarms & 0 Trending

Scale

Min Max
000 200.00
000 | 20000
000 200.00
000 200.00
000 200.00
000 200.00
000 200.00
000 4000.0
000 10000
000 2000.0
5000 | 150.00
000 | 30000
000 200.00
000 200.00
000 200.00
000 200.00

System

Control

Setpoints Status and Bently

Setup





Figure 22 Typical Analog Input Status Screen
The Analog Inputs screen displays the scaled values of all analog transmitters wired to the controller.  The inputs are listed in order as wired to the analog input card.

Scale Min and Scale Max

The scaled value is calculated using the min and max range values for each transmitter.  For a 4-20mA transmitter, the scaled value at 4mA will equal the value shown in the “Scale Min” box.  The scaled value at 20mA will equal the value shown in the “Scale Max” box.
RTD Inputs
[image: image45.png]TE-1231A10A
TE-1231A11A
TE-1231A12A
TE-1231A108
TE-1231A118

TE-1231A12B

[6817
[ 6802
[6701
[6701
[ 6824

66.12

RTD Input Card Slot 13

Motor Stator A Temp RTD
Motor Stator B Temp RTD
Motor Stator C Temp RTD
Motor Stator A Temp RTD
Motor Stator B Temp RTD

Motor Stator C Temp RTD

Alarms & 0 Trending

System

CURRENT USER:
DEFAULT

Setpoints Status and Bently

Setup




Figure 23 Typical RTD Input Status Screen
The RTD Inputs screen displays the actual temperature of all RTD’s wired to the controller.  The RTD’s are listed in order as wired to the RTD input card.  Since the processor derives the temperature directly from the resistance sensed at the RTD, no scaling is required. 
Analog Outputs

[image: image46.png]PY-1231A3A
TY-1231A4A
TY-1231A5A
TY-1231A6A

Analog Output Card Slot 12 (CURRENT USER:

0.00 400 mA
0.00 400 mA
0.00 400 mA
0.00 400 mA
0.00 400 mA
0.00 400 mA
0.00 400 mA
0.00 400 mA

DEFAULT

Discharge Back Pressure Control Valve
Stage 1 Recycle Temperature Control Valve
Stage 2 Recycle Temperature Control Valve
Stage 3 Recycle Temperature Control Valve
SPARE
SPARE
SPARE
SPARE

Alarms & 0 Trending System

Setpoints Status and Bently Setup




Figure 24 Typical Analog Output Status Screen
The Analog Outputs screen displays the scaled (0 to 100%) values of all analog transmitters in the controller.  The outputs are listed in order as wired to the analog input card.

7. ALARM SCREENS

Alarm Setpoint Entry Screens
[image: image47.png]_ GURRENT USER:
verauLT
ALARM SETPOINTS 1
LoLoLmr LoLmT LT HHILMT  Delay (sec)

PT-1231A3 PSIA
PT-1231A0 PSIA

PT-1231A15 PSIG

PT-1231A13 PSIG

PDT-1231A14 PSID

PDT-1231A10 PSID

PDT-1231A11 PSID

PDT-1231A12 PSID

1P - PID Status Alarms & 0 Trending System

HEAMEAI

Control Screens  Setpoints s and Bently Setup




Figure 25 Analog Alarm Setpoint Entry Screen
The analog Alarm Setpoint Entry Screens are used for entering in low alarm / shutdown, and high alarm / shutdown, setpoints and delays. The center value is the current reading of the analog input.
[image: image48.png]CURRENT USER:
DEFAULT

DIGITAL ALARM DELAY SETUP 5

Delay (sec)

Enclosure Low Purge Pressure Alarm

Compressor Oil Sump Low Level Alarm

Gear Oil Sump Low Level Alarm

Seal Oil Pot High Level Alarm

Seal Oil Pot Low Level Alarm

Compressor Stage Drain High Level Alarm

Motor Air Box Pressure Differential Alarm

1P - PID Status Alarms & 0 Trending System

Control Screens  Setpoints s and Bently Setup




Figure 26 Digital Alarm Setpoint Entry Screen

The Digital Alarm setup page allows for limited adjustment of the alarm delay time.
Alarm Navigation Box
[image: image49.png]Active, Unacknowledged Alarms R

DEFAULT

Alarm time.

11/16/2009 10:45:35 PM  PDT-1231A7 Stage 2 Strainer Dff Pressure - Transmitter Out of Range Alarm

11/16/2009 10:45:35 PM  PDT-123148 Stage 1 Suction Strainer Diff Pressure - Transmitter Out of Range Alaim
11/16/2009 10:45:35 PM  HIT-1231A16 Comp Discharge Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A10 Stage 1 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A12 Stage 3 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A15 Stage 3 Upstream Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A11 Stage 2 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A14 Stage 2 Upstream Block Valve Position - Transrmitter Out of Range Alarm

11/16/2009 10:45:35 PM  HZT-1231A13 Stage 1 Block Valve Position - Transrmitter Out of Range Alarm

First Out/
Freeze Menu

P .PID s Alarms & Trending System
Control Screens  Setpoints and Bently Setup





Figure 27 Alarm Navigation Box found on Alarm History and Active Alarms Screen
The Alarm Navigation Box is used on the Alarms History and Active Alarms screen.  Each screen is capable of storing up to 100 alarms, but only 15 can be displayed at a time.  The buttons on the Navigation box are used to control a highlighter, which shows focus on an alarm. The Navigation box is broken down into 3 columns.  The columns are used as follows:

· Column 1 – These 2 buttons are used to move the highlighter to the top or the bottom of the alarm list.

· Column 2 – These 2 buttons are used to move the highlighter up or down 1 page of alarms, or approximately 15 alarm messages.

· Column 3 – These 2 buttons are used to move the highlighter up or down 1 alarm message.

Alarm Silence and Alarm Reset Buttons
The Alarm Banner, Active Alarms, and Alarms History screen all include the ability to silence and reset alarms.  Silencing, or acknowledging, an alarm / shutdown will cause the following to happen:

· Change the alarm indicator from New Shutdown/New Alarm Exists to Shutdown/Alarm Exists.

· Remove the alarm occurrence from the Active Alarms Screen.

· Silence alarm horn (on equipped machines).

Resetting an alarm / shutdown will cause the following to happen:

· Change the alarm indicator on the top right of all screens to No Alarms or Shutdown

· Clear the Active Alarms Screen.

· Silence alarm horn (on equipped machines).

· Energize the Common Alarm Relay (Used for alarm indicator lights and dry-contact interlocking).
· Energize the Common Shutdown Relay (Used for alarm indicator lights and dry-contact interlocking).

 Note:  Once an alarm or shutdown has been tripped, the actual value must return to within the respective alarm and shutdown range before it can be reset on the active alarm or alarm history display.  See the Alarms and Shutdowns section of this manual for a detailed description of the alarm logic
New Alarm Banner

[image: image50.png]New Unacknowledged Alarms Popup

2:28:54 PM 2/17/2010  PT-1231A9 Common Stage 1 Suction Pressure - Transmitter Out of Range Alarm

lence Alarm Active gio=s
Alarms History Alarms Window

w9 7 > piscrnrce| =
Pz 250 S| | R =T
¥y Fmias AT-2s1AG v
== = -
> >
25 1 25 1 250 250
Syncrault R 4, e V1231 AT FETAZaNATT
o ey —
i Ui e P -
a7 i 113 pSia Sty it 50t
1 psin s | & Y R TR
w W
Ist Stage Suction Header 1 »-
250 250
25 o0 F-1ze1A2 GHEFTE &
POTTZEAT _ —
b T Pz
Compressor Status y |
Frizsiaz 250 250 60 PSIA ]
Compressor Running in Alarm REESEE ERESTS 3rd Stage Suction Header
500 ron
PRV Override Status b
el ETTN <) o
FTAZAT 260 S| -

PUAZIAT  RZ-1231A14 2nd Stage Suction Header

Alarms & Trending

Setpoints and Bently




Figure 28 New Alarm Banner showing an analog shutdown
The New Alarm Banner is displayed at the top of the HMI display any time a new alarm or shutdown occurs.  The New Alarm Banner is a “Pop-Up” style window and includes the ability to Silence or Reset Alarms.  Analog Alarms and Shutdowns are displayed in the format: Tag, Description, Low / High Reading Alarm / Shutdown.  Discrete Alarms and Shutdowns are displayed using a description of the alarm / shutdown and the tag if applicable.
Note:  Active Alarms cannot be reset until the error or conditions that caused the alarm to occur have been corrected.
Active Alarms
[image: image51.png]Active, Unacknowledged Alarms R

DEFAULT

Alarm time.

11/16/2009 10:45:35 PM  PDT-1231A7 Stage 2 Strainer Dff Pressure - Transmitter Out of Range Alarm

11/16/2009 10:45:35 PM  PDT-123148 Stage 1 Suction Strainer Diff Pressure - Transmitter Out of Range Alaim
11/16/2009 10:45:35 PM  HIT-1231A16 Comp Discharge Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A10 Stage 1 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A12 Stage 3 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A15 Stage 3 Upstream Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A11 Stage 2 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A14 Stage 2 Upstream Block Valve Position - Transrmitter Out of Range Alarm

11/16/2009 10:45:35 PM  HZT-1231A13 Stage 1 Block Valve Position - Transrmitter Out of Range Alarm

First Out/
Freeze Menu

P .PID s Alarms & Trending System
Control Screens  Setpoints and Bently Setup





Figure 29 Active Alarms Screen showing alarms in yellow and shutdowns in red
The Active Alarms screen display all active, unacknowledged alarms and includes the ability to silence and reset alarms.  Up to 100 unacknowledged alarms can be viewed using the alarm navigation box.  
Alarms and Shutdowns are displayed in the format:  Alarm Date, Alarm Time, Tag ID, Description, Low/High Reading Alarm/Shutdown.  Discrete Alarms and Shutdowns only display a tag ID when applicable.
Alarms History

[image: image52.png]Alarms History CURRENT USER:

DEFAULT

Alarm time.

11/16/2009 10:45:35 PM  PDT-1231A7 Stage 2 Strainer Dff Pressure - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  PDT-123148 Stage 1 Suction Strainer Diff Pressure - Transmitter Out of Range Alaim
11/16/2009 10:45:35 PM  HIT-1231A16 Comp Discharge Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A10 Stage 1 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A12 Stage 3 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A15 Stage 3 Upstream Block Valve Position - Transritter Out of Range Alarm
11/16/2009 10:45:35 PM  HZT-1231A11 Stage 2 Downstream Block Valve Position - Transmitter Out of Range Alarm
11/16/2009 10:45:35 PM  HIT-1231A14 Stage 2 Upstream Block Valve Position - Transrmitter Out of Range Alarm

11/16/2009 10:45:35 PM  HZT-1231A13 Stage 1 Block Valve Position - Transrmitter Out of Range Alarm

First Out/
Freeze Menu

System P .PID s Alarms & 0 Trending System

Overview Control Screens  Setpoints Status and Bently Setup




Figure 30 Alarms History Screen showing alarms in yellow and shutdowns in red
The Alarms History screen display all acknowledged alarms and includes the ability to silence and reset active alarms.  Up to 100 acknowledged alarms can be viewed using the alarm navigation box.  Alarms and Shutdowns are displayed in the format:  Alarm Date, Alarm Time, Tag ID, Description, Low/High Reading Alarm/Shutdown. Discrete Alarms and Shutdowns only display a tag ID when applicable.  

The Clear History Button is used to clear all alarms from the Alarms History Display box.
First Out / Freeze
[image: image53.png]



Figure 31 Compressor Shutdown First Out Screen with links to freeze screens at bottom
The first out screen identifies the specific fault that has shutdown the compressor.  The fault description, tag number, and date / time stamp are displayed.  The first out fault will not be reset until the shutdown has been reset from the active alarm screen. 
Freeze Screens

On the lower half of the First-Out Screen are buttons to view instantaneous data captured at the moment of a system shutdown. This data is updated after every system shutdown.  The values displayed on the Freeze Screens are in a format identical to the I/O data screens used for real time data.

8. TRENDING SCREENS

Purpose of Trending
Trending screens are used to view historical data in a graphical format.  The primary purpose(s) of viewing the trended information is troubleshooting machine events (alarms, shutdowns, etc), tuning PID Loops, and record keeping.  All Analog Input, Analog Output, and RTD temperatures can be viewed.  Trending snapshots are shown in a 10 minute format.
Screen Features include the ability to go back in time several hours to view historical data, view up to 8 pens at a time, pause, and scale adjustment.

Trending Screen
[image: image54.jpg]Pen Scale Increase Buttons;

A
Pen Scale Decrease Buttons =

Pen Color Assignment Chart|





Figure 32 Typical Trending Screen for 4-20mA transmitters, comments show location of buttons on screen
Pen Color Assignment Chart

Used to show which pen value is assigned to which pen.
Pen Scale Increase / Decrease Buttons

The Pen Scale Increase / Decrease Buttons are used to zoom in and zoom out the Pen Scale Value.  The top 2 buttons increase and decrease the max scale value.  The bottom 2 buttons increase and decrease the min scale value.  Scaling can be adjusted by 50 units at a time (50 PSI, 50%, 50Amps).
Trend Control Buttons
The trend control buttons are used to control the time axis of the chart.  There are 5 trend control buttons which include:
· Home – Moves the current snapshot to the current time on the trend chart. 
· Go Left – Move the time snapshot left (back in time), 10 minutes. 

· Pause / Run – Pauses or un-pauses the real-time trend.

· Go Right – Moves the time snapshot right (forward in time), 10 minutes.

· End – Moves the current snapshot to the end of the real-time trend.
9. SETUP SCREENS - Commissioning

HMI Display Setup
[image: image55.png]_ Setup HMI GURRENT USER:
veFsLT

Screen Protector. PLC Date and Time Setup———
Delay Time to Start
Screen Protector 6 |/ 25|/ 2008
30-300 min
1m | [ | [ 2009
30

16 | = 26 | - 22
5 [ 14 [

Set PLC Date and Time

Panelview Terminal Setup

Terminal Configuration Screens
(Update Program, TCP/IP Config).

Requires YORK login Credentials

Go To Panelview Plus Panel
Configuration

P .PID Status Alarms & 0 Trending System
Control Screens  Setpoints s and Bently Setup





Figure 33 HMI Display Setup Screen
Screen Protector

The screen protector is used to prevent screen “burn”, primarily on the overview screen.  If the overview screen is active for the delay setpoint (30 – 300 minutes), a temporary logo screen will appear for 60 seconds, and then the overview screen will reappear.  The screen protector feature can be disabled if desired.
PLC Date and Time Setup

This function is used to configure the PLC Date and Time to match real-world date and time.  PLC Date and Time is primarily critical for any time clock specific features or controls, and DCS communications.
PanelView Plus Panel Configuration

This function is used to shut down the HMI operator interface screen and enter the PanelView Plus panel configuration.  The PanelView Plus panel configuration can be used to access the following functions:

· Load application from flash card

· Change panel regional settings

· Change TCP/IP address for networking and communications

· Change screen saver settings

· Enable / Disable screen cursor

· Adjust display intensity

· View event logs
· View terminal status
AOP Setpoints

[image: image56.png]New Setup Compressor and Gear AOP e

-Compressor AOP-
Comp AOP /S Diff Pressure | 33.00 PSIA
Start Comp AOP if Diff. Pressure is< [ 3000 PSIA (Alarm Setpoint)

Run Comp AOP For 100 Sec. on Low Pressure Post Lube For 120 Sec.

Comp Supply Oil Differential Pressure | 33.00 PSIA
Compressor Start Permissive | 20.00 PSIA (Shutdown Setpoint)

Run Comp AOP For 2 Min.  Every 8 Hours When Comp Not Running

Gear AOP-
Gear AOP s/S Pressure | 1400 PSIA
Start Gear AOP if Pressureis < | 1300 PSIA (Alarm Setpoint)

Run Gear AOP For 100 Sec. Post Lube For 120 | sec.

Gear Bearing Oil Inlet Press | 17.00  PSIA
Compressor Start Permissive | 10.00  PSIA (Shutdown Setpoint)

1P - PID Status Alarms & 0 Trending System

Control Screens  Setpoints s and Bently Setup




Figure 34 Compressor and Gear AOP Setup Screen
Overview of AOP control

This screen is intended to give the startup technician flexibility in configuring the oil pump operation to the particular job.  Time delays can be changed on this screen; however, pressure setpoints must be changed on the Pressure Alarms screen.   The description of operation is inherent in the screen itself, therefore, no further operating descriptions are defined.
NOTE:  The machine Logic Diagram contains more detailed information on the control sequence of the Gear and Compressor Auxiliary Oil Pump.
Compressor AOP Setpoints

The following is a list of setpoints displayed on compressor AOP setup section.  Some of these setpoints can only be adjusted from the alarm setpoints screen:
· Start Comp AOP if Diff. Pressure is < - When the compressor is running and the Compressor AOP S/S Diff Pressure is below this value, the AOP will start.  This setpoint can only be changed from the Alarms setpoint screen that has the Compressor AOP S/S Oil Diff. Pressure.
· Run Comp AOP for - In low oil pressure conditions, the compressor AOP will run for this length of time to increase the AOP pressure to maintain safe operating conditions and prevent an alarm or shutdown.
· Post Lube for – When the compressor is stopped or shutdown, the compressor AOP will run for this length of time to maintain adequate lube oil pressure.
· Compressor Start Permissive – The Compressor Journal Bearing Oil Inlet Diff Pressure must be above this value to energize the permissive that will allow the compressor to start.  This setpoint can only be changed from the Alarms setpoint screen that has the Compressor Journal Bearing Oil Inlet Diff. Pressure.
· Run Comp AOP for xxx Min. Every xx Hours When Comp Not Running – When the compressor is not running, these parameters define how frequent, and the length of time, that the compressor AOP will run to maintain adequate lube oil pressure to system components.
Gear AOP Setpoints

The following is a list of setpoints displayed on Gear AOP setup section.  Some of these setpoints can only be adjusted from the alarm setpoints screen:
· Start Gear AOP if Diff. Pressure is < - When the compressor is running and the Gear AOP S/S Pressure is below this value, the Gear AOP will start.  This setpoint can only be changed from the Alarms setpoint screen that has the Gear AOP S/S Oil Pressure.
· Run Gear AOP for - In low oil pressure conditions, the Gear AOP will run for this length of time to increase the AOP pressure to maintain safe operating conditions and prevent an alarm or shutdown.
· Post Lube for - When the compressor is stopped or shutdown, the Gear AOP will run for this length of time to maintain adequate lube oil pressure.
· Compressor Start Permissive - The Gear Journal Bearing Oil Inlet Pressure must be above this value to energize the permissive that will allow the compressor to start.  This setpoint can only be changed from the Alarms setpoint screen that has the Gear Journal Bearing Oil Inlet Pressure.
Setup Page 1

[image: image57.png]System Setup Page 1 CURFENT VSR

——PRV Constants Setup Surge Control Setup
Suction Comparator

Delta Setpoint Add to Min PRV Bias After Each Surge 5 %
Operating Min. 5.00 Surge Input Delay Timer Preset 1 Sec.
R .60 Surge Reset Timer Preset 30 Sec.
Increase Hot Gas Valve at 1st Surge 33%
PR2 . 6.90 B
Increase Hot Gas Valve at 2nd Surge 100%
sP1 | 100.00
sr2 | 13.00 — Misc.Control Setup:
Hot Gas Valve Shutdown Position 0 %
Pressure Ratio (PR) | 6.90
e
Calc. Min. Bias 0.00 Motor Current Force Unload PRV 2 )
Calculated Min. 13.00 Sump Vent Valve Open Duration Timer 30 Min.
PRV Position 0 %
Qil Cooler Valve Open Duration Timer 30 Sec.

Alarms & 0 Trending System

Setpoints Status and Bently Setup




Figure 35 System Setup Page 1 Screen
PRV Constants Setup

The PRV constants Setup section is used to view and adjust the setpoints that control the operation of the PRV.  Setpoints in this section include:

· Suction Comparator Delta Setpoint – value for the comparator that compares Local (PT-1231A0) & Common Header Suction Pressure (PT-1231A9) to determine which one will be used for capacity control.
· Operating Min. – This is the fixed operating minimum PRV position.  The Control Minimum PRV will not fall below this setpoint with or without bias.  (0% when not running, 5% when running)
· PR1 - Maximum Pressure Ratio
· PR2 - Minimum Pressure Ratio
· SP1 - PRV position at maximum pressure ratio
· SP2 - PRV position at minimum pressure ratio
· Pressure Ration (PR) - (Pressure Ratio) = Discharge Pressure / Suction Pressure
· Calc. Min. Bias - A setpoint entry will increase or decrease the Control Minimum PRV value (explained below) that is calculated in the processor.   A negative entry will decrease the minimum PRV.  A positive entry will increase the minimum PRV.
· Calculated Min. - Displays the Minimum Pre Rotation Vane Position 0 - 100 %.  This value is calculated from the processor using the compressor suction pressure, discharge pressure and other constants of the compressor capacity.  The PRV's will not fall below this setpoint during normal operation or during force unload conditions. The hot gas valve will begin to open when the PRV closes to this minimum value.
Surge Control Setup

NOTE: For a more detailed explanation of surge control refer to the YORK Process Systems – Application Engineering Standard 1500.12 
· Add to Min PRV Bias After Each Surge - On the first event, the respective hot gas valve is opened to the preset value (default 25%) and the surge bias (see below) is added to the PRV Control Minimum.  
· Surge Input Delay Timer Preset - This adjustable time setpoint defines the length of time in-between recorded surges.  No matter how many times the surge input opens and closes during this time, only one surge event will be recorded.  This prevents multiple surges from occurring due to chatter of the discrete surge input.  (Default 10 seconds, adjustable 0-30 seconds)

· Surge Reset Timer Preset - This adjustable time setpoint defines the length of time to accumulate surge events.  This timer is started with the first surge event.  Subsequent surge events must occur before this preset time in order to count as a second or third surge.  If this time expires, the surge counter will reset to zero.  Any surge that takes place after this time expires will be counted as the first surge event.

· Increase Hot Gas Valve at 1st Surge - After the first surge event the recycle gas valve is adjust this amount.
· Increase Hot Gas Valve at 2nd Surge - After the second surge event the recycle gas valve is adjust this amount.
Misc. Control Setup

· Hot Gas Valve Shutdown Position – This is the position the Recycle Gas Valve will go to on a system shutdown.
· Motor Current Force Unload PRV (% / Second) – In High Motor Current Situations, the PRV is Unloaded to stabilize the motor current.  This setpoint adjusts how far the PRV is unloaded every second during a force unload condition.
· Sump Vent Valve Open Duration Timer – This is the Length of time it would take, in minutes, to fully open the Sump Vent Valve from 0 to 100%.  The default value for this timer is 30 minutes. The Sump Vent Valve begins to open 30 seconds after the Compressor Motor Auxiliary input is energized.
· Oil Cooler Valve Open Duration Timer – This is the Length of time it would take, in seconds, to fully open the Oil Cooler Valve from 0 to 100%.  The default value for this timer is 30 seconds.
Setup Page 2

[image: image58.png]_ System Setup Page 2 CURFENT VSR

Rate of Change Filters-

Limit PRV Increase Rate of Change to 33 | ke
Limit PRV Decrease Rate of Change to 33 | ke
Limit HGV Decrease Rate of Change to 3.30 | hper

second

Slow Suction Pulldown.

On Startup if Slow Pulldown is enabled 5.00 % per
Recycle Gas Valve will Deacrease - second
Terminate Slow Pulldown when 40.00 PSIA

Suction Pressure is less then

Actual Suction Pressure
Recycle Gas valve is closed,

Starting Capaci
Hold PRV's at m

Then Subtract 1 PSI  every 1 Min.

1P - PID Status Alarms & 0 Trending System

Control Screens  Setpoints s and Bently Setup




Figure 36 System Setup Page 2 Screen
Rate of Change Filters

Rate of Change filters are used to prevent the PRV and Hot Gas Valve from ramping open or close to fast.  In the case of the Hot Gas Valve, only the decrease rate is adjusted to allow rapid opening in the case of surge conditions.  To allow complete PID control over the valves, enter 100% / second.
NOTE: The PID Loop Gain and Reset setpoints control the ramping of all valves.  These filters are used to prevent ramping of the valve open or closed too fast.
Slow Suction Pulldown

· On Startup if Slow Pulldown is enabled Recycle Gas Valve will decrease (% / second) –The recycle gas valve will ramp closed at this interval.
· Terminate Slow Pulldown when Suction Pressure is less then –   If the suction pressure falls below this value, then Slow Pulldown will be terminated and normal system operation will resume.
· Hold PRV’s at minimum until Recycle Gas Valve is closed, then subtract xx PSIG ever xx Sec. - The PLC will then subtract a set amount (in PSIG) from the capacity setpoint at a rate specified by the technician.  The result will be the new capacity control setpoint.
· Slow Pulldown Enable / Disable – Located on the PRV PID Screen this toggle button is used to enable or disable the slow suction pressure Pulldown feature of the compressor.
Note: Upon slow Pulldown activation, the actual suction pressure will be written to the capacity control setpoint to prevent the PRV’s from opening while the recycle gas valve is ramping closed.
Setup Page 3

[image: image59.png]_ System Setup Page 3

Sump Temp Permissive.

CURRENT USER:
DEFAULT

Suction Pressure ATL or Soft Start
To Start Compressor, 0il Sump Temp

Compressor Starts with Soft Start unless
Must be greater then

Suction Pressure is greater then

75.0 °F 54.00 Psl
AND 0il Sump Temp Must be > ai
T e e e Forced into ATL Starting Mode

Bently Trip Multip

After Compressor Startup,
De-Energize Bently Nevada
Multiplier after

10 Sec.

—Alarm | Shutdown Warning.

Flash Dry Contacts with New Alarm
Shutdown

0

No
Yes

1P - PID s Alarms &

Trending System
Control Screens  Setpoints and Bently Setup




Figure 37 System Setup Page 3 Screen

Sump Temp Permissive

The compressor oil sump temperature must be greater than this setpoint to allow the compressor sump temp permissive signal to be true.  Oil heaters are used to maintain adequate sump temperature during system shutdown in cold climates.  Also, the oil sump temperature must be greater than the value of (Saturated Suction Temperature at suction pressure) + (30F)
Bently Trip Multiplier

Most of the motor temperatures and vibrations are monitored and alarmed using a Bently Nevada Vibration Monitoring System.  During system startup vibration levels are much higher than normal, and often higher then system shutdown values.  The Trip Multiplier is a dry-contact signal used to prevent nuisance alarms and shutdowns during system startup.   When the trip multiplier signal is energized, the Bently Nevada system uses a multiplied value (default 1x) for shutdown setpoints.  For example, when the Trip Multiplier signal is energized, a Vibration Shutdown setpoint of 2 mil with a trip multiplier setting of 2x, would be 4 mil during system startup.  The compressor motor auxiliary contacts must be energized for 10 seconds until the trip multiplier signal will de-energize.
Alarm / Shutdown Warning

This system provides the customer with a dry set of contact to monitor the alarm and shutdown status of the control system.  These contacts are normally energized and will open when an alarm or shutdown occurs.  The options for these contacts are as follows:

Flash with new occurrence (NO) – When set to no the alarm and shutdown relays will remain de-energized anytime an alarm or shutdown is active.

Flash with new occurrence (YES) – This option will open and close the relay repeatedly every second when a new alarm or shutdown occurs.  When the alarm or shutdown is acknowledged the relay will be de-energized.  This option can be enabled in order to differentiate between an existing and new alarm.

Note:  The compressor shutdown light and alarm light will respond according to dry contact setup.
Suction Pressure ATL or Soft Start 

The Suction Pressure ATL or Soft Start selection setpoint will determine which start signal will be sent to the compressor motor switchgear based on the suction pressure at startup.
· Compressor Starts with Soft Start unless Suction Pressure is greater then ##.## PSI – If the suction pressure is above 54 (adjustable 0 to 200) PSIA the ATL (Across The Line) start signal will be sent. If the pressure is less than the set value it will issue the Soft Start signal.
· Push To Force into ATL Mode –This button is used to ignore the setpoint & force the ATL (Across The Line) signal to be sent. 

Note: Caution is to be used when forcing this mode especially if more than one compressor is forced at the same time.
Setup Page 4
[image: image60.png]System Setup Page 4 GURRENT USER:

DEFAULT
PID Control Setup.

Max Increase Max Decrease Operating  Mtr Current  HGVF Output]
Action Direction % per Second % per Second  Minimum Unload Bias% Disable

] o flema - 100 3.3

33

33 33 5 -50

PIDA 3.3 3.3 5 50
] Fonuar | 3.3 5
~o7 [ 3.3 5
N

Alarms & Trending System

Setpoints s and Bently Setup




Figure 38 System Setup Page 4 Screen
Action

Determines the response of the PID loop.  Forward action will be a direct action loop, if the pressure or temperature increases the output will increase.  For Reverse acting as the pressure or temperature increases the value will decrease.
Direction

Determines the direction of the PID loop for the valve.  If 4mA = 100% then the valve will be open at 4mA, if 20mA = 100% then the valve will be open at 20mA.

Rate of Change Filters

Rate of Change filters (Max Increase & Max Decrease) are used to prevent the PID Valves from ramping open or closed too fast.  To allow complete PID control over the valves, enter 100% / second.
NOTE: The PID Loop Gain and Reset setpoints control the ramping of all valves.  These filters are used to prevent ramping of the valves open or closed too fast.
Operating Minimum
The Minimum the valve can be closed. Default 5% (adjustable 0 to 100%) see 669D0127 sheet 8
Mtr Current Unload Bias

The Motor Current Unload Bias will change the rate of the valve unloading during a Current Force Unload condition. Default 0 (adjustable -50% to 50%)

HGVF Output Disable

The Hot Gas Valve Flow Output Disable will keep the PID (PID 5, 6, or 7) output at 0% if the corresponding Flow Controller (PID 1, 2, or HGVF) is closed more than this setpoint Default 5% (Adjustable). This protects against adding Hot Gas Liquid Injection when you have reduced flow preventing a surge condition. see 669D0127 sheet 7
NOTE: The Hot Gas Valves are Reverse Acting (4ma = Open) so the logic box “IS FLOW CONTROLLER FIC-1231A#A OUTPUT < 95%?” is understood to be the inverse value for this setpoint. 
Setup Page 5
[image: image61.png]System Setup Page 5 CURFENT VSR
Hot Gas Valve Calculation Values

-Suction STAGE 2 STAGE 3-
PR1 8.60 PR1 8.60 PR1 8.60
PR2 6.90 PR2 6.90 PR2 6.90
FLOMAX1 1175 FLOMAX1 3425 FLOMAX1 2375
FLOMIN1 825 FLOMIN1 2404 FLOMIN1 1668
Surge Bias 5.00 Surge Bias 5.00 Surge Bias 5.00

P .PID Status Alarms & Trending System

Control Screens  Setpoints and Bently Setup




Figure 39 System Setup Page 5 Screen

Suction
The Suction Hot Gas Valve PR1, PR2 FLOMAX1, & FLOMIN1 are constants used in flow calculations. These values are located in a table on 669D0127 sheet 10.
Stage 2 & 3
The PR1, PR2 FLOMAX1, & FLOMIN1 are constants used in flow calculations. These values are located in a table on 669D0127 sheet 9.
Surge Bias
The Surge Bias is the percentage that is added to the Minimum Compressor Flow while in a surge condition. Default 5% (Adjustable 0 to 100%)

10. MODBUS DCS ADDRESSING

Modbus Port Settings and Connection

Connection to the Frick PLC is done through a ProSoft MVI56-MNETR module.  A DB9 pin to RJ45 adaptor is included for ease of connection.  

For a detailed listing of Modbus Addresses see:

Document Name:    C1231X Modbus Mapping

Document Number: 13706-MUS-INS-PH-0013-C1231X




























































































































































40

