YORK

Process Systems
Installation Operation Maintenance Manual

YORK

Process Systems
Installation Operation Maintenance Manual


FIELD REFRIGERANT PIPING BY CUSTOMER

Refrigerant piping required to interconnect components of field installed systems must be designed and installed to the Applicable Codes and Standards (REF ASME B31.5 or ASME B31.3).

All pipe and fittings should be cleaned prior to installation.  Piping should be cleaned internally to SSPC-SP6 " Commercial Blast Cleaning" or if not available to SSPC-SP3 "Power Tool Cleaning".  Cleaned pipe should be capped to maintain cleanliness.

It is very important that every effort be made to prevent moisture, air, grit or other foreign particles from entering the system during installation.  Clean the inside of all pipe welds.  A Tig Root pass should be used on all welded pipe joints which cannot be cleaned from the inside.  Be especially careful to prevent dirt from entering any part of the lube oil system.

Do not trap any part of the suction line for any reason.  However, minimal traps in the discharge line would be unwanted, but acceptable.  Verify that all field piping is completed and that all field installed valves are in their normal operating position before attempting to start the compressor.

CAUTION :
DO NOT HYDROSTATICALLY TEST FIELD REFRIGERANT PIPING.  PRESSURE TEST AND EVACUATE IN ACCORDANCE WITH INSTRUCTIONS IN SECTION 5 OF THIS MANUAL.
























































































































































































Section-03 data
Status: Released
8 Aug 00  Ver 1.04


