YORK

Process Systems
Installation Operation Maintenance Manual

YORK

Process Systems
Installation Operation Maintenance Manual


INSTALLING AND GROUTING PACKAGED SKIDS

The steel base is to be bolted down to a concrete substructure with anchor bolts at locations shown on the drawing. Sub-structure must be level, and it must be grouted to assure continuous contact with all accessible full depth members. This is essential on structural members supporting drivelines. It is recommended that the steel base to be filled with concrete to top of base in all pockets that are accessible and free of piping (allowing access for drain valves, etc.)

[image: image1.png]ANCHOR BOLT

HEAVY HEX NUT

WASHER

SKID_MEMBER

sRoUT

FOUNDATION

Typical Installation



Anchor bolts should be positioned in ferrules fabricated from 2’ pipe (or equivalent). The ferrule should be flush with the surface of the rough level. Soft wadding (or equivalent) should be used to center the bolt in the ferrule during placement of the package unit. This provides bolt flexibility to allow for final position and manufacturing tolerances. After final position has been obtained, the grout should flow into the ferrules and lock the anchor bolts into position.

























































































































































































Installation and Grouting Packaged Skids.doc
Status: Released
21 Jan 02  Ver 1.05


