	YORK

Process Systems
	Installation Operation Maintenance Manual


	YORK

Process Systems
	Installation Operation Maintenance Manual



WARNING:
THE MAIN DRIVE MOTOR SWITCHGEAR MUST BE LOCKED OPEN AND TAGGED OUT BY A QUALIFIED ELECTRICIAN PRIOR TO PERFORMING THE TESTS IN THIS SECTION.  CARE MUST BE TAKEN TO INSURE THAT NO STARTER IS ENERGIZED WHILE PERSONNEL ARE WORKING ON THE AFFECTED EQUIPMENT.

CAUTION:
Do not hydro test YORK supplied equipment.

CAUTION:
Be sure to use a pressure regulator between any nitrogen bottle and the system being pressurized to prevent over pressure.  Otherwise, overpressure may lift the relief valves.

CAUTION:
Do not use a halide torch, electronic leak detector or sulfur sticks in a hazardous area.  Either will develop local temperatures capable of igniting flammable gases.

CAUTION:
Care must be taken not to damage system seal materials or components by using incompatible leak test media.  For example, do not use R-22 to leak check ammonia systems.  R-22 may react with system oil or elastomers to cause a chemical incompatibility with ammonia.  The result may cause the formation of compounds that will be detrimental to operating components.  Sulfur sticks may be used to pinpoint leaks in a non-hazardous area.  Do not use sulfur sticks in a N.E.C. hazardous area.  Litmus paper and soap bubbles may also be used to help pinpoint ammonia leaks.  Similarly, do not use propylene to leak test a propane system or vice versa, etc.  Contact the factory for guidance.

CAUTION:
Relief valves and rupture disks must be removed and their associated connections sealed during pressure/leak testing at any pressure higher than approximately 80% of their set pressure.  Otherwise, these devices will open and must be replaced or recalibrated per manufacturer’s recommendation.

CAUTION:
Special shaft seals with support system piping require special testing to avoid damage to the seal (refer below).

LEAK TESTING
Following strength testing and prior to commissioning, all refrigerant pipework and vessels should be thoroughly leak tested.

The purpose of the test is to prove the integrity of the installed system prior to evacuation and the introduction of the refrigerant charge.  It is not a mechanical strength test and must not be considered as such, since all refrigerant pipework shall have been hydraulically/pneumatically strength tested, cleaned and dried prior to installation.

NOTE:
This test shall only be performed prior to the application of insulation on vessel, piping or tubing joints (E.G. flanged, welded, threaded or cinched).
Field Erected Piping
NOTE:
If the refrigeration system is completely manufactured and assembled at the factory, the Code pressure test is not required.  The Code test was completed at the factory.

Field erected piping is piping that is welded or assembled at the installation site.  An example of this is piping that interconnects packages.  In such case, the applicable ASME Piping Code requires that the piping shall be tested at a pressure equal to the design pressure of the component with the lowest design pressure in that piping section.  In the case of a centrifugal system with no compressor isolation valves, the test shall be conducted at the low side design pressure.  Conduct the test as follows:

Remove system relief valves as they will open under the required test pressure.

CAUTION:
Any conventional refrigeration relief valve that has been lifted under pressure must be considered compromised and must be replaced.

Open all manually operated valves.  Close all vents and drains.  Make sure all flange closures are rated for the test pressure.  If there is any question, contact the York Process Systems Service for clarification.

All relief devices (relief valves and rupture disks) should be removed initially and any openings or connections not used must be adequately sealed with caps, plugs or blind flanges.

Check that all control and pneumatically actuated valves are correctly installed in respect of the required direction of flow and are free to operate.  Install calibrated test gauge(s) to permit verification of system test pressure.

The test medium should be dry nitrogen.  Do not use mixtures of air and refrigerant due to possible explosion hazard.  Do not hydrostatically test York refrigeration components using water without prior written approval from York.

For safety purposes all personnel, except those immediately concerned with execution of the test, should be excluded from an area of at least 50 feet (15 meters) around the package during the test.  The test should preferably be carried out outside normal working hours.  The test area should be roped off and warning notices stating "CAUTION - HIGH PRESSURE TESTING" displayed at all points of access.

Although factory leak tested prior to shipment, the package piping and components may have to be included within the scope of this pressure test if it cannot be isolated with a permanent valve or spectacle blind.

NOTE:
YORK recommends that this test be conducted under the guidance of a YORK Service Representative.  A record of the test and the results should be kept on file for future reference.

A test pressure in accordance with the applicable ANSI/ASME Piping Code (1.1 x maximum working pressure) shall be used.  Test apparatus shall include a pressure limiting relief device, pressure control valve with gauge, or other device for preventing any pressure being imposed over that prescribed.

The design working pressure specified on all vessel data plates must be checked to ensure compliance of system test pressure.  Check the ratings of ANSI flanges to make sure ratings agree with vessel markings.  If there is any question, contact York Process Systems Service for clarification.

Where no markings are found the pressure test should not be attempted.  A thorough examination of the system is recommended to ensure that the system is safe to pressurize.

Using a valve on the charge line, or an equivalent low point connection, pressurize the system slowly to a preliminary pressure, about 25 psi (1.7  Bar).  A preliminary visual leak check shall be made using a soap solution.

Thereafter, the pressure shall be gradually increased in steps until the test pressure (1.1 x DWP) is reached, holding the pressure at each step long enough to equalize piping strains. The test pressure must be maintained for at least 10 minutes. The pressure shall then be reduced to the design pressure before examining for leakage.   Follow the instructions provided in the governing piping code.

Any leakage detected at any stage of the pressure test shall be made good before the test is continued.

CAUTION:
A leak will require the full release of pressure in the section of pipework to be repaired before it can be rectified.  The full procedure must be repeated for the section repaired.  If unable to isolate the section safely the entire system should be de-pressurized before repair work is commenced.
By adding glycerin to the soap solution, the bubble action is improved.  For flange joints it may be advisable to tape the joints and put a small hole through the tape between the flanges to improve leak detection.

The test pressure (1.0 x DWP) must then be held for a minimum period of 4 hours with no change in pressure other than that which may result from changes in ambient temperature.

On completion, release the test gas slowly from the lowest point of the system.  Install any system relief valves that were removed for this test.  (Ensure that all relief valves are correctly set to lift at their specified pressures.)

System Leak Test 

(For any refrigerant, including ammonia (NH3/R717) or for any system in a hazardous area.)

NOTE:
If the refrigeration system is completely manufactured and assembled at the factory, the leak test must be conducted anyway to insure a leak-tight system.

NOTE:
If the above ASME Piping Code pressure test has been conducted, this leak test is not required.

The system should now be leak tested using oxygen free nitrogen.  The pressure should slowly be increased until the pressure reaches 80% of the lowest relief valve setting.

Re-check all joints for tightness using a soap solution, particular attention should be paid to relief valves.   Repair any leaks found and re-test until the system is leak tight.

CAUTION:
A leak will require the full release of pressure in the section of pipework to be repaired before it can be rectified.  The full procedure must be repeated for the section repaired.  If unable to isolate the section safely the entire system should be de-pressurized before repair work is commenced.

On completion slowly release the test gas as before.  If, however, vacuum dehydration is not to commence immediately, a holding charge of 15 psig (1 Bar G) should be left in the system to eliminate risk of moisture ingress.

 A certificate of the satisfactory gas leak test shall be witnessed by the customer and the York Commissioning Engineer and issued by the engineer in charge of testing.  Use the form in the front of this manual.

Insulation of the system may now be commenced, however, flanged joints must not be covered until vacuum dehydration has been completed.

For Non-Hazardous Areas and Any Refrigerant Except Ammonia
The system should now be leak tested using an oxygen free nitrogen/refrigerant gas mixture (ammonia must not be used).  The system should first be charged with a quantity of refrigerant then the pressure should be slowly increased to 80% of the lowest relief valve setting using oxygen free nitrogen.

Re-check all joints for tightness using electronic leak detector.  Particular attention should be paid to relief valves.  Repair any leaks found and re-test until the system is leak tight.

CAUTION:
A leak will require the full release of pressure in the section of pipework to be repaired before it can be rectified.  The full procedure must be repeated for the section repaired.  If unable to isolate the section safely the entire system should be de-pressurized before repair work is commenced.

On completion slowly release the test gas as before.  If, however, vacuum dehydration is not to commence immediately, a holding charge of 15 psig (1 Bar G) should be left in the system to eliminate risk of moisture ingress.

A certificate of the satisfactory gas leak test shall be witnessed by the customer and the York Commissioning Engineer and issued by the engineer in charge of testing.  Use the form in the front of this manual.

Insulation of the system may now be commenced, however, flanged joints must not be covered until vacuum dehydration has been completed (ref. to Para. 4.2).

Leak Test of Shaft Seal Support Systems (where applicable, follow manufacturer's instructions when avaialble)

This specification provides testing instructions for special shaft seal support systems.  These instructions are superseded by any instructions provided on project drawings or documents.  Special in this context refers to seals that utilize special piping and components connected to the seal cover plate for the purpose of draining, venting and or lubricating any portion of the seal.

CAUTION: SHAFT SEALS ARE NOT DESIGNED TO WITHSTAND REVERSE PRESSURE DIFFERENTIAL.  "REVERSE" HAS DIFFERENT MEANINGS FOR TANDEM SEALS AND DOUBLE SEALS.

Before pressure and vacuum testing, the following information must be obtained: Seal type (E.G. tandem or double - if the seal is not indicated as one of these types then seek clarification from Engineering.  Also, the seal piping system proof and leak test pressure must be known.  After the seal type has been identified, follow the applicable instruction below.

TANDEM SEAL OR SINGLE WITH OUTBOARD BARRIER
: The support system for a these seals is designed to operate at a lower pressure than the compressor.  The seal piping must be held to a pressure equal to or lower than the compressor pressure.  NEVER PRESSURIZE THE SEAL PIPING WITHOUT EQUALIZING IT TO THE COMPRESSOR.  It is not necessary to pressurize the seal piping when the compressor is pressurized.  To pressure test the seal piping, proceed as follows:

Connect an equalizing line with an isolation valve from the seal piping to the compressor piping.

Install a test pressure gauge on the seal piping and the compressor piping.

Pressure test the compressor system and the seal piping in accordance with instructions given earlier in this section.  Increase pressure per standard procedure until the compressor and seal piping have reached the specified seal piping proof test pressure.  After piping pressure equalizes, reduce to the seal piping leak test pressure, and leak test the seal piping and components.  

Isolate the seal piping from the compressor using the valve referenced above.

When the seal piping is confirmed tight by testing, vent the pressure slowly from the seal piping to atmospheric pressure.

If the seal system test pressure is lower than the compressor piping test pressure, proceed to increase the compressor system pressure and leak check according to standard procedure.  The seal piping should be equalized to atmosphere during this part of the test.  When the compressor system piping is confirmed tight by test, vent the pressure slowly.  The test is complete.

DO NOT VACUUM TEST THE SEAL PIPING.

DOUBLE SEAL: The support system for a double seal is designed to operate at a higher pressure than the compressor.  The seal piping must be held to a pressure equal to or higher than the compressor pressure.  NEVER PRESSURIZE THE COMPRESSOR PIPING WITHOUT EQUALIZING IT TO THE SEAL.  It is not necessary to pressurize the compressor piping when the seal piping is pressurized.  To pressure test the system, proceed as follows:

Connect an equalizing line from the seal piping to the compressor piping.

Install a test pressure gauge on the seal piping and the compressor piping.

Pressurize the compressor and the seal piping in accordance with standard procedures.  Increase pressure per standard procedure until the compressor and seal piping have reached the compressor piping proof test pressure.  After piping pressure equalizes, reduce to the compressor piping leak test pressure, and leak test the seal piping and components.  

When the compressor system piping is confirmed tight by test, vent the pressure slowly.  The test is complete.

DO NOT VACUUM TEST THE SEAL PIPING.

DRY GAS SEAL: Refer to manufacturer's instructions.

Leak Test of Water Piping (where applicable)

The same procedure shall be followed for all York supplied water piping as is used for refrigerant piping, with the exception that nitrogen only is to be used, and therefore, leaks can only be identified using a soap solution.

Leak Test for Control-Air Piping (where applicable)

The control air piping shall be leak tested by introducing nitrogen, initially at a pressure corresponding to the lowest pressure regulator setting shown on the pneumatic diagram.  The regulators should progressively be set one at a time, starting with the lowest set regulator and finishing with the highest set regulator, the nitrogen pressure then being increased in steps accordingly.  Leak test all joints with a soap solution, mark all leaks and then repair as necessary. Re-check until the system is considered leak tight.  When complete release the nitrogen slowly.
























































































































































































� Example of single seal with outboard barrier is the M compressor Zero Emission seal





	Leak Testing.doc
	Status: Released
	3 Mar 04  Ver 1.07



