YORK

Process Systems
Installation Operation Maintenance Manual

YORK

Process Systems
Installation Operation Maintenance Manual


LOW TEMPERATURE OPERATIONS

On systems that are located outdoors or are in unheated buildings where the ambient temperatures could drop below +40F, attention should be given to the insulating and/or heat tracing of compressor lube oil systems:

It is recommended that oil separators be provided with insulation as a minimum requirement to preserve the heat generated by the oil heaters.  It is important that the coalescer end be insulated to prevent refrigerant condensation.

When low ambient temperatures (below +20F) are to be encountered, attention should be given to heat tracing and insulation of lube oil lines, oil filters, oil pumps and oil coolers.

Freeze-up protection must be provided for all water-cooled equipment.
























































































































































































Section-03 data
Status: Released
8 Aug 00  Ver 1.04


