	YORK

Process Systems
	Installation Operation Maintenance Manual


	YORK

Process Systems
	Installation Operation Maintenance Manual



REFRIGERANT / LUBE OIL CHARGING, GENERAL
Ensure that the package has been fully insulated and that the system is adequately grounded.  Now check that the compressor(s) and lube oil pump(s) are ready for operation.

NOTE: 
Before charging and startup of the compressor(s), it is necessary to ensure that the lube oil circuit pipework is clean and free of grit, scale or other foreign matter.  This is usually accomplished at the factory, however, if field connections are made to the system (E.G. remote air cooled oil cooler), flushing is required for the connected piping.  Carry out a flushing procedure for the non-factory assembled piping during commissioning.  Include air-cooled heat exchangers in the flush.
As it will be necessary to run the compressor(s) to complete refrigerant charging, a preliminary test run of the drive motor must be completed and a check must be taken to ensure that the drivetrain has been aligned correctly.

At this time, any acoustic housing's coupling guards, etc., should be assembled and fitted before proceeding.

Removal of the holding charge by evacuation to 3 mm Hg Abs (4 m Bar A) must also be achieved if introduced into the system.  See Section 5.
























































































































































































	Section-06
	Status: Released
	2 May 02  Ver 1.06



