YORK

Process Systems
Installation Operation Maintenance Manual

YORK

Process Systems
Installation Operation Maintenance Manual


 SAFE REFRIGERATION PRACTICES
Holding Procedure
If the system is to stand for any long period of time, a holding charge of oxygen free nitrogen (OFN) should be introduced.

A holding charge is usually introduced after vacuum dehydration or after the refrigerant has been removed from the system, this ensures that no air or moisture ingress occurs as the holding charge is above atmospheric pressure.  The system pressure is usually raised to a 15 psig (1 bar G) using the following procedure:

(1) Open all manually operated valves with the exception of vents and drains.

(2) Install pressure gauge in a position from where regular monitoring can take place.

(3) Using the charging point or a similar low point connection, charge OFN to a pressure of 15 psig (1 bar G).

(4) Clearly identify at all accessible valves and areas that THIS SYSTEM IS OFN CHARGED TO 1 bar G PRESSURE.

(5) Regularly monitor and record at daily/weekly intervals the system pressure.

Exposure Limits & Physical Properties
As more and more information is gathered on refrigerants the maximum exposure limits may vary, however for the current exposure limits refer to the manufacturers MSDS sheets.

Chemical & Physical Properties of Common Refrigerants
Refrigerant
Halocarbons
Hydrocarbons
R717

Effect on metal
May attackmagnesium but no other normal constructional metals
Generally inert to metals. High sulfer concentrations will attack copper and aluminum.
With presence or water attacks copper, zinc, tin, cadmium and most of their alloys

Effect on rubber
All refrigerants attack natural rubber and many synthetics.  Various synthetic rubber mixtures are suitable for individual refrigerants.

Behavior with Oil
Miscible at high temp
Depends on Oil.  Generally miscible to various degrees with mineral and PAO oils.  Non-miscibel with PAG oils.
Non-miscible

Dielectric Strength
Medium
Medium
Low

Flammability
Generally non-flammable but may be explosive when combined with air at high pressure.  Will breakdown at red heat to produce toxic fumes
Flammable and/or explosive.
16-25% by vol. In air explosive

Toxicity
Relatively non-toxic in 0.5 hours
0.5% by vol. In air can kill

Odor
Very little
Little, unless odorizer has been added.
Pungent
























































































































































































Section-07xxxxxxx
Status: Released
16 May 02  Ver 1.08


