YORK

Process Systems
Installation Operation Maintenance Manual

YORK

Process Systems
Installation Operation Maintenance Manual


SHUTDOWN AND OPERATING SETPOINTS DATA SHEET

SCREW COMPRESSOR
ADJUSTABLE SETPOINTS

TAG NUMBER

SERVICE





SETPOINT











DESIGN

ACTUAL
CC

CAPACITY CONTROL (AUTO)



114 PSIA

LPCO

LOW COMPRESSOR SUCTION PRESSURE 



CUTOUT






30 Psig

LPA

LOW COMPRESSOR SUCTION PRESSURE 



ALARM






40 Psig

HPCO

HIGH COMPRESSOR DISCHARGE PRESSURE 



CUTOUT






260 PSIG

HPA

HIGH COMPRESSOR DISCHARGE PRESSURE 



ALARM






250 PSIG

MLC 1
MOTOR LOAD CONTROLLER STOP LOAD 


95 % 

MLC 2
MOTOR LOAD CONTROLLER FORCE UNLOAD 

100 % 

CT FACTOR

CURRENT TRANSFORMER FACTOR

73

RECY. DELAY
MOTOR RESTART RECYCLE DELAY

30 MIN

NOTE :
SETPOINTS LISTED ARE SUGGESTED INITIAL SETTINGS.  THEY SHOULD BE CHECKED AND REVISED, IF NECESSARY, TO SUIT ACTUAL OPERATING CONDITIONS.

FIXED SETPOINTS
TAG NUMBER

SERVICE





SETPOINT











DESIGN

ACTUAL
DTCO


HIGH COMPRESSOR DISCHARGE TEMPERATURE




CUTOUT





100°C (212° F)

DTA


HIGH COMPRESSOR DISCHARGE TEMPERATURE




ALARM





93.3°C (200° F)

HTCO


HIGH OIL TEMPERATURE CUTOUT

75°C (167° F)

HTA


HIGH OIL TEMPERATURE ALARM

70°C (158° F)

LTCO


LOW OIL TEMPERATURE CUTOUT

9.4° C (49° F)

LTA


LOW OIL TEMPERATURE ALARM

12.8° C (55° F)

PB


PROPORTIONAL BAND



10%

DB


DEAD BAND





1.0 PSI

FDA


HIGH FILTER DIFFERENTIAL PRESSURE




ALARM





25 PSID

OHTR


OIL HEATER ON




50°C (122°F) 

OPCO


LOW COMPRESSOR OIL PRESSURE CUTOUT
*

OPA


LOW COMPRESSOR OIL PRESSURE ALARM
*




*
Setpoint determined by Quantum; refer to S90-010 O.
























































































































































































Section-12XXXX
Status: Released
27 Feb 02  Ver 1.04


