	YORK

Process Systems
	Installation Operation Maintenance Manual


	YORK

Process Systems
	Installation Operation Maintenance Manual



UTILITIES

LOCATION:
OUTDOORS, UNDER ROOF
EXPECTED AMBIENT:


Ambient Temp. (Min.)
10 F


Ambient Temp. (Design/Max.)
105 F


Relative Humidity
17-100 %

PNEUMATIC AIR REQUIREMENTS PER DRIVELINE:


Pneumatic Air Pressure Required
80 – 100 PSIG

Pneumatic Air Flow Required
6400 SCFM 
Note:  6400 SCFM includes 4000 SCFM required for each package and 2400 SCFM for field mounted valves and instrumentation associated with one package.
ELECTRICAL REQUIREMENTS:


Area Classification
NEMA 4X, PURGED, N.E.C. CLASS I, GP C&D, DIV 2


Driver Motor Voltage
  4000 V- 3 PH - 60 HZ


Oil Pump Voltage
  460 V- 3 PH - 60 HZ

Oil Heater Voltage
  120 V- 1 PH - 60 HZ

Control Voltage
  120 V- 1 PH - 60 HZ
LUBE OIL REQUIREMENTS:


EQUIPMENT
OIL TYPE - DISCRIPTION
QTY (GAL)

Compressor
YORK J - Synth Ester, 41-50 cSTat 40°C (104°F) 
55-70 GALS

Gear
ISO VG 32 (150 SSU at 100°F)
50-55 GALS

Driver
(see motor vendor IOM in Section 8)


Oil accompanying refrigerant escaping from a system can form a mist that could cause a fire or explosion.

WARNING: Lubrication oils may be flammable and must be handled with care.  Oils are toxic to various degrees. For critical information, obtain a MSDS data sheet by contacting YORK International Corporation (717) 762-2121 or  (800) 451-8346 (Frick oils only).
Many lube oils are hygroscopic and subject to degradation when exposed to atmosphere moisture.

REFRIGERANT REQUIREMENTS:


Refrigerant
R-134A

System Refrigerant Charge
By System Designer (Customer)

Approximate Package Charge
500 lbs

Oil Cooler Requirements:


Cooling Duty:
146.75  KBtu/hr


Refrigerant Flow Rate:
2206.2 Lb/Hr


Minimum Supply Pressure
119 PSIA























































































































































































	Utilities.doc
	Status: Released
	25 Sep 00  Ver 1.04



